## Sheet1
issue_name | 290T658 | 337X233 | 337X244 | 337X305 | 337X380 | 337X704 | 761X004
IR, PI | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] "Standard electrical testing on the field winding included: 1. Insulation Resistance testing at 500 VDC... The measured value of 16.59 Gig ohm at 1 minute... Test result = PASS... 1. Polarization Index... The resultant PI ratio... of 4.2 is indictive of a dry/clean winding." [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 195] "PI 5.14 4.15 #VALUE! 1.97 3.96 3.95" and table shows 1â€‘minute IR as low as 2.20 (GÎ©) on Mar 24, 2025. [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 194] "We did see a decrease in the IR/PI values on March 24, 2025. This was the result of the space heater being unplugged... The next few tests saw the IR/PI values recover and is in satisfactory condition for return to service." | [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory." [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 608] "INSULATION RESISTANCE AT 500V (TM4030) ... Time (min) R (megohms) ... 0.50 8600 ... 10 87500 ... PASS PI 5.1" | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'The last test performed had a final insulation resistance value of 29.8 megohms and a PI of 0.94. The minimum PI should be 1.2 at 29.8 megohms.' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 24] 'Final PI after collector cleaning and heating. PI value was 0.94...' (Field Measurements table shows 10 min = 29.8 MÎ©). [FSR File: Ravenswood_Generating_Station_-_U40.pdf] [Page: 348-349] 'Rotor Megger ... Based on the results, the insulation is in electrically good ... condition and is good to return into service until next outage.' | [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 274] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 275] 'INSULATION RESISTANCE AT 500V (TM4030) ... Time (min) R (megohms) ... 1 6880 ... 10 20700 ... PASS PI 3.0' | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 632] 'INSULATION RESISTANCE AT 500V (TM4030) ... 10 67300 ... PASS PI 2.3' [Field_Service_ReportProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 631] 'Generator rotor field electrical tests series was performed ... â€¢ Insulation Resistance with Polarization Index ... Results ... resulted satisfactory' [Field_Service_ReportProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 633] 'This test is performed to help detect if shorted coils exist ... RSO ...' | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 30] '...10.29G' and 'Post-Hipot 500V Megger' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 31] 'PI 4.1' and '13.31G' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 36] 'PI 4.4' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] 'ALL TEST PASSED' | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 553] "The test was made with 500 VDC in the rotor winding per 10 minutes. By GE criteria the values presented are accepted." [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 555] "INSULATION RESISTANCE AT 500V (TM4030)... 10 94300... PI 4.6" [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] "The following Electrical Tests were carried out to this device, Polarization Index & Insulation, DLRO and Impedance at zero speed... All of them were passed successfully and exceeding the GE standards for this device."
Winding resistance | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] "Winding Resistance - ... The measured resistance taken this year is within the allowable +/-2% tolerance for return to service. Test result = PASS." [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 193] "FIELD WINDING RESISTANCE (TM4010) ... CE 18.0 0.1406 ... TE 18.0 0.1403 ... Average 18.0 ..." [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 192] "The observed impedance is within acceptable tolerance (as per GE TM4020) for return to service. Test result = PASS." | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 608] 'FIELD WINDING RESISTANCE (TM4010) ... CE 15.8 0.1385 ... TE 15.9 0.1403 ... 0.1338' | [Ravenswood_Generating_Station_-_U40.pdf] [Page: 358] "FIELD WINDING RESISTANCE (TM4010) 0.1346 ... 10/03/22 S.Proctor"; [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 25] "Resistance corrected to 25 Âº C = 0.1395" and "Factory Resistance at 25ÂºC= 0.1403" | [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 274] '3.5.14 Field Electrical Test... The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 275] 'FIELD WINDING RESISTANCE (TM4010) ... CE 24.0 0.1413 ... TE 24.0 0.1403 ... Average 24.4' and instrument IDs with calibration dates. | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 511] 'Electrical testing performed on the generator rotor fields... Results for the performed on both generator rotor fields resulted satisfactory, within or above the minimum recommended.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 631] 'Field copper winding resistance value resulted within the acceptable range values.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 632] 'FIELD WINDING RESISTANCE (TM4010)... CE 0.1375 ... TE 0.1403 ... Resist. @25 ÂºC' | [FSR: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 36] 'Resistance = 0.1400' [Page: 38] 'Resistance = 0.1434' [Page: 37] 'Resistance = 0.1420' [Page: 31] '0.1397' [Page: 30] 'Resistance = 0.1410' | [PRISM Data] 'ADJ_RISK: 0.35417130941121944' 'RISK_PROFILE: Rotor Medium Risk' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 555] 'FIELD WINDING RESISTANCE (TM4010)... TE 0.1305 ... CE 0.1313 ... Resist. @25 ÂºC' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 553] 'According to results, the rotor presented acceptable values according to GE criteria.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 554] 'The graph obtained indicates the winding has no shorted turns. Test result is satisfactory.' [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 51] 'Factory Resistance at 25ÂºC= 0,1035' [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'Electrical Tests... Polarization Index & Insulation, DLRO and Impedance at zero speed.'
RSO (Recurrent Surge Oscilliograph) | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 192] 'Field Winding Electrical Testing... The resultant impedance vs voltage plot... within acceptable tolerance... Test result = PASS.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 213] 'Verify field ground detector' with FGPA readings. | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 608] Field impedance and 500V megger/PI data table shown; no RSO listed. [337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] 'Shorted Turn (Flux Probe) test data was acquired... shows the permanent flux probe was providing a clean noise free signal.' | [FSR File: Ravenswood_Generating_Station_-_U40.pdf] [Page: 349] 'A flat or gradually increasing line indicates that no shorted turns have been detected.' [FSR File: Ravenswood_Generating_Station_-_U40.pdf] [Page: 358] 'FIELD IMPEDANCE (TM4020)... PASS PI 4.0' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'An impedance test was performed... The resultant curve was linear, suggesting a lack of gross shorted turns at standstill.' | [337X305 2022-11-18 Robotic.pdf] [Page: 81] '1 - 55 Hz, 0.0035 g/lbf PASS' [337X305 2022-11-18 Robotic.pdf] [Page: 264] '3 - 77.0 Hz, 0.2790 g/lbf ... 1 - 55 Hz, 0.1287 g/lbf PASS' | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 511] "Electrical testing performed on the generator rotor fields were the following: â€¢ Copper Winding Resistance â€¢ -Insulation resistance test with Polarization Index (PI) â€¢ -AC Impedance Test â€¢ RSO ... Results for the performed on both generator rotor fields resulted satisfactory, within or above the minimum recommended." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 633] "This test is performed to help detect if shorted coils exist... Contamination can interfere with the measurements... we strongly recommend... perform a probe test signal measurement of flux the next start and making a measurement every 10% load increment during both signals, radial and tangential," | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] "ALL TEST PASSED"; [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 31] "O-Scope... 1 Minute Pass ... RSO"; [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 36] "**The error should be less than 3%, to proceed with test" and "Sum of Voltages 100.3 AC ... % comparison*** 0.1%"; | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 553] "The test was made with 500 VDC in the rotor winding per 10 minutes. By GE criteria the values presented are accepted. AC Impedance Test This test was performed on rotor field to determine the windingâ€™s impedance... detect the presence of shorted turns" [PRISM Data] ADJ_RISK: 0.35417130941121944; RISK_PROFILE: Rotor Medium Risk
Gen Field Excitation Fleet | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 218] 'Verify equality... M1 M2 C Controller equality? equal... As Found Efd Ifd...' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 224-225] 'As Found Efd Ifd... Verify De-Excitation Modules... Battery test... Current sensor test' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Pages: 231-234] 'TIL 2529... Exciter trip reliability improvement... update ExcitrPLLUnsyncTime parameter to one second' | [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 624] "JPS Pins 7 & 8 M1 M2 C 29Vdc 28.18 28.01 27.98" [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 623] "No blown fuses found"; "Harmonics Filter checks â€¦ R1 10.3 C1 5.20 â€¦" [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 622] "Inspect control wiring â€¦ Capacitor checks" [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 608] "FIELD IMPEDANCE (TM4020) â€¦ PASS PI 5.1" [FSR File: 337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] "Coil #3 of Pole X contains 3 (three) shorted turns." | [Ravenswood_Generating_Station_-_U40.pdf] [Page: 358] 'FIELD IMPEDANCE' (form template, no unit-specific values shown) [Ravenswood_Generating_Station_-_U40.pdf] [Page: 366] 'Generator Test & Inspection... HIGH VOLTAGE PROOF TEST per TM2050' (no excitation delta ratio shown) [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 25] 'Resistance corrected to 25 Âº C = 0.1395... Factory Resistance at 25ÂºC= 0.1403' and 'PI 0.5' [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 24] 'Final PI after collector cleaning and heating. PI value was 0.94...' [IBAT Data] 'No IBAT data found.' [PRISM Data] 'No PRISM data found.' | [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 84] 'GENERATOR ENDWINDING RESONANCE TEST... COLLECTOR END SERIES LOOP RESPONSES' (stator endwinding test) [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 122] 'GENERATOR ENDWINDING RESONANCE TEST... COLLECTOR END PHASE CONNECTION RESPONSES' (stator endwinding test) [IBAT Data] No IBAT data found [Contract Data] No contract data found [PRISM Data] No PRISM data found | [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 10] 'Percent Load: 6.3; MWs: 12.0; MVars: 1.0; Amps: 630; Volts: 85' [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 12] 'Percent Load: 11.0; MWs: 21.0; MVars: -2.0; Amps: 630; Volts: 85' [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 14] 'Percent Load: 14.7; MWs: 28.0; MVars: 0.0; Amps: 630; Volts: 85' [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 17] 'S-I Percent Load: 15.7; MWs: 30.0; MVars: 0.0; Amps: 660; Volts: 90' [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 22] 'Percent Load: 69.2; MWs: 132.0; MVars: 11.0; Amps: 1000; Volts: 150' [IBAT Data] 'No IBAT data found.' [PRISM Data] 'No PRISM data found.' | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 30] 'Electrical Testing - Field Assembly' [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 36] 'FIELD WINDING RESISTANCE... IB collector ring to P-P 50.1 AC ... OB collector ring to P-P 50.2 AC ... Voltage across rings 100.6 AC' [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 37] 'IB collector ring to P-P 50.1 ... OB collector ring to P-P 50.1 ... Voltage across rings' [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] 'ALL TEST PASSED' | [FSR File: 53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 51] 'FIELD IMPEDANCE CHARACTERISTIC' [FSR File: Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 557] 'If no shorted turns exist, the voltages from each collector ring to the pole-to-pole connector should be approximately equal.' [PRISM Data] 'ADJ_RISK: 0.35417130941121944; RISK_PROFILE: Rotor Medium Risk' [IBAT Data] 'No IBAT data found.' [Contract Data] 'No contract data found.'
Flux probe | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] "The resultant PI ratio (measured during this outage) of 4.2 is indic[t]ive of a dry/clean winding. Test result = PASS." and "The measured resistance taken this year is within the allowable +/-2% tolerance for return to service. Test result = PASS." and "AC Impedance - This test can detect shorted turns between the coils of the winding." | [FSR File: 337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] 'This field has 2 poles with 5 coils per pole. Coils #1 through #5 contain 16 turns each.' [FSR File: 337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] 'The analysis of this data concludes the field contains the following turn shorts: Coil #3 of Pole X contains 3 (three) shorted turns.' [IBAT Data] No IBAT data found. [Contract Data] No contract data found. [PRISM Data] No PRISM data found. | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'The resultant curve was linear, suggesting a lack of gross shorted turns at standstill.' [Ravenswood_Generating_Station_-_U40.pdf] [Page: 349] 'A flat or gradually increasing line indicates that no shorted turns have been detected.' [Ravenswood_Generating_Station_-_U40.pdf] [Page: 358] Field Impedance data table showing gradual Z increase with voltage (standstill AC test). [Ravenswood_Generating_Station_-_U40.pdf] [Page: 370] 'Slot 37 Typical view of flux Probe. 14â€ from CE RR.' [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] 'The end windings... were inspected and no problems were observed.' | [337X305 2022-11-18 Robotic.pdf] [Page: 48] "The Collector End Series Loop axial, radial and tangential responses were acceptable and found within limits. The Collector End Phase Connection axial, radial and tangential responses were acceptable and found within limits." [337X305 2022-11-18 Robotic.pdf] [Page: 193] same summary language confirming CE series loops and phase connections testing (stator end-winding bump test). | [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 3] "The analysis of this data concludes the generator field contains the following turn shorts: 4 turn shorts in coil #2 at pole X, 4 turn shorts in coil #4 at pole Y, 5 turn shorts in coil #5 at pole X." [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 3] "This field has 2 poles with 5 coils per pole. Coils #1 through #5 each contain 16 turns." [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 3] "The data was acquired at 20 load points... Loads ranged from 0 MWs... to 175 MWs..." [337X380 2022-02-12 Flux Probe Test.pdf] [Page: 24-25] High-load data records shown for 91.7% load (175 MW) confirming valid data acquisition. | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 7] 'After all the coils are installed perform a set of electrical tests (winding resistance, megger-PI, AC impedance, pole balance test)' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 36] 'FIELD WINDING RESISTANCE... Electrical Testing - Field Assembly' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 38] 'FIELD IMPEDANCE CHARACTERISTIC' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] 'ALL TEST PASSED' | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 542] 'During field installation, flux probe was broken... replaced with a new one provided by Customer, original FP was located on the CE side.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 543] 'According to the unit drawings this shows to be on the TE side... flux probe installation on the TE side, slot 32 as per drawing.' [PRISM Data] ADJ_RISK (Rotor): 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk
Vibration | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 194] "We did see a decrease in the IR/PI values on March 24, 2025... The next few tests saw the IR/PI values recover and is in satisfactory condition for return to service." [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 195] "Insulation resistance recovered over the next few tests and has stabilized due to the consistent atmospheric temperature provided by the space heater." | [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 514] "Based on ER recommendations... It is safe to leave the temp blocking material as-is... The field will run hotter. It is recommended to carryout flux probe testing in 6 months and thermal sensitivity test in a year." [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory." | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] "Field Winding; ... A polarization index test was performed and the results were below our minimum standard indicating a damp, dirty winding. ... The collector rings and insulating sleeve were cleaned ... The PI increased from 0.53 to 0.97 but was still below our minimum acceptable value. ... The last test performed had a final insulation resistance value of 29.8 megohms and a PI of 0.94. The minimum PI should be 1.2 at 29.8 megohms." | [FSR - 337X305 2022-11-18 Robotic.pdf] [Page: 294] "The CDM#11 appeared to be disconnected. The generator bearing 2 drain temperature was reading over 200 degrees F but the generator bearings metal temperature was reading withing acceptable limit." [FSR - 337X305 2022-11-18 Robotic.pdf] [Page: 295] "Recommendation â€¢ When unit is offline, check the connection between CDM probe and cable. â€¢ Check the generator bearing drain thermocouple (see screen shot)." [FSR - 337X305 2022-11-18 Robotic.pdf] [Page: 275] "Reading Checks per TM4010 ... 8 Point Resistance Check ... FIELD IMPEDANCE" | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 633] "This test is performed to help detect if shorted coils exist... The results shows an possibility of shorted coils... Recommendation Description: Flux probe reading it necessary for proper evaluation of shorted coils"; No PRISM data found; No IBAT data found; No Contract data found | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] 'ALL TEST PASSED' [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 31] '1 Minute Pass' (post-Hipot 500V Megger) | [PRISM Data] SERIAL_NUMBER: 761X004, ADJ_RISK: 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk. [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 363] 'Seismic Vibrations are operating under alarm limits and in normal operational ranges.'
Thermal Sensitivity Test | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] 'Standard electrical testing on the field winding included: 1. Insulation Resistance... The measured value of 16.59 Gig ohm at 1 minute... PI ratio ... of 4.2 ... Test result = PASS.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 192] 'AC Impedance - ... observed impedance is within acceptable tolerance ... Test result = PASS.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 194] 'We did see a decrease in the IR/PI values on March 24, 2025... This was the result of the space heater being unplugged...' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 512] 'MAGIC Jr. visual inspection of Field â€¢ Borescope under Retaining Rings (RR) â€¢ Field test' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 513] 'ER20221021-1242 Temp blocking found in Field sub slot at 90 degrees Recommendation: 1) Remove Field... 3) Leave material in place' | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'A polarization index test was performed... The last test performed had a final insulation resistance value of 29.8 megohms and a PI of 0.94. The minimum PI should be 1.2 at 29.8 megohms.' 'An impedance test was performed and the data was plotted. The resultant curve was linear, suggesting a lack of gross shorted turns at standstill.' | [337X305 2022-11-18 Robotic.pdf] [Page: 59] 'CER002 ... 1 - 55 Hz, 0.0094 g/lbf PASS' [337X305 2022-11-18 Robotic.pdf] [Page: 70] 'CER014 ... 1 - 55 Hz, 0.0090 g/lbf PASS' | [337X380 2016-01-18 HNI Test.pdf] [Page: 3] "Table of Contents" referencing HNI test (stator-related). [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 610] "3.3 Stator Tests" [Page: 618] "DC leakage was performed at 1.05E (1.05X18=18.9KVdc) as per customer request." | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 32] "GE Energy Parts & Repair Services Electrical Testing - Field Assembly" [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] "ALL TEST PASSED" | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 430] "MAJOR INSPECTION (MI) - 298374, MAJOR INSPECTION (ROTOR) - 761X004" [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 422] Table entries: "1R-RingC-GT1" ... "0 - 20 g pk" (vibration channel listing, no thermal sensitivity results)
Ventilation hole blocking (migration of slot components) | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] '...blocking is in place with no evidence of fretting/dusting between the blocks and copper turns. Visually the field end turns are in acceptable condition for return to service.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 524] 'Found temp blocking in Field sub slot at 90 degrees... The weight of the block ~2.7 lbs, the length is ~23 in... The field will run hotter... carryout flux probe test in 6 months and thermal sensitivity test in a year.' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 526] '294 Deg View looking down partially blocked field vent hole ~143â€ from CE RR' and '294 Deg View looking down partially blocked field vent hole ~85â€ from CE RR'. | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 28] "A visual examination was performed utilizing a MAGIC (rotor in-situ) inspection... The vent holes were clean but several holes were partially obstructed by creepage block and wedge movement. The field was covered with a light film of oil." and "Partial vent hole blockage." | [337X305 2022-11-18 Robotic.pdf] [Page: 205] '1 - 55 Hz, 0.0010 g/lbf PASS ... CER003' [337X305 2022-11-18 Robotic.pdf] [Page: 214] 'CER013 ... 1 - 55 Hz, 0.0009 g/lbf PASS' [337X305 2022-11-18 Robotic.pdf] [Page: 215] 'CER014 ... 1 - 55 Hz, 0.0008 g/lbf PASS' [337X305 2022-11-18 Robotic.pdf] [Page: 223] 'CET023 ... 1 - 55 Hz, 0.0044 g/lbf PASS' [337X305 2022-11-18 Robotic.pdf] [Page: 75] 'CER019 ... 1 - 55 Hz, 0.0120 g/lbf PASS' | [337X380 2014-07-16 Robotic.pdf] [Page: 35] "No observation was made regarding movement or migration of any of the field components that could cause blockage of gas flow thru generator rotor field copper windings." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] "Generator rotor field ventilation passages were found partial blocking." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] "Some creepage block migration was observed on some of the rotor field slots as well as leaf spring migration." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] "Special attentions need to be carry on the vent holes blocking issue, elevated vibration level can confirm thermal sensitivity." | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 26] '3 Wedges per slot (24 total), none are staked, all are held in place by snap rings.' | [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] "FIELD VENTILATION PASSAGES: Field ventilation passages were inspected for obstruction from either debris or internal components such as creepage block migration... No observation was made regarding movement or migration of any of the field components that could cause blockage of gas flow thru generator rotor field copper windings." [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 546] "Field ventilation passages were inspected for obstruction from internal components such as creepage block migration... Ventilation passages were free from obstruction." [PRISM Data] ADJ_RISK: 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk
Turn to turn insulation migration | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] 'Standard electrical testing on the field winding... The measured value of 16.59 Gig ohm at 1 minute... Test result = PASS.'; 'Polarization Index... PI ratio of 4.2 is indictive of a dry/clean winding. Test result = PASS.'; 'AC Impedance - This test can detect shorted turns between the coils of the winding.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 192] 'The observed impedance is within acceptable tolerance (as per GE TM4020) for return to service. Test result = PASS.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] 'The blocking is in place with no evidence of fretting/dusting between the blocks and copper turns... Visually the field end turns are in acceptable condition for return to service.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 194] 'field had to be removed... periodic testing was performed to monitor the integrity of the winding insulation.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 195] 'Insulation resistance recovered... and has stabilized due to the consistent atmospheric temperature provided by the space heater.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 512] "MAGIC Jr. visual inspection of Field ... Borescope under Retaining Rings (RR) ... Field test" [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] "While inspecting the Field it was noticed that a temporary blocking was found ... There was also slot insulation ... movement at the slot" [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 513] "ER20221021-1242 ... The sub slot insulation was to be monitored and verify the slot button is still in place to keep slot insulation" [Field_Service_ReportProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 514] "It is recommended to carryout flux probe testing in 6 months and thermal sensitivity test in a year." [Field_Service_ReportProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI ... results were satisfactory." [337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] "Coil #3 of Pole X contains 3 (three) shorted turns." | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] 'The end windings were clean and there were no sign of insulation migration between the turns.' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 7] 'Field ... End Turns Borescope Inspection No Problem Areas Found' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'The resultant curve was linear, suggesting a lack of gross shorted turns at standstill.' | [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 274] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory." [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 138] "A visual inspection of the Stator Core and Field was performed using MAGIC Jr." [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 275] "Reading Checks per TM4010... 8 Point Resistance Check... FIELD IMPEDANCE" | [337X380 2014-07-16 Robotic.pdf] [Page: 35] 'Collector End field winding end turns (windings) were inspected for cleanliness, signs of overheating, distortion, turn-to-turn insulation migration and elongation. None, of these previous mentioned signs were observed during this outage.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 633] 'This test is performed to help detect if shorted coils exist due to insulation degradation between coils, copper dusting, or insulation migration between coils...' [Field_Service_ReportProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] 'Slight center wedge migration was observed, no signs of end ...' | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 45] 'Figure 16: Damage Coil Connector' / 'Figure 17: Foreign material in winding' / 'Figure 18: Rolled Locking Ring' | [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'FIELD WINDING END TURNS ... were inspected for cleanliness, signs of overheating, distortion, turn-to-turn insulation migration and elongation. None ... were observed during this outage.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] 'Turn to Turn Insulation It was not observed any sign of mechanical or electrical issue in the insulation of the winding coils.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 554] 'The graph obtained indicates the winding has no shorted turns. Test result is satisfactory.'
Slot armour migration/damage/cracking | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 175] 'Dirty, No cracking observed on slot liner corners, No migration observed.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 188] 'Sub Slot ... Insulation Migration Blocker, acceptable.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 455] "Vane... Trailing Edge Max Length of Crack" (gas turbine vane data, not generator rotor) [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 461] "Vane... Diaphragm..." (non-rotor) [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 467] "Vane 1 Trailing Edge Max Length of Crack 4 mm" (non-rotor) [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 469] "Vane... Discourager Seal..." (non-rotor) | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 28] 'The vent holes were clean but several holes were partially obstructed by creepage block and wedge movement. The field was covered with a light film of oil.' and 'Partial vent hole blockage.' [Ravenswood_Generating_Station_-_U40.pdf] [Page: 370] 'Slot 19 Cracked wedge. Wedge number 15. 75â€ from CE RR.' | [337X305 2022-11-18 Robotic.pdf] [Page: 48] "The collector end of the generator was disassembled as part of the MAGIC inspection." and rotor items listed with "No major issues were found" (oil deflectors) and "No issues were noted" (bearing/H2 seal case). [337X305 2022-11-18 Robotic.pdf] [Page: 49] "End shield ... No defects were noted..." and "Fan blades ... No issues were noted." [337X305 2022-11-18 Robotic.pdf] [Page: 140] "CE RR View of sub-slots at 90 deg... CE RR View of foreign material at 90 deg. Which was removed." | [337X380 2014-07-16 Robotic.pdf] [Page: 6] 'Field Assembly: Field body, wedges, balance weights, vent holes, field sub slots, collector rings, and retaining rings...' [337X380 2014-07-16 Robotic.pdf] [Page: 35] 'No observation was made regarding movement or migration of any of the field components that could cause blockage of gas flow thru generator rotor field copper windings.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] 'Slight center wedge migration was observed...' and 'Generator rotor field ventilation passages were found partial blocking.' | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 46] 'Figure 19: Damaged Slot Armor' and 'Figure 20: Damaged Slot Armor Cont.' | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 546] 'Field ventilation passages were inspected for obstruction from internal components such as creepage block migration... Ventilation passages were free from obstruction.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] 'The slots armor and the sub slot insulation were inspected for any sign of cracking... it was not detected any sign that could lead to a broken insulation or electrical issue during normal operation.' [PRISM Data] ADJ_RISK: 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk
EW support blocking migration (end winding) | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] 'The blocking is in place with no evidence of fretting/dusting between the blocks and copper turns. Visually the field end turns are in acceptable condition for return to service.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 186] 'The blocking is in place with no evidence of fretting/dusting between the blocks and copper turns. Visually the field end turns are in acceptable condition for return to service.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] "The MAGIC inspection found the following on the Stator and Field: ... Field ... End Winding blocking ... While inspecting the Field it was noticed that a temporary blocking was found ... There was also slot insulation ... movement at the slot exits." [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 524] "Opened ER-20221021-1242 - Found temp blocking in Field sub slot at 90 degrees ... The weight of the block ~2.7 lbs, the length is ~23 in ... Put temp blocking deeper in the slot exit ~4ft inside opening." | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 7] 'Field ... End Turns Borescope Inspection No Problem Areas Found' ¦ [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] 'The end windings were clean and there were no sign of insulation migration between the turns.' ¦ [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 28] 'The vent holes were clean but several holes were partially obstructed by creepage block and wedge movement.' ¦ [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 29] Rotor inspection checklist comments: 'The field body was covered with a light film of oil.' | [337X305 2022-11-18 Robotic.pdf] [Page: 48] "The turbine end of the generator was disassembled to investigate the end winding vibrations. Fan blades were cleaned and NDE performed... No issues were noted." [337X305 2022-11-18 Robotic.pdf] [Page: 49] "The end shield was cleaned and inspected. No defects were noted... the weight of the field was taken out of the end shield and the seal case step was set to less than 0.001 inches as per specification." | [337X380 2014-07-16 Robotic.pdf] [Page: 35] 'The field blocking was inspected for signs of looseness and/or dislodging. The blocking pattern appeared to be concentric with no signs of movement or migration.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 624] 'The field blocking was inspected for signs of looseness and/or dislodging. The blocking pattern appeared to be concentric with no signs of movement or migration.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] 'Slight center wedge migration was observed' (note: wedge migration, not blocking migration). | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 44] 'Figure 14: Loose Blocks' | [FSR File: 53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'FIELD WINDING BLOCKING: The field blocking was inspected for signs of looseness and/or dislodging. The blocking pattern appeared to be concentric with no signs of movement or migration.' [FSR File: 53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'FIELD WINDING END TURNS ... None of these previous mentioned signs were observed during this outage.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 554] 'The graph obtained indicates the winding has no shorted turns. Test result is satisfactory.' [PRISM Data] Rotor ADJ_RISK: 0.3542, RISK_PROFILE: Rotor Medium Risk
MTS leaves cracking/distortion (Main Terminal Stud aka goose neck) | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 177] 'Gooseneck #1 Comments No cracks or mechanical stress observed on copper leaves.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 177] 'Bore Copper Stud #1 ... Stud centered on ring. No thermal or mechanical stress observed.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 182] 'Bore Copper Stud #2 ... no thermal or mechanical stress observed.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] 'â€¢ Gooseneck assemblies' (listed among MAGIC inspection items) and 'The MAGIC inspection found the following on the Stator and Field: â€¢ Field â€¢ Dusting on Wedges â€¢ Partial blockage on vent holes â€¢ Scratches on Field â€¢ Gap between Field wedges' (no mention of MTS/gooseneck cracking or distortion). [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 524] Discussion focuses on temporary blocking in field sub-slot; no MTS findings. | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 6] "A complete set of electrical tests on the generator field... A MAGIC visual inspection of the stator and field... Bore scope inspection under the collector end retaining ring and collector end windings." [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] "Field Winding; Electrical testing was performed on the field... The collector rings and insulating sleeve were cleaned..." [IBAT Data] No IBAT data found. [Contract Data] No contract data found. [PRISM Data] No PRISM data available. | [337X305 2022-11-18 Robotic.pdf] [Page: 48] "The collector end of the generator was disassembled as part of the MAGIC inspection... The Hydrogen seal case was found with minor pitting... new seals were lapped... No issues were noted." [337X305 2022-11-18 Robotic.pdf] [Page: 269] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory." [337X305 2022-11-18 Robotic.pdf] [Page: 133] "A visual inspection of the Stator Core and Field was performed using MAGIC Jr." [337X305 2022-11-18 Robotic.pdf] [Page: 2] "The following inspections were preformed â€¢ MAGIC visual inspection of Stator â€¢ MAGIC partial wedge tightness â€¢ Visual inspection of End Winding Support System â€¢ High Voltage Bushing (HVB) â€¢ RTDs â€¢ Bump Test" | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 624] "The main leads and goosenecks, at 0 and 180 degrees, were inspected for signs of looseness, broken leaves, discoloration and overheating. Both main leads or gooseneck connectors were found in great condition and all hardware in place... No signs of damage was observed." [337X380 2014-07-16 Robotic.pdf] [Page: 35] "The main leads and goosenecks, at 0 and 180 degrees, were inspected for looseness, broken leafs, discoloration and overheating. Both leads were found in good condition." | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 24] 'MAIN / COLLECTOR TERMINAL STUD AREAS ... Very rusty in the area, normal wear' and 'MAIN / COLLECTOR TERMINAL STUD AREAS ... Very rusty in the area, normal wear marks, and mechanical damage visible.' | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] "The both goosenecks and mayor insulation components were inspected, and it was not found any indication of cracking in the leaf's or electrical problem..." [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 548] photo captions documenting main lead goose neck and stud inspection (e.g., "Main lead stud nut 0Â°, main lead goose neck, 0Â° pole") [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] "MAIN LEADS... The main leads and goosenecks... were found in good condition." [PRISM Data] "ADJ_RISK: 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk"
MTS/bore copper contact (Main Terminal Stud aka goose neck) | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 177] 'Bore Copper Stud #1 ... Stud centered on ring. No thermal or mechanical stress observed.'; [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 177] 'Gooseneck #1 ... No cracks or mechanical stress observed on copper leaves.'; [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 182] 'Bore Copper Stud #2 ... Stud centered on ring, no thermal or mechanical stress observed.'; [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] 'Borescope inspection ... dust accumulation ... The dust is originating from the stator wedges ... No mechanical or thermal stress ... Visually the field end turns are in acceptable condition for return to service.'; [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 186] '... dust accumulation ... originating from the stator wedges ... Visually the field end turns are in acceptable condition for return to service.' | [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] 'â€¢ Gooseneck assemblies' and 'The MAGIC inspection found the following on the Stator and Field: â€¢ Field â€¢ Dusting on Wedges â€¢ Partial blockage on vent holes â€¢ Scratches on Field â€¢ Gap between Field wedges' [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 609] 'Performed visual inspection of the collection rings and no worn warped rings noted... OB terminal stud IB terminal stud' [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The results of these tests were satisfactory.' | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] "A borescope inspection was performed under the collector end retaining ring... no problems were observed. The end windings were clean..." [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 28] "A visual examination was performed utilizing a MAGIC robot. No indications of any unusual deposits or mechanical damage were found... The field was covered with a light film of oil." [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 29] "Collector Ring Condition: Grooving, Burning, and Brush Film S" [Ravenswood_Generating_Station_-_U40.pdf] [Page: 349] "This is a visual examination of the collector rings... No evidence was noted of brush selectivity or arc erosion." [Ravenswood_Generating_Station_-_U40.pdf] [Page: 431] "ULTRASONIC INSPECTION... MATERIAL DESCRIPTION: Unit 40 GS Coupling Bolts... Date: 10/6/2022" | [337X305 2022-11-18 Robotic.pdf] [Page: 48] "The collector end of the generator was disassembled as part of the MAGIC inspection." [337X305 2022-11-18 Robotic.pdf] [Page: 49] "Fan blades were cleaned and NDE performed... No issues were noted." [337X305 2022-11-18 Robotic.pdf] [Page: 138] "A visual inspection of the Stator Core and Field was performed using MAGIC Jr." [337X305 2022-11-18 Robotic.pdf] [Page: 274] "The following electrical tests were performed on the Field: ... The results of these tests were satisfactory." | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 510] 'A borescope inspection was performed under the RRs paying special attention to the main terminal and gooseneck.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 624] 'Both main leads or gooseneck connectors were found in great condition and all hardware in place.' and 'There areas under retaining rings were inspected with borescope, and the overall condition of the visually accessible components was satisfactory...' [337X380 2014-07-16 Robotic.pdf] [Page: 35] 'The main leads and goosenecks... Both leads were found in good condition.' | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 24] "MAIN / COLLECTOR TERMINAL STUD AREAS ... Very rusty in the area, normal wear marks, and mechanical damage visible." [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 24] "Both main leads are intact and looks ok, with no visible issues." [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 23] "Carbon dust and rust on the surface, heavy carbon in holes." [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 7] "Clean the bore copper hole" and "Fit and install the borecopper assembly" (process steps, not findings). | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] 'The both goosenecks and mayor insulation components were inspected, and it was not found any indication of cracking in the leaf's or electrical problem that could indicate a major problem.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 548] 'Main lead stud nut 0Â°, main lead goose neck, 0Â° pole' (image caption) [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 559] 'Bore copper Inspection Collector Main Terminals Hardware Removed' [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'The main leads and goosenecks... Both leads were found in good condition.' [PRISM Data] Rotor ADJ_RISK: 0.3541713094, RISK_PROFILE: Rotor Medium Risk
Pole to pole connector cracking/distortion | [FSR File: Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 183] "Pole to Pole Jumper #1 ... Acceptable, no thermal or mechanical stress observed." and "Brazed connections acceptable." [FSR File: Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 184] "Pole to Pole Jumper #1 ... No problems observed." [FSR File: Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 185] "Pole to Pole Jumper #2 ... Acceptable, no thermal or mechanical stress observed." and "Brazed connections acceptable." [FSR File: Field_Service_ReportProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] "No mechanical or thermal stress was observed on the brazed joints... Visually the field end turns are in acceptable condition for return to service." [FSR File: Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] "Insulation Resistance... 16.59 Gig ohm at 1 minute... PI... 4.2... Test result = PASS." | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] 'â€¢ Coil-to-coil jumpers â€¢ Pole-to-pole jumper ... The MAGIC inspection found the following on the Stator and Field: ... Field â€¢ Dusting on Wedges â€¢ Partial blockage on vent holes â€¢ Scratches on Field â€¢ Gap between Field wedges' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 609] 'Performed visual inspection of the collection rings...' [337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] 'A standard analysis is performed... This field has 2 poles with 5 coils per pole.' | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] "A borescope inspection was performed under the collector end retaining ring. The end windings, main leads, coil to coil, and pole to pole jumpers were inspected and no problems were observed." [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 27] "90 degree pole to pole jumper." (photo reference) [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 6] "Bore scope inspection under the collector end retaining ring and collector end windings." [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 29] "Field Inspection Checklist Date:(m/d/y) 4/9/2013... ROTATING FIELD..." | [337X305 2022-11-18 Robotic.pdf] [Page: 138] "A visual inspection of the Stator Core and Field was performed using MAGIC Jr." [337X305 2022-11-18 Robotic.pdf] [Page: 274] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory." [337X305 2022-11-18 Robotic.pdf] [Page: 48] "The collector end of the generator was disassembled as part of the MAGIC inspection." (Rotor mechanical inspection items listed; "No issues were noted.") | [337X380 2014-07-16 Robotic.pdf] [Page: 35] "Each coil jumper was inspected for overheating, breaks, cracks and proper brazing. All jumpers were in satisfactory condition." and "The main leads and goosenecks... Both leads were found in good condition." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 624] "Each coil jumpers were inspected for overheating, breaks, cracks and proper brazing. No signs of damage was observed." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] "The main leads and goosenecks... were found in great condition..." | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 45] 'Figure 16: Damage Coil Connector' (no details on connector type or crack extent) [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 39] 'ALL TEST PASSED' (electrical tests passed; no connector crack/distortion noted) [IBAT Data] No IBAT data found [Contract Data] No contract data found [PRISM Data] No PRISM data found | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] 'The pole jumpers were found in optimal conditions and it was not detected any sign of cracking bent or overheating issue in these.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 533] 'Coil-to-Coil Jumpers/Connectorsâ€¦ none of these were observed during the inspection and the jumpers were found in normal conditions' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 556] 'the difference in voltages was only .001%. Therefore, the rotor is well balanced. This test result is satisfactory.' [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'COIL-TOCOIL- JUMPERS: â€¦ All jumpers were in satisfactory condition.'
Coil to coil connection cracking/distortion | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] 'No mechanical or thermal stress was observed on the brazed joints... Visually the field end turns are in acceptable condition for return to service.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 175] 'Turn to Turn Jumper ... Dirty, No thermal or mechanical stress observed.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 182] 'Turn to Turn Jumper ... brazed connections are acceptable, no thermal or mechanical stress observed.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 185] 'Pole to Pole Jumper #2 ... Acceptable, no thermal or mechanical stress observed.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 181] 'Gooseneck #2 ... Loose tape and some movement markings ... indicators of aging material.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 177] 'Bore Copper Stud #1 ... No thermal or mechanical stress observed.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] 'â€¢ Coil-to-coil jumpers ... The MAGIC inspection found the following on the Stator and Field: ... â€¢ Field â€¢ Dusting on Wedges â€¢ Partial blockage on vent holes â€¢ Scratches on Field â€¢ Gap between Field wedges' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 512] 'MAGIC Jr. visual inspection of Field ... Borescope under Retaining Rings (RR) ... Field test' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] "A borescope inspection was performed under the collector end retaining ring. The end windings, main leads, coil to coil, and pole to pole jumpers were inspected and no problems were observed." [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 7] "Field End Turns Borescope Inspection No Problem Areas Found" [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] "An impedance test was performed... The resultant curve was linear, suggesting a lack of gross shorted turns at standstill." [IBAT Data] No IBAT data found. [PRISM Data] No PRISM data found. [Contract Data] No contract data found. | [337X305 2022-11-18 Robotic.pdf] [Page: 138] "A visual inspection of the Stator Core and Field was performed using MAGIC Jr." [337X305 2022-11-18 Robotic.pdf] [Page: 140] "CE RR View of coil to coil jumper at 0 deg. Image 20" [337X305 2022-11-18 Robotic.pdf] [Page: 141] "CE RR View of coil to coil jumper at 180 deg. Image 42" [337X305 2022-11-18 Robotic.pdf] [Page: 274] "3.5.14 Field Electrical Test... The results of these tests were satisfactory." | [FSR File: 337X380 2014-07-16 Robotic.pdf] [Page: 35] 'Each coil jumper was inspected for overheating, breaks, cracks and proper brazing. All jumpers were in satisfactory condition.' [FSR File: Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 624] 'Each coil jumpers were inspected for overheating, breaks, cracks and proper brazing. No signs of damage was observed.' [FSR File: Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 625] 'Gus Neck Coil to Coil Jumper' (section heading indicating rotor coil-to-coil jumper inspection). | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 45] 'Figure 16: Damage Coil Connector' ¦ | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 546] "Coil-to-Coil Jumpers/Connectors... visually inspected for any sign of cracking or overheating, none of these were observed... jumpers were found in normal conditions"; [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] "Pole-to-Pole Jumpers/Connectors... found in optimal conditions and it was not detected any sign of cracking bent or overheating"; [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] "COIL-TOCOIL- JUMPERS... inspected for overheating, breaks, cracks and proper brazing. All jumpers were in satisfactory condition." [PRISM Data] ADJ_RISK: 0.35417130941121944; RISK_PROFILE: Rotor Medium Risk
EW distortion | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] 'Borescope inspection of the collector end - end turns found dust accumulation on the blocking and copper surfaces... The blocking is in place with no evidence of fretting/dusting between the blocks and copper turns. Visually the field end turns are in acceptable condition for return to service.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 49] 'Prior to removal from the generator, the field underwent the following tests: â€¢ Insulation Resistance and Polarization Index â€¢ Winding Resistance â€¢ AC Impedance' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] 'The measured value of 16.59 Gig ohm at 1 minute exceeds the return to service criteria... Test result = PASS... The resultant PI ratio (measured during this outage) of 4.2 is indicative of a dry/clean winding. Test result = PASS.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 192] 'The observed impedance is within acceptable tolerance (as per GE TM4020) for return to service. Test result = PASS.' | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 523] 'The MAGIC inspection found the following... Field... End Winding blocking... While inspecting the Field it was noticed that a temporary blocking was found... There was also slot insulation movement at the slot' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 607] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' [337X233_9-30-2024_Waterford Power Facility GT1_172215_Flux Probe Report.pdf] [Page: 3] 'The analysis of this data concludes the field contains the following turn shorts: Coil #3 of Pole X contains 3 (three) shorted turns.' | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 26] 'A borescope inspection was performed under the collector end retaining ring... no problems were observed. The end windings were clean and there were no sign of insulation migration between the turns.' [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 7] 'Field End Turns Borescope Inspection No Problem Areas Found' [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'The resultant curve was linear, suggesting a lack of gross shorted turns at standstill.' [Ravenswood_Generating_Station_-_U40.pdf] [Page: 358] 'Field Measurements' (shows field impedance data and 'PASS PI 4.0'). [Ravenswood_Generating_Station_-_U40.pdf] [Page: 349] 'Collector rings... No evidence was noted of brush selectivity or arc erosion.' | [337X305 2022-11-18 Robotic.pdf] [Page: 133] '3.5.1 Stator End Winding Assembly' and 'A visual inspection of the CE and TE winding was performed.' [337X305 2022-11-18 Robotic.pdf] [Pages: 52-53] 'End winding Vibration Test Report' and 'frequency response functions... obtained on the collector end (CE) series loops and phase connections.' (Stator) [337X305 2022-11-18 Robotic.pdf] [Page: 48] 'The turbine end of the generator was disassembled to investigate the end winding vibrations. Fan blades were cleaned... End shield was cleaned and inspected...' (Rotor-adjacent work noted, but no rotor end-winding/field coil distortion evaluation or findings documented). | [FSR File: 337X380 2014-07-16 Robotic.pdf] [Page: 35] "Collector End field winding end turns (windings) were inspected for cleanliness, signs of overheating, distortion, turn-to-turn insulation migration and elongation. None, of these previous mentioned signs were observed during this outage." [FSR File: Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] "No signs of overheating or arcing... Slight center wedge migration was observed" [FSR File: Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 633] "This test is performed to help detect if shorted coils exist... The results shows an possibility of shorted coils... perform a probe test..." [FSR File: 337X380 2022-02-12 Flux Probe Test.pdf] [Page: 3] "the permanent flux probe was providing a clean noise free signal." | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 23] "Both Collector Rings have concave wear very visible"; [Page: 26] "No overheating or mechanical damage noted on the body." | [FSR File: 53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] 'FIELD WINDING END TURNS ... were inspected for cleanliness, signs of overheating, distortion, turn-to-turn insulation migration and elongation. None, of these previous mentioned signs were observed during this outage.' [FSR File: Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 554] 'The graph obtained indicates the winding has no shorted turns. Test result is satisfactory.' [FSR File: Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 553] 'By GE criteria the values presented are accepted.' [PRISM Data] 'ADJ_RISK: 0.35417130941121944; RISK_PROFILE: Rotor Medium Risk'
Retaining ring insulation damage | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 49] "Prior to removal from the generator, the field underwent the following tests: â€¢ Insulation Resistance and Polarization Index â€¢ Winding Resistance â€¢ AC Impedance" [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 191] "The measured value of 16.59 Gig ohm at 1 minute exceeds the return to service criteria... A PI ratio... of 4.2 is indicative of a dry/clean winding. Test result = PASS." [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 194] "The field was out of the stator for approximately 15 days... periodic testing was performed to monitor the integrity of the winding insulation... We did see a decrease in the IR/PI values... the space heater being unplugged..." | [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 512] 'â€¢ Borescope under Retaining Rings (RR)' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 513] 'ER20221021-1242 Temp blocking found in Field sub slot at 90 degrees ... The sub slot insulation was to be monitored and verify the slot button is still in place to keep slot insulation' [Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 524] 'Opened ER-20221021-1242- Found temp blocking in Field sub slot at 90 degrees-- ... The slot exit insulation movement was recommended to monitor ... The weight of the block ~2.7 lbs, the length is ~23 in.' | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 6] 'Bore scope inspection under the collector end retaining ring and collector end windings.' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 29] 'Retaining Rings S' (Field Inspection Checklist). [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 7] 'Field End Turns Borescope Inspection No Problem Areas Found'. [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 23] 'The collector ring insulating sleeve was contaminated with carbon dust... The PI increased from 0.53 to 0.97... The last test... had a PI of 0.94.' | [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 48] 'The collector end of the generator was disassembled as part of the MAGIC inspection.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 138] 'A visual inspection of the Stator Core and Field was performed using MAGIC Jr.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 274] 'The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory.' | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 623] "Retaining rings are the most stressed component on the field... Retaining rings were also inspected for signs of pitting, cracks and mechanical damage. Overall condition of retaining rings is satisfactory. No visible defects observed." [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 624] "There areas under retaining rings were inspected with borescope... the overall condition of the visually accessible components was satisfactory on both ends of the generator rotor field." [337X380 2014-07-16 Robotic.pdf] [Page: 35] "Retaining rings... were inspected for discoloration caused by arcing between the inboard side of the ring and the field end wedges... Overall condition of retaining rings is satisfactory. No visible defects observed." | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 44] 'Figure 15: Retaining Ring Insulation' [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 43] 'Figure 10: CE Retaining Rings' / 'Figure 11: TE Retaining Ring' [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 26] 'No overheating or mechanical damage.' | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 546] "Retaining Rings were visually inspected in the accessible areas for discoloration caused by arching between the inboard side of the ring and the field end wedges... The overall condition of these were in a satisfactory condition, nonrelevant defects were observed." [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 547] "Slot Armor... it was not detected any sign that could lead to a broken insulation or electrical issue during normal operation." [53321_03_30_2022_15_52_25_CCI0K97ZL2VIYWXJ.pdf] [Page: 50] "Retaining rings... were inspected for discoloration caused by arcing... Overall condition of retaining rings is satisfactory. No visible defects observed." [PRISM Data] ADJ_RISK (Rotor): 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk; ADJ_RISK (Stator): 0.11274547703635862, RISK_PROFILE: Stator Low Risk.
Contamination | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 48] 'During the initial borescope inspection, a significant amount of dust and debris was observed within the generator core... this contamination was determined to have originated internally.' [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 194] 'We did see a decrease in the IR/PI values... The next few tests saw the IR/PI values recover and is in satisfactory condition for return to service.' | [FSR File: Field_Service_Report_ProjectID_A-1561864_EV-118524_C-10357248.pdf] [Page: 600] "The following electrical tests were performed on the Field: â€¢ Winding (copper) resistance DLRO â€¢ AC Impedance â€¢ 500V Megger/PI The results of these tests were satisfactory." | [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 29] 'The field body was covered with a light film of oil.' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 6] 'The generator was contaminated with oil... The field winding PI was below our minimum recommended value. Heat should be applied to the collector rings...' [FSR File: 49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 22] 'Air or Hydrogen Surface Coolers Free of Contanination U... The generator was contaminated with oil. Two coolers were removed and a third party vendor vacuumed the oil out of the cooler cavity.' | [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 48] 'The collector end of the generator was disassembled as part of the MAGIC inspection.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 48] 'Oil deflectors were cleaned and inspected. No major issues were found.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 49] 'Fan blades were cleaned and NDE performed... No issues were noted.' [FSR File: 337X305 2022-11-18 Robotic.pdf] [Page: 49] 'The end shield was cleaned and inspected. No defects were noted.' | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] 'The field body was inspected for oil contamination, rust, or mechanical damage... The field body presented a very thin layer of oil film on the TE and CE... Despite the excessive evidence of humidity, the overall condition of field body resulted satisfactory.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Pages: 634-635] 'UNIT GT1 338X380 01/17/22' (date/context marker). | [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 23] 'Carbon dust and rust on the surface, heavy carbon in holes.' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 24] 'Very rusty in the area, normal wear marks, and mechanical damage visible.' [337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 28] 'Heavy deflector seal riding and rust all over.' | [FSR File: Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 48] 'NO DETECTED INDICATIONS OUT OF STANDARD.' [FSR File: Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 62] 'NO DETECTED INDICATIONS OUT OF STANDARD.' [PRISM Data] Rotor ADJ_RISK: 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk
FOD (Foreign Object Damage) | [Field_Service_Report_ProjectID_A-1813284_EV-147582_EVP-534570.pdf] [Page: 174] "Borescope inspection... found dust accumulation... The dust is originating from the stator wedges... No mechanical or thermal stress was observed... Visually the field end turns are in acceptable condition for return to service." [IBAT Data] No IBAT data found. [Contract Data] No contract data found. [PRISM Data] No PRISM data available. |  | [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 7] 'Field End Turns Borescope Inspection No Problem Areas Found' and 'Field Body Borescope Inspection No Problem Areas Found' ¦ [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 28] 'No indications of any unusual deposits or mechanical damage were found... The field was covered with a light film of oil.' and 'The vent holes were clean but several holes were partially obstructed by creepage block and wedge movement.' ¦ [49354_03_30_2022_14_57_44_6XED3BIFWK5MB4N5.pdf] [Page: 29] Field checklist shows 'Foreign Material S' and 'Internal Cleanliness U.' | [337X305 2022-11-18 Robotic.pdf] [Page: 48] "Oil deflectors were cleaned and inspected. No major issues were found." [337X305 2022-11-18 Robotic.pdf] [Page: 131] "Location Oil Deflector Journal Clearance... Satisfactory No Repair Necessary". [337X305 2022-11-18 Robotic.pdf] [Page: 133] "3.5 Generator T&I... Stator End Winding Assembly... Bump test results showed no issues" (stator-focused). [337X305 2022-11-18 Robotic.pdf] [Page: 305] "Inspection Details... Date 22 09 2022" | [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 4] 'This report describes and documents the borescope examination ... with respect to abnormal depositing, foreign object damage (FOD) and normal wear.' [Field_Service_Report_ProjectID_A-1376620_FSP-278367_C-10344197.pdf] [Page: 622] 'The field body was inspected for ... mechanical damage. ... No mechanical damage was found during this inspection.' [337X380 2014-07-16 Robotic.pdf] [Page: 8] 'foreign objects, specially looking for cracks or damages.' | [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 24] "Very rusty in the area, normal wear marks, and mechanical damage visible." [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 25] "Visible seal riding, minor rust, surface scratches, very heavy wear on the most O/B area." [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 23] "Both Collector Rings have concave wear very visible, the O/B ring has more wear than the I/B." [FSR File: 337X704 2016-03-14 Dallas Shop - Full Field Rewind Existing Copper.pdf] [Page: 28] "Heavy deflector seal riding and rust all over." | [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 62] 'NO DETECTED INDICATIONS OUT OF STANDARD.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 66] 'NO DETECTED INDICATIONS OUT OF STANDARD.' [Field_Service_Report_ProjectID_A-1632720_EV-118196_C-10357780.pdf] [Page: 68] 'NO DETECTED INDICATIONS OUT OF STANDARD.' [PRISM Data] 'ADJ_RISK: 0.35417130941121944, RISK_PROFILE: Rotor Medium Risk' [IBAT Data] 'No IBAT data found' [Contract Data] 'No contract data found'