## Sheet1
equipment_type | technology_group | technology | component | Persona | issue_grouping | issue_name | issue_prompt | severity_criteria_0_no_data | severity_criteria_1_light | severity_criteria_2_medium | severity_criteria_3_heavy | severity_criteria_4_immediate | applicable_data_objects
GEN | Hydrogen Cooled |  | Rotor | REL | Electrical Tests | IR, PI | Are there any valid Insulation Resistance (IR), Polarization Index (PI) test results? If yes, please classify per the FM Severity criteria. Note: For IR results, only use 10 min. | No Results / Test Not Performed | IR > 4000 Mega-ohm AND PI > 1 | 4000 Mohm > X > 25 Mega-ohm AND PI > 1 | IR < 25 Mega-ohm OR PI ≤ 1 | IR = 0 OR Could not hold voltage OR field is grounded | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Electrical Tests | Winding resistance | Are there any valid Winding resistance test results? If yes, please classify the results per the FM Severity criteria. | No Results / Test Not Performed | within +/-2% factory test result OR within +/-1% previous test result | n/a | outside +/-2% factory test result OR outside +/-1% previous test result. | Open Circuit | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Shorted Turns | RSO (Recurrent Surge Oscilliograph) | Are there any Recurrent Surge Oscilliograph (RSO) test results? If yes, please classify the results per the FM Severity criteria. | No Results / Test Not Performed | No evidence of shorted turns. | Evidence of shorted turns | n/a | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Shorted Turns | Gen Field Excitation Fleet | What is the Excitation Delta Max Val Ratio for this unit? | No Data | Excitation Delta Max Val Ratio < 1.01 | 1.01 < Excitation Delta Max Val Ratio < 1.05 | Excitation Delta Max Val Ratio > 1.05 |  | ACP Analytic, Time Series Data
GEN | Hydrogen Cooled |  | Rotor | REL | Shorted Turns | Flux probe | Are there any flux probe test results, or definitive statements about the presence of shorts or shorted turns? If yes, please classify the results per the FM Severity criteria. Percent of shorted turns is the ratio of shorted turns per total turns. | No Results / Test Not Performed | 0 Shorts | < 5% of turns shorted | > 5% of turns shorted |  | FSR, ER, LES Reports
GEN | Hydrogen Cooled |  | Rotor | REL |  | Vibration | Does the unit exhibit signs of thermal sensitivity? | no data | <3 mils AND no signs of thermal sensitivity (< 1 mil variation with excitation current and steady MW) | 1-3mils AND >1 mil variation with excitation current and steady MW (derived from GER3809). | 3mils-6mils AND >1 mil variation with excitation current and steady MW (derived from GER3809). Determined thermally sensitive (from test instruction 503HA212) | ≥ Alarm limits (> 6 mils steady state or >7.5 or 9 mils transient, depending on unit) | Time Series Data
GEN | Hydrogen Cooled |  | Rotor | REL |  | Thermal Sensitivity Test | Was a thermal sensitivity test performed? If yes, please classify the results per the FM Severity criteria. | No Results / Test Not Performed | Pass | n/a | Fail |  | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | Ventilation hole blocking (migration of slot components) | Was this unit evaluated for ventilation hole blocking or migration? | Not mentioned at all or not inspected | minor migration AND ventilation hole blocking OR a definitive statement of no migration or ventillation hole blocking | moderate migration AND ventilation hole blocking | Severe or extensive migration AND ventilation hole blocking | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | Turn to turn insulation migration | Was this unit evaluated for signs of turn to turn insulation migration? | Not mentioned at all or not inspected | definitive statement of no migration | Any observations | Noted as severe or heavy, OR > 5 pieces migrated | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | Slot armour migration/damage/cracking | Was this unit evaluated for signs of slot armour migration or damage or cracking? | Not mentioned at all or not inspected | definitive statement of no migration | evidence of slot armor fatigue or movement | Evidence of cracking or significant movement. Signs of shortened creepage distance to ground. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | EW support blocking migration (end winding) | Was this unit evaluated for any signs of End Winding (EW) support blocking migration? | Not mentioned at all or not inspected | definitive statement of no migration | evidence of migration | Blocks missing or signifcantly moved. Noted as heavy or severe. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | MTS leaves cracking/distortion (Main Terminal Stud aka goose neck) | Was this unit evaluated for any Main Terminal Stud (MTS) distortion or any MTS leaves cracked? | Not mentioned at all or not inspected | definitive statement of no cracking or distortion OR cracking or distortion noted on ≤ 2 leaves | Cracking or distortion noted in 3 or 4 leaves | Cracking or distrotion noted on ≥ 5 leaves. | Over half the package cracked. | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | MTS/bore copper contact (Main Terminal Stud aka goose neck) | Was this unit evaluated for any signs of contact or rubbing between the bore copper and the Main Terminal Stud (MTS)? This would include any copper dust or flakes present where the MTS screws into the forging. | Not mentioned at all or not inspected | Definitive statement of no signs of MTS contacting the bore copper | n/a | Observed or Copper dust or flakes present where the MTS screws into the forging. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | Pole to pole connector cracking/distortion | Was this unit evaluated for any signs of pole to pole connector cracking or distortion? | Not mentioned at all or not inspected | Signs of distortion or fatigue, but no cracks or minor cracks OR a definitive statement of no damage. | Flexible connector that has one or two leaves cracked all the way through (also called laminations) | Flexible connector with more than 2 leaves cracked all the way through , OR a solid connector that is partially cracked | A solid connector cracked all the way through, OR a flexible connector with the majority of leaves cracked all the way through | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | Coil to coil connection cracking/distortion | Was this unit evaluated for any signs of coil to coil connector cracking or distortion? | Not mentioned at all or not inspected | Signs of distortion or fatigue, but no cracks or minor cracks OR a definitive statement of no damage. | Flexible connector that has one or two leaves cracked all the way through (also called laminations) | Flexible connector with more than 2 leaves cracked all the way through , OR a solid connector that is partially cracked | A solid connector cracked all the way through, OR a flexible connector with the majority of leaves cracked all the way through | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | EW distortion | Was this unit evaluated for any signs of End Winding (EW) distortion in the coil or copper? Distortion of insulation should be ignored. | Not mentioned at all or not inspected | no distortion | Minor distortion | Extensive or heavy distortion noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | Retaining ring insulation damage | Was this unit evaluated for retaining ring insulation damage? | Not mentioned at all or not inspected | no damage | Minor damage | Extensive or heavy damage noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | Contamination | Was this unit evaluated for signs of contamination? | Not mentioned at all or not inspected | light contamination noted OR a definitive statement of no contamination | Medium or unquantified contamination | Extensive or heavy contamination noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | FOD (Foreign Object Damage) | Was this unit evaluated for Foreign Object Damage (FOD) indications? | Not mentioned at all or not inspected | Light or minor FOD damage OR a definitive statement of no FOD | Medium or unquantified FOD damage | Extensive or heavy FOD damage noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | DC leakage | Is there an issue with stator winding DC leakage test results? | not performed or not mentioned | Zone A | Zone B | Zone C for more than 1 phase | Zone C for 1 phase only | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | DC Hipot (Optional/rare, and Secondary to DC Leakage) | Were DC Hipot measurements taken, and if so what were the results? | not performed or not mentioned | Zone A | Zone B | Zone C for more than 1 phase | Zone C for 1 phase only | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | IR, PI | Is there an issue with the insulation resistance and/or the polarization index test (IR, PI Test) results? | not performed or not mentioned | Pass | Decreasing Trend or close to the limit | Fail for more than 1 phase | Fail for exactly 1 phase | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | Winding resistance | Is there an issue with the winding resistance test? | not performed or not mentioned | Pass All Rules | Pass Rule 1, but Fail 2 and/or 3/4. | n/a | Fail Rule 1 | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Corona | Slot Corona Activity (Can see in end of slots only) | Is there any corona damage in the slot area? | Slot Corona activity is not mentioned | Slot Corona activity is observed as light or definitive statement of not present | Slot Corona activity is observed as medium / moderate / average / observed but unquantified | Slot corona activity is stated as heavy |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Corona | End winding Corona Activity | Is there any corona damage in the end winding area? | Not mentioned | stated as light or definitive statement of not present | Observed | Stated as Heavy |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | Dusting or Greasing at the ends of the stator slots. | Is there moderate to heavy greasing or dusting at the ends of the stator slots? | Not mentioned | stated as minor/light or definitive statement of not present | Stated as medium or moderate. Mentioned but not called light / minor. AND DC Leakage is still zone A | Stated as Heavy or major or extreme. Notes Side Ripple Spring (SRS) digging into bar. OR Mentioned and DC leakage is zone B or C |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | Connection Ring (CR) dusting or greasing | Is there moderate to heavy greasing or dusting at connection ring (CR)? | Not mentioned | definitive statement of not present or noted as light or cleaning and application of red eye epoxy | Needs to be cleaned and replacement of ties (or wet ties) | Clean, remove ties, remove blocks, and fix insulation |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | End Winding (EW) dusting or greasing | Is there moderate to heavy greasing or dusting at End winding (EW)? | Not mentioned | definitive statement of not present or noted as light or cleaning and application of red eye epoxy | Needs to be cleaned and replacement of ties (or wet ties) | Clean, remove ties, remove blocks, and fix insulation | unrepaired damage to bar insulation or temporary repair | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | Oil ingress | Is there greasing present? | Not mentioned. | oil or greasing noted, and stated as light. OR Dusting mentioned but no mention of greasing. | Oil or Greasing noted, but stated as moderate or not quantified. | Heavy oil ingress noted. Mention of oil in bushings. Phrases like "pools of oil" or "heavily soaked with oil" or "Pockets of oil". Liquid level detector or belly alarm. |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Stator slot wedge tightness | Is there any indication of stator slot wedge looseness or are there any stator slot wedge assessment results? | Not mentioned | Pass | Fail - Partial rewedge or wedge tightening or shimming | Fail - Full rewedge |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Winding Connection Failure (Phase Connection /Series Loop) | Are there any indications of winding connection failure? specifically Coil to Connection Ring or Coil to Coil | Not mentioned | Not present, no indication, pass copper resistance test, no M&D alarm | n/a | Any form of detection. Failed Copper resistance, M&D alarm, or visual observation. Greasing coming out of hand applied tape at phase connection. |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Stator core looseness (or low tightness, not tight) | Are there any signs of stator core looseness or any knife test results? | not mentioned | Pass | n/a | Fail. Loosness present in any form. | Damage to Core Laminations | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | High Stator Bar Temps | Has the unit had ER cases related to elevated bar temperatures as observed by analytics RTDs? Or is there any indication for high stator bar temperatures? | not mentioned | Temps below limit and steady (as a function of ambient & load, i.e. trending w/ Hot gas and cold gas temps) | One RTD showing elevated compared to others, or entire machine trending higher | Above limit |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Ventilation duct blocking | Are there any signs of ventilation blocking? | not mentioned | Not present | Present but not causing temperature increase | Noted as heavy, or presence of increased bar temps |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Stator core burning | Are there signs of stator core burning? | not mentioned | Not present | n/a | Observed in any way |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Shorted Strand in stator bar | Were any shorted strands in the stator bar observed? | not mentioned | Not present | n/a | Observed in any way |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Reversed fan blades | Are there signs of reversed fan blades such as vibrations or fan Differential Pressure (DP or FDP) alarm? | not mentioned | Not present | n/a | n/a | Observed in any way | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Stator Frame Vibrations | Are there signs of stator frame vibrations? | not mentioned | Not present | Present but below alarm limits | Above alarm limits or impacting unit operations |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Noisy during operation (Unit noisy) or Red Oxide Dust inside core | Has the unit failed a harmonic noise index (HNI) test? In other words is the unit noisy during operation or is there red oxide dust inside the core? | not mentioned | Not present | Present but passing HNI test | Failing HNI test | Heavy Red Oxide dust or Heavy Noise and no HNI test | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Inside Space Block (ISSB) or Outside Space Block (OSSB) migration | Were there any signs of Inside Space Block (ISSB) or Outside Space Block (OSSB) migration? | not mentioned | Not Present | Present and noted as minor | Noted as major or heavy, or already cutting into the stator bar insulation |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Contamination | Is there signs of sand, dirt, carbon dust, or lead? | Not present | Noted as light | Noted as medium | Noted as heavy, or any mention of lead contamination |  | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Foreign Object Damage (FOD) | Is there damage by a foreign object (FOD)? | not present | noted as light / minor | Described as medium | Described as heavy or major or severe |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Collector Ring Repairs / Replacement | Are there any signs of collector ring issues, such as excessive or uneven brush wear, arcing, flashing, foot printing, or dimensional checks out-of-spec? Any mention of dishing or issues with the run-out measurements? Any recommendations for Collector Ring machining? | Not mentined | Definitive statement of no findings OR Symptoms noted as light or acceptable. | Symptoms noted, but not quantified OR suggested to address at a future outage. | Symptoms stated as heavy or extreme, OR a recommendation to address it now or at first opportunity. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Collector Assembly / Brush Rigging | Are there any indications of uneven brush wear, loose or mis-aligned brush holders, or damaged collector springbacks? | Not mentined | Definitive statement of no findings OR Symptoms noted as light or acceptable. | Symptoms noted, but not quantified OR suggested to address at a future outage. | Symptoms stated as heavy or extreme, OR a recommendation to address it now or at first opportunity. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Grounding Brushes | Are there any signs of uneven wearing or improper rotor contact of grounding brushes? | Not mentined | Definitive statement of no findings OR Symptoms noted as light or acceptable. | Symptoms noted, but not quantified OR suggested to address at a future outage. | Symptoms stated as heavy or extreme, OR a recommendation to address it now or at first opportunity. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Collector Stud Repair / Tightening | Are there any signs of unaddressed hydrogen leaks, or any recommendations to tighten the collector stud? Was the work completed as recommended? |  | Definitive statement of no findings OR Previous recommendation to tighten the collector stud with evidence that it was perfomed. | Previous recommendation to tight the collector stud without evidence that it was performed. | Evidence of a hydrogen leak or alarm since last outage. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Hydrogen / Scavenging System Maintenance | Are there any signs of hydrogen purity issues or increased hydrogen consumption? | No mention of hydrogen purity | >95% purity | Purity is > 75% buy < 95% | < 75% H2 purity |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Hydrogen Seal Repair or Upgrade | Is there any mention of damage to, repair of, or replacement of hydrogen seals or hydrogen casings? | No mention of hydrogen seal/case repair, replacement, or damage. | Cleaning needed OR observations noted as minor OR a recommendation to repair or replace that has been completed. | indications of scoring, pitting, or damage that can be repaired. | Observations that lead to a recommendation to replace. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Bearings | Any issues with Bearing vibrations or Bearing metal temps? | No mention of bearings. | Definitive statement that the bearings are ok or good condition. | Any recommendation to inspect the bearing or babbet OR Any maintaned bearing metal temps > 225 F OR Any vibrations > 6 mils or a step change in vibrations more than 1 mil increase | Any recommendations to repair or replace a bearing or to rebabbet OR Any bearing metal temps above alarm limit (> 250 F) OR Any vibrations > 9 mils |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Bearing Oil deflectors | Are there signs of oil ingress on this unit or visiual indications of damage on the oil deflectors. | No mention of the Oil deflectors OR oil ingress. | recommendations to clean oil deflectors OR minor oil ingress | recommendations to repair the oil deflectors OR moderate oil ingress | recommendations to replace the oil deflectors OR severe oil ingress |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Stator RTD Test | Is there any evidence of failing the stator RTD test? | No mention of RTD test | Pass | n/a | Fail |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | High Voltage Bushings | Any issues with the visual inspection of High Voltage Bushings (HVB) or Stand-off Insulators (SOI), such as insulation degredation, oil leaks, or cracked/chipped porcelin? | No mention of HVB inspection. | Definitive statement of no issues with the HVB or stand-off insulator (SOI). | Any observations of oil leakage, cracking, cracked/chipped porcelin, or damaged insulation OR recommendations to address or repair at next outage. | Any observations quantified as serious, major, or severe OR recommendations to replace at next outage. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Hydrogen Coolers | Is there any evidence of a visual inspection or test of the hydrogen coolers? If yes, please classify per the severity criteria. | No mention of Hydrogen Coolers. | Definitive statement of no issues with the Hydrogen coolers. | Recommendations to clean or inspect the hydrogen coolers | Recommendations to do repairs or replacements to hydrogen coolers OR mention of leaks or corrosion or damage in hydrogen coolers or cooling fins OR failed test of the hydrogen coolers. |  | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Excitation System / LCI | Are there any issues noted with the excitation system or Load Cummulative Inverter (LCI) or Static Start? | Not mentioned | Definitive statement of one or more of these systems having no issues OR mention of a EX2100e. | Any recommendations to upgrade to EX2100e OR mention of a EX2000. | Recommendations to upgrade board or hardware for any of these systems OR statement of obsolete hardware. |  | FSR, ER
GT | 7F |  | Bearings | OE |  | Journal Bearing Issues | Was this unit evaluated for signs of journal bearing issues? |  | No mention of journal bearings. | Definitive statement that the journal bearings are ok or in good condition. | Any unfulfilled recommendation to inspect the bearing or babbet OR Any maintaned bearing metal temps > 240 F OR Any vibrations > 6 mils or a step change in vibrations more than 1 mil increase or observation of SHAFT CENTER LINE POSITIONING SHIFT | Any unfulfilled recommendations to repair or replace a bearing or to rebabbet OR Any bearing metal temps above alarm limit (> 260 F) OR Any vibrations > 7.5 mils | FSR, ER
GT | 7F |  | Bearings | OE |  | Bearing Vibration Issues | Was this unit evaluated for signs of bearing issues? |  | No mention of bearing vibration. | Definitive statement that the bearing vibrations are within limit | Evidence of bearing vibration spikes or step changes of vibration > 0.1 | Evidence of bearing vibration that exceeds M&D limits or high vibrations in critical speed zones | FSR, ER
GT | 7F |  | Bearings | OE |  | Bearing Condition | Was this unit evaluated for signs of bearing condition? |  | No mention of bearing condition. | Definitive statement that bearings are in good condition | Evidence of pad scoring | Evidence of bearing wipe | FSR, ER
GT | 7F |  | Bearings | OE |  | Bearing Lube oil pump leaks | Was this unit evaluated for signs of bearing lube oil pump leak? |  | No mention of bearing lube oil pump leaks | Definitive statement that there are no bearing lube oil pump leak |  | Evidence of bearing lube oil pump leak | FSR, ER
GT | 7F |  | Bearings | OE |  | Bearing Oil contamination | Was this unit evaluated for signs of bearing lube oil contamination? |  | no mention of bearing oil contamination | Definitive statement that there is no lube oil contamination |  | Evidence of lube oil contamination or alarm | FSR, ER
GT | 7F |  | CBV | OE |  | Compressor Bleed Valve maintenance | Was maintanenance performed on the compressor bleed valves (CBV)? |  | No mention of compressor bleed valve maintenance | Definitive statement that compressor bleed valve maintenance was performed |  | no mention of compressor bleed valves (CBV) preventative maintenance being performed | FSR, ER
GT | 7F |  | CBV | OE |  | Compressor Bleed Valve (CBV) trips | Was this unit evaluated for signs of compressor bleed valve (CBV) trips? |  | no mention of compressor bleed valve trips | Definitive statement of no compressor bleed valve trips | Evidence of 1 compressor bleed valve trip | Evidence of 2 or more compressor bleed valve trips | FSR, ER
GT | 7F |  | CBV | OE |  | Compressor Bleed Valve (CBV) operability | Was this unit evaluated for signs of compressor bleed valve (CBV) failure to open or close? |  | no mention of compressor bleed valve failing to indicate open or close | Definitive statement that the CBV's are ok or in good condition. |  | Evidence of compressor bleed valves failed to indicate open or closed | FSR, ER
GT | 7F |  | CBV | OE |  | Compressor Bleed Valve (CBV) response times | Was this unit evaluated for signs of compressor bleed valve (CBV) response times? |  | no mention of compressor bleed valve response times | Evidence of compressor bleed valve response times less than 5 seconds | Evidence of compressor bleed valve response times greater than 5 seconds OR a conditional recommendation to replace, repair, or refurbish CBV | Evidence of compressor bleed valve response times greater than 7.5 seconds OR a definitive recommendation to replace, repair or refurbish CBV | FSR, ER
GT | 7F |  | Bearings | OE |  | Journal Bearing Proximity Vibration | Was the unit evaluated for bearing amplitudes? |  | bearing amplitude data not available |  | bearing amplitude > 6 | bearing amplitude > 7.5 | Time Series Data, ER
GT | 7F |  | Bearings | OE |  | Journal Bearing Seismic Vibration | Was the unit evaluated for bearing vibration sensor? |  | bearing vibration data not available |  | vibration sensor > 0.50 | vibration sensor > 0.65 | Time Series Data, ER
GT | 7F |  | Bearings | OE |  | Journal Bearing Lube Oil (Header) Temperature | was the unit evaluated for lube oil header temperature? |  | lube oil header temperature data not available |  | lube oil header temperature > 150 | lube oil header temperature > 164 | Time Series Data, ER
GT | 7F |  | Bearings | OE |  | Journal Bearing Lube Oil Drain Temperature | was the unit evaluated for journal bearing drain temperature? |  | journal bearing drain temperature data not available |  | journal bearing drain temperature > 180 | journal bearing drain temperature > 200 | Time Series Data, ER
GT | 7F |  | Bearings | OE |  | Journal Bearing Metal Temperature | Was the unit evaluated for bearing metal temp? |  | bearing metal temperature data not available |  | bearing metal temp > 240 | bearing metal temp > 260 | Time Series Data, ER
GT | 7F |  | Compressor | REL |  | S17 Bushing Migration | Are there any signs of stage 17 Stator vane (S17) bushing wear, bushing migration? Are there any other signs of damage such as fretting of the Stage 17 shroud? |  | No Data | Definitive statement of typical or good condition of compressor S17 bushings or compressor S17 shrouds. Note: Typical condition can include observations like rocking, wear or fretting that is not quantified as heavy or severe. | An observation of wear or migration on single compressor S17 bushing AND no mention of clashing. | An observation of wear or migration on multiple compressor S17 bushing AND no mention of clashing. | FSR, ER
GT | 7F |  | Compressor | REL |  | S17 Replacement | were S17 stators replaced ? Which version Dwg No. Implemented ? |  | No Data | Definitive statement of compressor S17 stators replacementnt or upgrade | Definitive statement of full set of compressor S17 stators replacementnt or upgrade | n/a | FSR, ER
GT | 7F |  | Compressor | REL |  | Stator Replacements in other stages | were any of stage S## (0-16) stators replaced ? Which version Dwg No. Implemented ? |  | No Data | Definitive statement of S## compressor stators replacement or upgrade | Definitive statement of full set of S## compressor stators replacement or upgrade. Note: Part numbers that include "L" are kit level (i.e. full set). | n/a | FSR, ER