## FSR Tagging Gaps
Train ID | Plant Name | Tagged ESN | Tagged Equipment Type | Missing ESN | Missing Equipment Type | PDF Name | Document ID | Report Issued Date | Matched Event Date | Event Type | Sibling Event Type | Sibling Event ID | Field Scope | Days After Event | Gap Confirmed | Keyword Matches | Keywords Found | Sample Excerpt
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1899952_EV-172118_EVP-547693.pdf | 659b6e3f-4314-4cbb-a46d-1d335a4d020d | 2024-12-09 | 2024-10-18 | Call-Out |  |  | TA & Craft Labor | 52 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1867240_EV-165331_C-10379632_EVP-542904.pdf | e134daab-3391-42b7-baf6-9ba0948d6208 | 2024-04-11 | 2024-03-26 | Call-Out |  |  | TA & Craft Labor | 16 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1716886_EV-131375_C-10368867.pdf | dff0e1ca-a0ba-4e15-b0e1-caa0bace15cc | 2022-04-18 | 2022-03-15 | Call-Out |  |  | None | 34 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1719162_EV-131794.pdf | d2d10cb3-0b9e-4d68-910c-b30b9ecd68c0 | 2022-03-30 | 2022-03-15 | Call-Out |  |  | None | 15 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1677892_EV-116598_C-10363565.pdf | 418f5be8-6bd7-4841-8f5b-e86bd7f841bf | 2021-12-06 | 2021-11-29 | Call-Out |  |  | TA & Craft Labor | 7 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1694146_FSP-314939_C-10366370.pdf | 23c728ac-ebd2-4a50-8728-acebd22a502c | 2021-10-13 | 2021-10-04 | Call-Out |  |  | TA & Craft Labor | 9 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1627558_FSP-298093_C-10353008.pdf | 0398371c-704c-4e8f-9837-1c704c3e8f52 | 2021-02-12 | 2021-01-23 | Call-Out |  |  | TA & Craft Labor | 20 | NO | 0
UNI235470 | Ninemile Point | 299140 | Gas Turbine | 337X474 | Generator | Field_Service_Report_ProjectID_A-1617124_FSP-295687_C-10351294.pdf | 0ff5747b-dbc9-4e6a-b574-7bdbc9ae6a99 |  | 2021-01-23 | Call-Out |  |  | TA & Craft Labor | 5 | NO | 1 | Retaining Rings | . GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the The S16 vanes that were inspected along the lower half of the unit contain signs of twisting (.030”) on the base of the vanes. A small gap (.115”) was also observed at the left horizontal joint. The R17 blades that were inspected contain a minor nick on the leading edge side of one blade. The S17 vanes that were
UNI067472 | Tihama-1 Rastanura Site | 298490 | Gas Turbine | 436X023 | Generator | Field_Service_Report_ProjectID_A-1974178_EV-187575_EVP-557243.pdf | 827c924a-ec64-47ae-9ce1-af83bf6f046c | 2026-01-15 | 2025-10-31 | Large Call-Out |  |  | TA & Craft Labor | 76 | NO | 1 | Greasing | Next Outage • Check for IGV inner bushing migration and keep spares in stock of inner bushing - outer bushing - thrust washers - spring washers. • Greasing of IGV control ring and linkage arm. • It is strongly advised to inspect IGV during next planned outage as per TIL 2363-R1. • It is highly recommended to have a spare set of pinion/rack gears, and Next Outage IGV hardware during next planned Inspection. Part Condition: Fair Part Description: Variable Inlet guide vanes (VIGV) were manually cle
UNI067472 | Tihama-1 Rastanura Site | 298490 | Gas Turbine | 436X023 | Generator | Field_Service_Report_ProjectID_A-1837168_EV-158512_EVP-537872.pdf | 8117b10e-67f9-4fa0-8793-9a849dd2046e | 2024-05-06 | 2024-04-25 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 11 | NO | 0 |  | RTR Tihama GT-2 TSN: 298490 GSN: 436X023 28th April 2024 Prepared BY: Mahmoud Alshammasi 1 1- MCC-1 and MCC-2 Inspection
UNI222464 | SALALAH | 875059 | Gas Turbine | 337X661 | Generator | Field_Service_Report_ProjectID_A-1864364_EV-151236_EVP-542463.pdf | 63fb9b16-7b2d-4485-a531-78c8ea111afb | 2026-03-05 | 2026-02-09 | Combustion Inspection (CI) |  |  | TA & Craft Labor | 24 | NO | 0 |  | End Date: 17 Feb 2026 ESN/SY: 875059 ¦ SY0343621 Generator Field Serial Number: 337X661 Oracle Project ID: A-1864364 ¦ EV-151236 ¦ EVP-542463 Report Issued: 05 Mar 202
UNI222464 | SALALAH | 875059 | Gas Turbine | 337X661 | Generator | Field_Service_Report_ProjectID_A-1372244_FSP-271172_C-10335477.pdf | 4e9a5397-9e8d-4a9b-9a53-979e8daa9b3f | 2021-11-07 | 2021-10-06 | Combustion Inspection (CI) |  |  | TA & Craft Labor | 32 | NO | 1 | Seal Rings | New Floating ring installed on all flow sleeves Installation of the new floating ring on flow sleeves g Combustion Section MS6001F Flow Sleeve - General Inspection Date 8 -10-2021 Turbine S/N 875059 Prepared by Al-Muntaser Al-Ha Photos Enclosed? yes Chamber # S/N # Inspected Defect Code and Location Seal Condition Seal Diameter Disposition 1 Slight wear on the spring seal 428.000 N 2 Slight wear on the spring seal 428.000 N 3 Slight wear on the spring seal 428.000 N 4 Slight wear on the spring s
UNI036579 | OUACHITA GENERATING PLANT | 270T505 | Steam Turbine | 290T505 | Generator | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 439c0fbf-3cf8-4125-93d6-1fa054099053 | 2023-05-16 | 2023-03-09 | Minor Inspection |  |  | TA & Craft Labor | 68 | YES | 27 | Core, DC Leakage, DLRO, End-winding, Fan Blades, Focused Generator Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Wedge Tightness Test, Wedges, Winding Resistance, Winding resistance DLRO, DC Hipot, High Voltage Bushings, Stator Winding, Centering Ring, Collector Rings, MAGIC Inspection, Retaining Rings, Hydrogen Seal Assembly, Greasing, AC Impedance, Gooseneck, Main Lead, Wedge Looseness, End Shield | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 2 1.3 EHS __________ 3 1.4 Quality __________ 12 STEAM TURBINE (270T505 ¦ SY0073340) __________ 13 1 Summary __________ 13 1.1 Steam Turbine Executive Summary __________ 13 1.2 Work Scope __________ 18 2 Technical __________ 20 2.1 TIL/ETC __________ 20 2.2 Recommendations __________ 24 3 Turbine __________ 28 3.1 Bearing __________ 28 GE Power Power Services GEGE
UNI036579 | OUACHITA GENERATING PLANT | 270T505 | Steam Turbine | 290T505 | Generator | Field_Service_Report_ProjectID_A-1684294_FSP-312901_C-10364672.pdf | 6e1fe789-69c4-431c-9fe7-8969c4c31c68 | 2021-10-15 | [6 empty] | NO | 0 |  | t rotating shots 30deg. Coupling ducting was removed to gain access to the HP / Generator coupling. Turning gear was engaged to rotate coupling to bring the correct bala
UNI036579 | OUACHITA GENERATING PLANT | 270T505 | Steam Turbine | 290T505 | Generator | Field_Service_Report_ProjectID_A-1673810_FSP-310296_C-10362656.pdf | 2e6f56e3-6f59-40a8-af56-e36f5900a864 | 2021-07-06 | 2021-05-29 | Call-Out |  |  | TA & Craft Labor | 38 | NO | 0 |  | hts installed as prescribed on HP rotor coupling, then ten weights installed on Generator Field Coupling. All weights and set screws staked into position with no movemen
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1947510_EV-182919_EVP-554033.pdf | f148ee48-fb92-4fa2-95ca-d8b3381508cc | 2026-03-24 | 2026-03-12 | Call-Out |  |  | TA & Craft Labor | 12 | NO | 2 | Wedges, Seal Rings | To support the borescope inspections, the following components or connections were removed and subsequently replaced after work-scope completion: the T1 bearing cavity access plug, the inlet plenum access panel, compressor borescope plugs, CDC borescope plugs, CDM probes, turbine casing inlet bleed heat hard piping segments, and turbine casing borescope plugs/pins. To support inquiries from GEV remote maintenance and development support, fuel gas flexible piping segments to combustion chambers 5
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1925954_EV-177878_EVP-551200.pdf | e1153c63-51ef-4473-b7f9-424382005dc7 | 2025-03-18 | 2025-02-26 | Call-Out |  |  | TA & Craft Labor | 20 | NO | 0
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1892054_EV-170197_EVP-546467.pdf | 223aaef4-0d7a-45d1-842f-8732cf657037 | 2025-03-11 | 2025-02-26 | Call-Out |  |  | TA & Craft Labor | 13 | NO | 1 | Wedges | . The technical data Serial #297842Error! Reference source not found.Error! Reference source not found. Columbia Energy LLCError! Reference source not found. TIL TIL Description Inspected TIL-1582-R2 F and H Class Lift Oil Hose Inspection and Replacement Yes *ETC 257 BORESCOPE INSPECTION REVISION FOR 7FA TRANSITION PIECES Yes TIL-1562-R1 Heavy-Duty Gas Turbine Shim Migration and Loss Yes TIL-1769 F-Class Aft Stator Rocking Inspection Yes TIL-2049-R2 F Class Inlet Guide Vane to rub ring rubbing Y
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1923460_EV-177148_EVP-550776.pdf | ee8095af-60ac-4291-a3bd-8a066abde26b | 2025-02-05 | 2025-01-29 | Call-Out |  |  | TA Only | 7 | NO | 0
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1874836_EV-166972_EVP-544026.pdf | b34b66f5-75ed-45d5-8dfb-8420aed17ac1 | 2024-11-22 | 2024-10-29 | Call-Out |  |  | TA Only | 24 | NO | 0
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1823322_EV-156137_C-10379367_EVP-535976.pdf | 1b3ac24d-3098-4a99-be6a-150c22c99d08 | 2024-04-25 | 2024-04-17 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 8 | NO | 1 | Wedges | . Site can further asses data after BI. GE Vernova Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property of GE and TIL Applicability Table: TIL Title Inspected (YES/NO) TIL-1582-R2 F and H Class Lift Oil Hose Inspection and Replacement YES *ETC 257 BORESCOPE INSPECTION REVISION FOR 7FA TRANSITION PIECES YES *ETC 270 7FA DLN2.6+ PHASE2 CAP EFFUSION PLATE OXIDATION INSP
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1866754_EV-164960_EVP-542737.pdf | a58a9132-c9a1-4585-8086-494ee35959ae | 2024-04-24 | 2024-04-17 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 7 | NO | 0
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1785732_EV-147448_C-10374938.pdf | 2fe3cc7a-cfd2-4356-9ad4-70f067515bc5 | 2023-05-15 | 2023-04-23 | Call-Out |  |  | Craft Labor Only | 22 | NO | 0 |  | OPCUA Communication • NTP Client Settings • FSR1 Transfer from gas to Liquid • Generator Volts Signal • PPDA diagnostics for AC input • Trip on Open Door Power Services
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1777062_EV-145531_C-10373605.pdf | 661cebd6-416f-4271-bb32-30ec6e07948d | 2023-02-02 | 2022-12-02 | Call-Out |  |  | TA & Craft Labor | 62 | NO | 0
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1729768_EV-135280.pdf | c840d605-2c91-4fae-9eea-821868bd16cc | 2022-08-12 | [6 empty] | NO | 0 |  | uired replacing; along with quaternary cleaning required TIL 1724. The attached generator was also in outage for TIL 2260 which provided an opportunity for the work to b
UNI035490 | COLUMBIA | 297842 | Gas Turbine | 338X424 | Generator | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | a2e95baf-9f0d-4ab0-a95b-af9f0dcab0be | 2021-05-31 | 2021-03-24 | Call-Out |  |  | TA & Craft Labor | 68 | YES | 27 | Core, End Shield, End-winding, Greasing, High Voltage Bushings, Keybars, Lamination Damage, Red Eye Repair, Stator Winding, Step Iron, Wedges, Field Body, Turn Insulation Migration, DC Leakage, Focused Generator Inspection, Hydrogen Seal Assembly, Polarization Index, Wedge Tightness Test, Retaining Rings, Amortisseur, MAGIC Inspection, Sub-slots, Wedge Looseness, DC Hipot, AC Impedance, Gooseneck, Main Lead | - 338X424 2.1.1 GT 1 - TIL-2260 Inspection - 338X424 Part Condition: Good Part Description: In accordance with TIL-2260, a borescope inspection was performed on the generator stator Air Gap region with careful attention and focus on finding visual evidence of TE step iron core damage or greasing/red dusting. In addition, the core compression nuts were inspected for visual signs of movement that could indicate a possible loose core. Greasing, that was noted mostly within the CE end wedge/step-iro
UNI048334 | Astoria Energy, LLC | 298936 | Gas Turbine | 338X390 | Generator | Field_Service_Report_ProjectID_A-1993566_EV-189917_EVP-559911.pdf | 32fe3b44-1bb0-45d6-9b99-b9d083fe06f4 | 2026-03-23 | [6 empty] | NO | 0 |  | rt covers the bearing leak for Site Unit "4" SN: 298936. Site has reported that Generator T4 bearing cap was observed to have a small oil leak since the completion of th
UNI048334 | Astoria Energy, LLC | 298936 | Gas Turbine | 338X390 | Generator | Field_Service_Report_ProjectID_A-1790006_EV-148415.pdf | 39346a8c-5601-4eca-b339-4cbd15cc6faf | 2023-05-04 | [6 empty] | NO | 0 |  | No Comment: Customer scope for maintenance of motors bearing Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI048334 | Astoria Energy, LLC | 298936 | Gas Turbine | 338X390 | Generator | Field_Service_Report_ProjectID_A-1731572_EV-132029_C-10372137.pdf | bd6fe43c-74ad-476a-9473-cdf0e0cd7efb | 2023-01-09 | [6 empty] | NO | 0 |  | 91-R1 Date of Disposition: 29 Sep 2022 Recurring: No Comment: Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI048334 | Astoria Energy, LLC | 298936 | Gas Turbine | 338X390 | Generator | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 0080e4b1-00ae-4b5a-80e4-b100aeab5a2e | 2021-04-21 | 2021-03-27 | Hot Gas Path Inspection (HGPI) |  |  | TA & Craft Labor | 25 | YES | 7 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Blue Check, Generator Pressure Test, Seal Rings | . 15.999 15.999 15.999 15.999 CLEARANCE 0.012 0.008 0.009 H2 SEAL SPRING MEASUREMENTS TURBINE END COLL. END UPPER LOWER UPPER LOWER LENGTH (±1/16 in.) WIRE DIA. COIL DIA. GRADIENT (#/in) Testing Data a. Seal Oil Flow G.P.M. b. Hydrogen Pressure P.S.I. c. Unit Speed R.P.M. Scavenging 338X390 Tom Mulvey English - inches 1 2 3 4 5 6 COIL DIA. WIRE DIA. LENGTH ST00066 D316501 Sheet: (a) Rev 0.0 - 10/01/04 GE Energy Proprietary Information D316501 - H2 Seals - As Left -338X390 g Hydrogen Seal Casing
UNI034468 | CENTRAL NUEVO PUERTO | 297011 | Gas Turbine | 337X510 | Generator | Field_Service_Report_ProjectID_A-1758782_EV-141814_C-10372348_EVP-526993.pdf | f9499959-d63e-41b7-a4eb-f3ed5f84e46c | 2023-12-15 | 2023-11-11 | Call-Out |  |  | TA & Craft Labor | 34 | NO | 0 |  | tion, flame stability, combustion dynamics, bearing drain/metal temperature and generator temperature (RTDs). That condition allows the unit to be maintained in a proper
UNI034468 | CENTRAL NUEVO PUERTO | 297011 | Gas Turbine | 337X510 | Generator | Field_Service_Report_ProjectID_A-1755366_EV-141155_C-10372108.pdf | 2a045836-8917-4840-9430-117ea6973452 | 2022-10-11 | 2022-09-26 | Borescope Inspection (BI) |  |  | TA Only | 15 | NO | 0
UNI034468 | CENTRAL NUEVO PUERTO | 297011 | Gas Turbine | 337X510 | Generator | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | bcea7111-b258-4ea3-aa71-11b258bea363 | 2021-10-25 | 2021-09-13 | Hot Gas Path Inspection (HGPI) |  |  | TA & Craft Labor | 42 | YES | 31 | Core, End-winding, Field Body, Focused Generator Inspection, Greasing, High Voltage Bushings, Loose End-winding Blocking, Retaining Rings, Sub-slots, Wedge Tightness Test, Wedges, End Shield, MAGIC Inspection, Step Iron, DC Leakage, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Centering Ring, Collector Rings, Fan Blades, Oil Deflector Alignment, Oil Deflectors, Blue Check, Generator Pressure Test, Seal Rings, Wedge Looseness, DC Hipot, Main Lead, AC Impedance, Gooseneck | . Body wedges did not have visual indications of looseness or damage. No blocked ventilation ducts were found but small pieces of foreign material were observed in some locations. Final Report_GE Generator SN 337X5… 7 High Voltage Bushings: Cracks on terminal insulation tape. End Winding Support System: Hardware. No indications. End Winding Support System: 9 o’clock position axial support. Missing bolt. (9A) End Winding Support System: 9 o’clock position axial support. Loose bolt. (9B) Generator
UNI036868 | SOUTHAVEN | 298003 | Gas Turbine | 338X340 | Generator | Field_Service_Report_ProjectID_A-1976564_EV-188251_EVP-557624.pdf | 9e60fb33-2b0a-4d7c-b3ad-e4513777a353 | 2025-12-05 | 2025-11-14 | Call-Out |  |  | TA & Craft Labor | 21 | NO | 0
UNI036868 | SOUTHAVEN | 298003 | Gas Turbine | 338X340 | Generator | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | faac5572-aaca-4253-9f7e-159bb61e7b41 | 2023-06-13 | 2023-05-07 | Hot Gas Path Inspection (HGPI) | Large Call-Out | 152830 | TA & Craft Labor | 37 | YES | 7 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Greasing, MAGIC Inspection | Outage Type: Planned Outage Turbine Hot Gas Path Inspection Generator Generator Gas Coolers, Bearings, Hydrogen Seals, End Shield(s) Off, Oil Deflectors, Minor (rotor in) 2 Technical
UNI036868 | SOUTHAVEN | 298003 | Gas Turbine | 338X340 | Generator | GAS_TURBINE_INSPECTION_REPORT_Borescope_CDC_-_Blend_Stage_3_Buckets_for_TENNESSEE_VALLEY_AUTHORITY_Southaven_Power_Unit_GT2_Gas_Turbine_298003_2011-10-18 | 090dbba1800ee6cc | 2011-11-15 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X340,270T5 Accessory Gear S/N: Service Type: Office Location: SE CS-MISSISSIPPI FSR#
UNI036868 | SOUTHAVEN | 298003 | Gas Turbine | 338X340 | Generator | GAS_TURBINE_INSPECTION_REPORT_Lube_Oil_Leak_Investigation_for_SOUTHAVEN_POWER_LLC_Southaven_Power_Unit_GT2_Gas_Turbine_298003_2011-10-12 | 090dbba1800ea65e | 2011-10-13 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X340,270T5 Accessory Gear S/N: Service Type: Office Location: SE CS-MISSISSIPPI FSR#
UNI036868 | SOUTHAVEN | 298003 | Gas Turbine | 338X340 | Generator | GAS_TURBINE_INSPECTION_REPORT_Turning_Gear_and_T-1_Lift_Oil_line_Replacements_for_Tennessee_Valley_Authority_SOUTHAVEN_POWER_LLC_Unit_GT2_Gas_Turbine_298003_2010-03-21 | 090dbba1800b041a | 2010-03-31 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X340,270T5 Accessory Gear S/N: Service Type: CONTRACT MAINT Office Location: SE FS-M
UNI076270 | RIYADH PP11 | 299014 | Gas Turbine | 338X600 | Generator | Field_Service_Report_ProjectID_A-1873692_EV-166755_EVP-543865.pdf | ed3e21e4-9b74-4d38-9dae-24d56342b19e | 2024-05-09 | 2024-03-23 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 47 | NO | 0
UNI076270 | RIYADH PP11 | 299014 | Gas Turbine | 338X600 | Generator | Field_Service_Report_ProjectID_A-1745780_EV-138773.pdf | d604a692-01ab-43da-a960-9a4ec055426c | 2023-04-14 | 2023-03-19 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 26 | NO | 0
UNI076270 | RIYADH PP11 | 299014 | Gas Turbine | 338X600 | Generator | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | d4a50ec8-8965-4d24-a50e-c889654d2475 |  | 2020-10-05 | Major Inspection (MI) |  |  | TA & Craft Labor | 0 | YES | 31 | Collector Rings, Core, End Shield, End-winding, Fan Blades, Field Body, Focused Generator Inspection, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance, AC Impedance, Greasing, Main Lead, Pole Jumper, Step Iron, Sub-slots, Red Eye Repair, Seal Rings, Blue Check, Keybars, DLRO, DC Leakage, Flux Probe Resistance, Flux probe resistance | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 3 1.4 Work Scope __________ 8 1.5 Quality __________ 8 2 Technical __________ 9 2.1 Recommendations __________ 9 3 Turbine __________ 10 3.1 Inlet Section __________ 10 3.1.1 T1 Journal Bearing __________ 10 3.1.2 Thrust Bearing __________ 13 3.1.3 Inlet Bellmouth __________ 13 3.1.4 Inlet Guides Vanes __________ 14 3.1.5 Inlet Bleed Heat __________ 18 3.
UNI036492 | Mahkeses Project | 297716 | Gas Turbine | 336X919 | Generator | Field_Service_Report_ProjectID_A-1778352_EV-145944_EVP-529350.pdf | b0c7bb03-0195-4b7e-ac22-2f6fb75dde17 | 2025-06-16 | 2025-04-25 | Call-Out |  |  | TA & Craft Labor | 52 | NO | 0 |  | urneyman millwrights. Flux probe testing was performed by customer E&I team. No generator testing or inspection was performed by One Field Services personnel. TIL 1607 w
UNI036492 | Mahkeses Project | 297716 | Gas Turbine | 336X919 | Generator | Field_Service_Report_ProjectID_A-1901096_EV-172504_EVP-547901.pdf | 0485eef3-c1ed-419a-a0cd-bb0924757dc3 | 2024-11-22 | 2024-10-27 | Call-Out |  |  | TA Only | 26 | NO | 0
UNI036492 | Mahkeses Project | 297716 | Gas Turbine | 336X919 | Generator | Field_Service_Report_ProjectID_A-1668584_EV-117481_C-10362761.pdf | 7f1f452c-4700-4d16-987e-107bc1144eb3 | 2023-06-12 | 2023-05-01 | Call-Out |  |  | TA & Craft Labor | 42 | YES | 7 | Core, Gooseneck, Pole Jumper, End-winding, Stator Winding, Wedges, End Shield | . Cleaning of the end windings is recommended for the major outage in 2024. As found conditions of the stator end windings are documented in the following photos. CE – Floor free of oil P a g e 10 ¦ 29 CE – 6 o’clock, light dusting between the axial support and binding band CE – area of missing paint on bar surfaces P a g e 11 ¦ 29 CE – 8 o’clock, Dusting between axial support and binding band CE – Connection Ring Blocking Good, more areas of missing paint P a g e 12 ¦ 29 CE – Neutral Side Phase
UNI036492 | Mahkeses Project | 297716 | Gas Turbine | 336X919 | Generator | Field_Service_Report_ProjectID_A-1805854_EV-152418.pdf | 878b671e-be5c-4e4d-8b9d-e96c0b8fc91f | 2023-06-12 | 2023-05-01 | Call-Out |  |  | TA & Craft Labor | 42 | NO | 0 |  | LOTO walkdown was performed to verify that the lube oil, hydraulics, fuel gas, generator, starting motor, ratchet motor, C02, spark plugs, and water wash are locked out
UNI036492 | Mahkeses Project | 297716 | Gas Turbine | 336X919 | Generator | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | fab7cef1-3378-49ea-b7ce-f1337839ea2f | 2022-05-22 | 2022-04-06 | Combustion Inspection (CI) |  |  | TA & Craft Labor | 46 | YES | 21 | AC Impedance, End-winding, Greasing, Polarization Index, Wedge Looseness, Wedge Tightness Test, Wedges, Winding Resistance, End Shield, MAGIC Inspection, Step Iron, Gooseneck, Pole Jumper, Retaining Rings, Sub-slots, Turn Insulation Migration, Turn Jumper, DC Leakage, DLRO, DC Hipot, Stator Winding | . The outer sheath on the core ground cable is starting to wear (page 4 of photos). This condition will not affect the operation of the generator as the ground conductor is still intact. The wear is most likely the result of personnel accessing the end winding compartment through the side inspection door. Example photos accompany this report for your inspection and records. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written c
UNI036492 | Mahkeses Project | 297716 | Gas Turbine | 336X919 | Generator | Field_Service_Report_ProjectID_A-1547224_FSP-273296_C-10337483.pdf | 590d2172-66db-4309-8d21-7266db7309c9 | 2021-06-03 | 2021-05-03 | Call-Out | Minor Inspection | 109515 | TA & Craft Labor | 31 | NO | 0 |  | illop GE TFA - GAS TURBINE Phil Torbela GE TFA - CONTROLS Roman Bobnar GE TFA - GENERATOR Jason Lewis GE BORESCOPE SPECIALIST Derek Steele GE APM SUPERINTENDENT Jerry Bo
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1748272_EV-139209_C-10371468.pdf | 1ec8608e-9fc3-4f5f-a889-301b1ed28e6f | 2023-04-12 | 2023-03-25 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 18 | NO | 0
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 64a55dfa-290f-45a5-a78c-65e4bae10a11 | 2023-01-11 | [6 empty] | YES | 32 | AC Impedance, DC Leakage, DLRO, End-winding, Focused Generator Inspection, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Retaining Rings, Sub-slots, Wedge Tightness Test, Wedges, Core, Field Body, Gooseneck, Greasing, Loose End-winding Blocking, Step Iron, High Voltage Bushings, Main Lead, Pole Jumper, Collector Rings, Wedge Looseness, Fan Blades, Hydrogen Seal Assembly, Winding Resistance, Blue Check, Seal Rings, DC Hipot, Stator Winding | . All fuel flex lines were inspected per TIL. All fuel piping was reinstalled see piping for details • Recorded ALL opening / closing clearances. • Steam cleaned compressor cases and visually inspected ALL stator Vanes for damage, the S5,and S14-16 vanes were removed and new vanes were installed per FMI. • Checked stator vane drops at horizontal joints. Performed shim pinning on required drop adjustments. • Removed and replaced both generator lift oil lines. • Removed, visually inspected and mea
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1656884_FSP-305587_C-10358824.pdf | 3ddb8ab4-50e8-4649-9b8a-b450e8e649dd | 2021-07-27 | [6 empty] | NO | 0 |  | ality of the field ground detection and trip that is integral to protecting the generator field in the event of a ground. 3. Recommend replacement of blower fans in powe
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1657440_FSP-305714_C-10358945.pdf | 1acfde27-e545-4f9b-8fde-27e545ff9b39 | 2021-06-09 | [6 empty] | NO | 0
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1662236_FSP-306871_C-10359909.pdf | f354c229-bc82-4c07-94c2-29bc823c0712 | 2021-05-13 | 2021-03-12 | Call-Out |  |  | TA & Craft Labor | 62 | NO | 0 |  | Til #: 1108-R1 Date of Disposition: 13 Mar 2021 Recurring: No Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1626876_FSP-297958_C-10352786.pdf | d381f151-f5a4-4d73-81f1-51f5a48d7332 | 2021-02-25 | 2021-02-03 | Call-Out |  |  | TA & Craft Labor | 22 | NO | 0
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | GAS_TURBINE_INSPECTION_REPORT_Combustion_Turbine_U2_Air_Leak_for_COTTONWOOD_ENERGY_COMPANY_LP_COTTONWOOD_ENERGY_PROJECT_Unit_COTTONWOOD_ENERGY_PROJECT_Gas_Turbine_297866_2011-10-02 | 090dbba1800ed811 | 2011-11-03 | [6 empty] | NO | 0 |  | nic Mark VI/TMR Frame Size: MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 811111,337X78 Accessory Gear S/N: Service Type: TECH DIRECTIO
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1640388_FSP-301823_C-10355859.pdf | c86521b8-de18-4f33-a521-b8de185f33a9 |  | 2020-11-12 | Call-Out |  |  | TA & Craft Labor | 1 | NO | 0
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1589790_FSP-287352_C-10345609.pdf | 1d9be6c8-076f-4179-9be6-c8076f01796c | [7 empty] | NO | 0 |  | Til #: 1108-R1 Date of Disposition: 6 Apr 2020 Recurring: No Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI025979 | COTTONWOOD | 297866 | Gas Turbine | 337X788 | Generator | Field_Service_Report_ProjectID_A-1585118_FSP-286041_C-10345180.pdf | 7e00a2b1-5f67-4c34-80a2-b15f678c3494 | [7 empty] | NO | 0 |  | ummary __________ 2 2 Technical __________ 3 2.1 Recommendations __________ 3 3 Generator __________ 4 3.1 Unit 2 GT EX2100 __________ 4 3.1.1 41DC Contactor __________
UNI035546 | DAHLBERG | 297553 | Gas Turbine | 336X882 | Generator | Field_Service_Report_ProjectID_A-1949122_EV-183027_EVP-554255.pdf | cc96114a-392e-4ad0-a29d-6f8ac5db0263 | 2025-12-18 | 2025-11-13 | Call-Out |  |  | TA & Craft Labor | 35 | NO | 2 | Oil Deflector Alignment, Oil Deflectors | Inspection Type: Visual Part Condition: Fair Part Description: The principal activity of this outage was the replacement of the T1 bearing, as the customer reported overheating during previous operation. The existing bearing was removed and replaced with a refurbished unit. During disassembly of the T1 bearing, it was observed that the oil passages located on the lower half (LH) of the bearing pedestal were obstructed with sealant. The rotor was lifted using a yoke to allow rotation of the old L
UNI035546 | DAHLBERG | 297553 | Gas Turbine | 336X882 | Generator | Field_Service_Report_ProjectID_A-1803824_EV-151495.pdf | 05a8cdff-1bb6-45e5-9801-de020493a0dc | 2023-05-16 | 2023-04-26 | Call-Out |  |  | TA & Craft Labor | 20 | NO | 0
UNI035546 | DAHLBERG | 297553 | Gas Turbine | 336X882 | Generator | Field_Service_Report_ProjectID_A-1725224_EV-132777.pdf | f7859613-ab2a-4f04-9b68-32be01f421f0 | 2022-06-27 | 2022-05-16 | Call-Out |  |  | TA & Craft Labor | 42 | NO | 0 |  | Outage Type: Planned Outage Turbine Turbine Section Generator Turbine Modifications

## Generator Scope Candidates
Train ID | Plant Name | PDF Name | Tagged ESNs | Tagged Equipment Types | Chunk ID | Page | Report Date | Scope Category | Components | Specific Scope | Keyword Count | Technical Keywords | Findings / Results | Reference Codes | Semantic Seed Query | Excerpt
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1947510_EV-182919_EVP-554033.pdf | 297842 | Gas Turbine | 8e9aa2377fddfc90f689eef280c17a1b | 9 | 2026-03-24 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  | ER-20260313-1109, ER-20260318-0080, ER-20260318-0081, ER-20260318-0082 | Focused Generator Review ¦ Wedges ¦ ER-20260313-1109 ¦ ER-20260318-0080 | To support the borescope inspections, the following components or connections were removed and subsequently replaced after work-scope completion: the T1 bearing cavity access plug, the inlet plenum access panel, compressor borescope plugs, CDC borescope plugs, CDM probes, turbine casing inlet bleed heat hard piping segments, and turbine casing borescope plugs/pins. To support inquiries from GEV remote maintenance and development support, fuel gas flexible piping segments to combustion chambers 5
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1947510_EV-182919_EVP-554033.pdf | 297842 | Gas Turbine | 8cde822103105eec66b2d3668348dd29 | 14 | 2026-03-24 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | new seal rings were inspected for manufacturing or handling defects and installed; |  | Focused Generator Review ¦ Seal Rings | Inspection Type: Visual Part Description: Per recommendations from the prior borescope inspection outage report from Spring 2025 (Internal Event A-1925954), the atomizing air flexible piping segment to combustion chamber 13 was removed and replaced with a new component. Additionally, per MND-20260303-1641 the gas fuel flexible piping segments were removed from combustion chambers 5 and 8 to facilitate additional inspections into gas fuel annuli, flexible piping segments, and fuel gas manifolds.
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1947510_EV-182919_EVP-554033.pdf | 297842 | Gas Turbine | 24640df90c67ab5f756fbf601af994e2 | 53 | 2026-03-24 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . Site is recommended to push back the migrated bushings and re-stake before starting the unit. After pushing back, measure the bushing clearance per TIL-2363-R1 to ensure they are within spec limits. If not within spec, site to replace the bushings at the earliest opportunity. - Rubs noted on R0. These rubs were noted in previous EBI also. The unit has enhanced R0 blades. It is unusual to see tip rubs with enhanced R0 blades. Since rubs are identified, site is recommended to perform NDI annuall
UNI067472 | Tihama-1 Rastanura Site | Field_Service_Report_ProjectID_A-1974178_EV-187575_EVP-557243.pdf | 298490 | Gas Turbine | 93b5261b0c5104e021fc78c10a1a3f91 | 17 | 2026-01-15 | Inspection |  | Focused Generator Review | 1 | Greasing | • Greasing of IGV control ring and linkage arm. |  | Focused Generator Review ¦ Greasing | Next Outage • Check for IGV inner bushing migration and keep spares in stock of inner bushing - outer bushing - thrust washers - spring washers. • Greasing of IGV control ring and linkage arm. • It is strongly advised to inspect IGV during next planned outage as per TIL 2363-R1. • It is highly recommended to have a spare set of pinion/rack gears, and Next Outage IGV hardware during next planned Inspection. Part Condition: Fair Part Description: Variable Inlet guide vanes (VIGV) were manually cle
UNI035546 | DAHLBERG | Field_Service_Report_ProjectID_A-1949122_EV-183027_EVP-554255.pdf | 297553 | Gas Turbine | eada101b821ec9c6f0e56a205fcfff41 | 22 | 2025-12-18 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Clearances were recorded on the oil deflectors along the horizontal lines. |  | Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual Part Condition: Fair Part Description: The principal activity of this outage was the replacement of the T1 bearing, as the customer reported overheating during previous operation. The existing bearing was removed and replaced with a refurbished unit. During disassembly of the T1 bearing, it was observed that the oil passages located on the lower half (LH) of the bearing pedestal were obstructed with sealant. The rotor was lifted using a yoke to allow rotation of the old L
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1892054_EV-170197_EVP-546467.pdf | 297842 | Gas Turbine | 4fd4b6338dd6d007c4ae3926f262e7e2 | 38 | 2025-03-11 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . The technical data Serial #297842Error! Reference source not found.Error! Reference source not found. Columbia Energy LLCError! Reference source not found. TIL TIL Description Inspected TIL-1582-R2 F and H Class Lift Oil Hose Inspection and Replacement Yes *ETC 257 BORESCOPE INSPECTION REVISION FOR 7FA TRANSITION PIECES Yes TIL-1562-R1 Heavy-Duty Gas Turbine Shim Migration and Loss Yes TIL-1769 F-Class Aft Stator Rocking Inspection Yes TIL-2049-R2 F Class Inlet Guide Vane to rub ring rubbing Y
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1823322_EV-156137_C-10379367_EVP-535976.pdf | 297842 | Gas Turbine | 4272534aeeb4eac1aa2bc1485edd57e0 | 26 | 2024-04-25 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . Site can further asses data after BI. GE Vernova Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property of GE and TIL Applicability Table: TIL Title Inspected (YES/NO) TIL-1582-R2 F and H Class Lift Oil Hose Inspection and Replacement YES *ETC 257 BORESCOPE INSPECTION REVISION FOR 7FA TRANSITION PIECES YES *ETC 270 7FA DLN2.6+ PHASE2 CAP EFFUSION PLATE OXIDATION INSP
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | cdda6999c2a037efa05a14ac72e49eb8 | 14 | 2023-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Planned Outage Turbine Hot Gas Path Inspection Generator Generator Gas Coolers, Bearings, Hydrogen Seals, End Shield(s) Off, Oil Deflectors, Minor (rotor in) 2 Technical |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Outage Type: Planned Outage Turbine Hot Gas Path Inspection Generator Generator Gas Coolers, Bearings, Hydrogen Seals, End Shield(s) Off, Oil Deflectors, Minor (rotor in) 2 Technical
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 4ba3e320eeeceedd17d2af25c50a1bad | 14 | 2023-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Planned Outage Turbine Hot Gas Path Inspection Generator Generator Gas Coolers, Bearings, Hydrogen Seals, End Shield(s) Off, Oil Deflectors, Minor (rotor in) 2 Technical |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Outage Type: Planned Outage Turbine Hot Gas Path Inspection Generator Generator Gas Coolers, Bearings, Hydrogen Seals, End Shield(s) Off, Oil Deflectors, Minor (rotor in) 2 Technical
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | aaa626b41abed8f58c61559962c136e7 | 161 | 2023-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | The piston seal rings were found with moderate wear and tear; |  | Focused Generator Review ¦ Seal Rings | . There were no indications of issue found during this inspection. These bellows were continued to service for another tour. Viewing inner xfire tubes as found condition Viewing inner xfire tubes as found condition Viewing inner xfire tube retainers as found condition Viewing outer xfire tube as found condition g Combustion MS7001F Crossfire Tube & Retainer Date 5/13/23 Turbine S/N 298003 Prepared by Jimmy Nguyen FSR # Sketches Enclosed? no Photos Enclosed? yes Defect & Location Disposition Defe
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 93643fad7641d79e05c968adf18e448c | 9 | 2023-06-13 | Inspection |  | Focused Generator Review | 1 | Greasing | 1214-R5 BUCKET LOCKWIRE REDESIGN AND DOWEL PIN ASSEMBLY AND INSPECTION PROCEDURE 1397-1R2 DLN 2.0 AND DLN 2.6 COMBUSTION FORWARD CASING INSPECTIONS 1460-2 7FA, 9FA, 7FB, AND 9H GAS TURBINE ENCLOSURE CRANES (MLI-1648) RE- GREASING / STORAGE |  | Focused Generator Review ¦ Greasing | . All applicable TILs, ETCs, and ER cases are conducted according to the recommendations. The details of the workscope for this outage can be found in the inspection sections of this report. The following capital parts (combustion & HGP) were replaced during this outage: Liner Caps (Job# 583424, Dwg#100T7180G009) Liners (Job#583428, Dwg#147E1624G001/2/3) Fuel Nozzles (Job#583426, Dwg#133T6082G0001) TP (Job#583438, Dwg#139E7464G003) S1S (Job#583441, Dwg#135T3557G0001) S1N (Job#626684, Dwg#116E525
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | f9ec606594ab74ec2ff900b281aef041 | 9 | 2023-06-13 | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection |  | FMI F6743G037 | MAGIC Inspection ¦ FMI F6743G037 | This report is to describe the activities of the Hot Gas Path (HGP) on the Gas Turbine ESN 298003 at TVA Southaven Combined Cycle (SCC) Plant. The unit was shut down in the evening of April 30, 2023 and the outage was started the on May 7, 2023. All mechanical works were completed on May 21, 2023 and all the LOTOs were released on May 22, 2023. The unit was started up on May 26, 2023 and reached FSNL without an issue. The breaker was closed and unit was reached baseload on May 26, 2023. An auto-
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 1267da502cfa52cd3208f808614b3f2a | 161 | 2023-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | The piston seal rings were found with moderate wear and tear; |  | Focused Generator Review ¦ Seal Rings | . There were no indications of issue found during this inspection. These bellows were continued to service for another tour. Viewing inner xfire tubes as found condition Viewing inner xfire tubes as found condition Viewing inner xfire tube retainers as found condition Viewing outer xfire tube as found condition g Combustion MS7001F Crossfire Tube & Retainer Date 5/13/23 Turbine S/N 298003 Prepared by Jimmy Nguyen FSR # Sketches Enclosed? no Photos Enclosed? yes Defect & Location Disposition Defe
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 1ced70357096950eef45aef91f4577da | 9 | 2023-06-13 | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection |  | FMI F6743G037 | MAGIC Inspection ¦ FMI F6743G037 | This report is to describe the activities of the Hot Gas Path (HGP) on the Gas Turbine ESN 298003 at TVA Southaven Combined Cycle (SCC) Plant. The unit was shut down in the evening of April 30, 2023 and the outage was started the on May 7, 2023. All mechanical works were completed on May 21, 2023 and all the LOTOs were released on May 22, 2023. The unit was started up on May 26, 2023 and reached FSNL without an issue. The breaker was closed and unit was reached baseload on May 26, 2023. An auto-
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 0ab58c0f8521c928f8640000011abc61 | 9 | 2023-06-13 | Inspection |  | Focused Generator Review | 1 | Greasing | 1214-R5 BUCKET LOCKWIRE REDESIGN AND DOWEL PIN ASSEMBLY AND INSPECTION PROCEDURE 1397-1R2 DLN 2.0 AND DLN 2.6 COMBUSTION FORWARD CASING INSPECTIONS 1460-2 7FA, 9FA, 7FB, AND 9H GAS TURBINE ENCLOSURE CRANES (MLI-1648) RE- GREASING / STORAGE |  | Focused Generator Review ¦ Greasing | . All applicable TILs, ETCs, and ER cases are conducted according to the recommendations. The details of the workscope for this outage can be found in the inspection sections of this report. The following capital parts (combustion & HGP) were replaced during this outage: Liner Caps (Job# 583424, Dwg#100T7180G009) Liners (Job#583428, Dwg#147E1624G001/2/3) Fuel Nozzles (Job#583426, Dwg#133T6082G0001) TP (Job#583438, Dwg#139E7464G003) S1S (Job#583441, Dwg#135T3557G0001) S1N (Job#626684, Dwg#116E525
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 67f4b89b9b1c37ffc61cc56a6e439edd | 163 | 2023-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | The piston seal rings were found with moderate wear and tear; |  | Focused Generator Review ¦ Seal Rings | . The piston seal rings were found with moderate wear and tear; thus, these rings were replaced new parts upon reassembly. Viewing flow sleeve as found condition Viewing flow sleeves as found condiiton Viewing flow sleeve as found condition Viewing flow sleeve hula spring as found condition 3.4.11 Flow Sleeves Viewing flow sleeve with new piston ring installed Viewing flow sleeve with new piston ring installed g Combustion Section MS 7001FA, 7001FA+, 7001FA+e Flow Sleeve - General Inspection (DL
UNI036868 | SOUTHAVEN | Field_Service_Report_ProjectID_A-1427092_EV-120437_C-10349150.pdf | 298003 | Gas Turbine | 0a68105cd1d798ece165deff1cf5f66a | 163 | 2023-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | The piston seal rings were found with moderate wear and tear; |  | Focused Generator Review ¦ Seal Rings | . The piston seal rings were found with moderate wear and tear; thus, these rings were replaced new parts upon reassembly. Viewing flow sleeve as found condition Viewing flow sleeves as found condiiton Viewing flow sleeve as found condition Viewing flow sleeve hula spring as found condition 3.4.11 Flow Sleeves Viewing flow sleeve with new piston ring installed Viewing flow sleeve with new piston ring installed g Combustion Section MS 7001FA, 7001FA+, 7001FA+e Flow Sleeve - General Inspection (DL
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1668584_EV-117481_C-10362761.pdf | 297716 | Gas Turbine | a4a00e555c0eb689a9342fff790c3003 | 260 | 2023-06-12 | Inspection | Field, Stator | Focused Generator Review | 3 | Core, Gooseneck, Pole Jumper | TE – Core Ground – Insulation on cable deteriorating, most likely from personnel access through inspection door P a g e 17 ¦ 29 TE – Floor and Windings free of oil TE – RTD exit conduit, seal intact P a g e 18 ¦ 29 TE – Flange Seal, no prob; No problems observed with the brazed connections on the pole-to-pole jumpers, turn to turn jumpers and gooseneck connections.; CE - Gooseneck Pole #1 – No evidence of thermal or mechanical stress P a g e 21 ¦ 29 CE - Gooseneck Pole 1, sideview, no problems observed.; P a g e 22 ¦ 29 CE - Pole to Pole Jumper #1 Brazed Connections – No evidence of thermal or mechanical stress CE - Pole to Pole Jumper #2 – no problems observed.; P a g e 23 ¦ 29 CE - Gooseneck, Pole #2, no evidence of thermal or mechanical stress CE - Gooseneck, Pole #2, Opposite side, no problems observed. |  | Focused Generator Review ¦ Core ¦ Gooseneck ¦ Pole Jumper | . Cleaning of the end windings is recommended for the major outage in 2024. As found conditions of the stator end windings are documented in the following photos. CE – Floor free of oil P a g e 10 ¦ 29 CE – 6 o’clock, light dusting between the axial support and binding band CE – area of missing paint on bar surfaces P a g e 11 ¦ 29 CE – 8 o’clock, Dusting between axial support and binding band CE – Connection Ring Blocking Good, more areas of missing paint P a g e 12 ¦ 29 CE – Neutral Side Phase
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1668584_EV-117481_C-10362761.pdf | 297716 | Gas Turbine | dd94e4a8316556b64b5aa43bb087762d | 324 | 2023-06-12 | Inspection | Stator | Focused Generator Review | 3 | End-winding, Stator Winding, Wedges | The generator stator winding insulation system is designed to operate with partial discharge, and the gradual degradation of insulation, referred to as “aging”, is a normal process throughout the service life of the insulation system.; December 30, 2023 Serial number 336X919 Number of poles 2 Frequency 60 Number of phases 3 Connection WYE Unit Value or Range Power KVA 112000 Armature Amps A 4686 Armature Volts V 13800 Field Amps A 922 Excitation Volts V 270 Power factor 0 |  | Focused Generator Review ¦ End-winding ¦ Stator Winding ¦ Wedges | . The partial discharge data was collected using a portable ePDA system with the generator at 84.5 MW and 1.1 Mvar. Surface discharges, gap-type discharges and internal discharges were observed in all phases. The maximum PD signal amplitudes (Qmax) were measured for each phase and trended with previous tests. Partial discharge amplitudes have slightly increased in phase A and decreased in phases B and C. The increase in phase A activity can be attributed to an increase in external activity. The
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1668584_EV-117481_C-10362761.pdf | 297716 | Gas Turbine | 6762295bcb9832fa211bdc8a783befa3 | 328 | 2023-06-12 | Inspection | Stator | Focused Generator Review | 1 | End-winding |  | GEK 103566, GEK120950 | Focused Generator Review ¦ End-winding ¦ GEK 103566 ¦ GEK120950 | . As further trending is completed any significant changes in this shape and/or magnitude of the data will be reported as a comparison between the base line data and the data illustrating the change. g GE Page 8 language, in any form or by any means, electronic, mechanical, magnetic, optical, chemical, manual, or otherwise, without GE Power Inspection & Life Extension Services Phase A: PD Activities Phase B: PD Activities Phase C: PD Activities Figure 3 g GE Page 9 language, in any form or by an
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1668584_EV-117481_C-10362761.pdf | 297716 | Gas Turbine | 30020ce0de2c766d8ea8fea33f5c1054 | 248 | 2023-06-12 | Inspection | Stator | Focused Generator Review | 1 | End-winding |  |  | Focused Generator Review ¦ End-winding | . The technical data herein is the property of GE and Section HGP Stage 3 Component Shroud Location Inner Shroud Sub-Location Honeycomb Seal Observation Typical Comments HGP_3_Shroud_Inner_Shroud_Honeycomb_Seal_001.JPG GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the A – Past Component History (Parts In/Out) Unit & Component History Event HGP FO/EBI EBI/HGPI EBI
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1668584_EV-117481_C-10362761.pdf | 297716 | Gas Turbine | 6d5d602898f95b8a5756379117b8b89d | 252 | 2023-06-12 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | The end shields of the generator were not removed for this inspection.; Access to the field end turns was through the filters mounted on the generator end shields.; Access to the area is difficult and will require the removal of the end shields. | ER-20230428-1044 | Focused Generator Review ¦ End Shield ¦ ER-20230428-1044 | . We trust that the content and formatting for this report is satisfactory; however, if you do require any additional information or clarification, please feel free to contact us at any time. At this time, we would like to take the opportunity to thank you for utilizing the services offered by FieldCore Services. Sincerely, FieldCore Services ___________________________ Owen Milburn, AScT Electrical Technologist Lead Generator Specialist P a g e 2 ¦ 29 SCOPE OF WORK / WORK PERFORMED 1) Visual In
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 5a5dbb44c827836509fb0fa8cadbbd07 | 2 | 2023-05-16 | Electrical | Field, Hydrogen Seals, Stator | DLRO; Winding Resistance | 13 | Core, DC Leakage, DLRO, End-winding, Fan Blades, Focused Generator Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Wedge Tightness Test, Wedges, Winding Resistance, Winding resistance DLRO | MINOR INSPECTION - 270T505 ENTERGY ARKANSAS, INC OUACHITA GENERATING PLANT 3.1.1 Journal Bearings __________ 28 3.1.2 Thrust Bearing __________ 44 3.1.3 Oil Deflectors __________ 51 3.2 Rotors __________ 59 3.2.1 HP Rotor Journal T-2 ______; MINOR INSPECTION - 270T505 ENTERGY ARKANSAS, INC OUACHITA GENERATING PLANT 3.4.1 Front / Turning Gear Standard __________ 209 3.4.2 Mid Standard __________ 215 3.4.3 LP T-1 Bearing Standard __________ 222 3.5 Other __________ 227 3.5.1 Turn; MINOR INSPECTION - 270T505 ENTERGY ARKANSAS, INC OUACHITA GENERATING PLANT 4.2.1 Armature Insulation Resistance with Polarization Index (PI) Test __________ 236 4.2.2 Armature Winding Resistance Test (DLRO) __________ 238 4.2.3 DC Leakage T |  | DLRO; Winding Resistance ¦ Core ¦ DC Leakage ¦ DLRO ¦ End-winding ¦ Fan Blades ¦ Focused Generator Inspection | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 2 1.3 EHS __________ 3 1.4 Quality __________ 12 STEAM TURBINE (270T505 ¦ SY0073340) __________ 13 1 Summary __________ 13 1.1 Steam Turbine Executive Summary __________ 13 1.2 Work Scope __________ 18 2 Technical __________ 20 2.1 TIL/ETC __________ 20 2.2 Recommendations __________ 24 3 Turbine __________ 28 3.1 Bearing __________ 28 GE Power Power Services GEGE
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | a01e43b16bc781846afd75e07fa00114 | 327 | 2023-05-16 | Electrical | Stator | Polarization Index; DC Leakage | 8 | Core, DC Hipot, DC Leakage, End-winding, High Voltage Bushings, Polarization Index, Stator Winding, Wedges | Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) ; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In 1 DC Leakage and Partial Discharge testing are optional but high; 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 5 This test does not apply to units with asphalt stator windings, GVPI windings (Global Vacuum Pressure Impregnated) or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds. |  | Polarization Index; DC Leakage ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ High Voltage Bushings ¦ Polarization Index | . Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) Stator Winding Contamination and/or deterioration of insulation X X X 6 X X X DC Leakage Current Stator Winding Contamination and/or deterioration of insulation X X X 6 O 1 X X Endwinding Tightness Check 8 Endwinding support rods Torque measurement X X X X W
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 3141e134910a604585e2d296318519a0 | 333 | 2023-05-16 | Inspection | Field, Stator | Wedge Tightness Test | 8 | Centering Ring, Collector Rings, Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically constructed for normal transient events including 10,000 start/stop cycles.; All structural components removed as part of the rewind (wedges, retaining rings, centering rings, radial fans, axial fan hubs, collector rings, coupling rings, etc.) should also be inspected. |  | Wedge Tightness Test ¦ Centering Ring ¦ Collector Rings ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings | . Compartment (GNAC)  Load Commutated Inverter & Excitation Compartment (LEC)  Medium Voltage Cell (EPE units)  Generator Voltage Transformer Cubicle  Generator Neutral Grounding as part of Cubicle  Bus Auxiliary compartment (BAC)  DC Link Reactor/AC link reactor  ISO Phase Bus Duct (IPBD)  Segregated Bus Duct  Non-Segregated Bus Duct 6 . Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 1dcac2f87445108cadf54e04c3eca2f4 | 325 | 2023-05-16 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 7 | End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Stator Winding, Wedge Tightness Test, Wedges | Partial Discharge 1 Stator Winding Insulation Localized deterioration X X X O 1 O-R 2 O-R 2 Visual Inspection All Visible Components within the End Winding Compartment Cleanliness, foreign material, loose or displaced parts, damage, wear, d |  | Wedge Tightness Test ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings ¦ Hydrogen Seal Assembly ¦ Stator Winding | . FIGURE 2 Example of alternate 32k Generator Inspection and Maintenance Interval Factored or Actual Turbine hours (hrs.) 8k 32k 64k 96k 128k 160k 184k 208k Gen Insp Type First Borescope Robotic Rotor-In Borescope Robotic Rotor-In Robotic Rotor-In Robotic Rotor-In Robotic Rotor-In Expected Interval for 6k hrs per year units ≤18 months 5 yrs. 10 yrs. 16 yrs. 21 yrs. 26 yrs. 30 yrs. 34 yrs. For this specific example, it is assumed that the generator inspection and maintenance interval is determine
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 9fd50a2db83e937170bb5de97d6c388c | 30 | 2023-05-16 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test; Oil Deflector Alignment | 7 | End-winding, Focused Generator Inspection, Greasing, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test, Wedges | Stator Connection Ring Blockings and Ties Immediate Repairs The ties that showed signs of greasing were cleaned, flooded with low viscosity epoxy, then high viscosity epoxy, and allowed to cure for solid attachment to the supports.; Stator Wedges/Slot Support System Immediate Repairs Stator Wedges/Slot Support System Immediate Repairs To prevent further migration, these areas had wet ties wrapped around the bars to create a ridge of insulation that would stop the fille; See the "Stator Repairs" and "Wedge Tightness Test" section of this report for further details on wedges and slot support repairs.; Oil Deflectors Next Outage Parts It is recommended to have replacement oil deflectors for the T-1 / T-2 TE and GE / T-3 TE and GE and generator bearings T-4 Outer and Inner and the T-5 Outer and Inner.; These oil deflectors at this time are in tolerance not requiring replacement. |  | Wedge Tightness Test; Oil Deflector Alignment ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | Stator End Winding Assembly Immediate Repairs The corona damaged bars were repaired during this outage using the recommended GE Outer Corona Protection repair procedure. See further details in the "Stator Repair" section of this report. Stator Connection Ring Blockings and Ties Immediate Repairs The ties that showed signs of greasing were cleaned, flooded with low viscosity epoxy, then high viscosity epoxy, and allowed to cure for solid attachment to the supports. See attached pictures for detai
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 8dc70794aaf9283017b87694c263de2f | 329 | 2023-05-16 | Electrical | Field, Stator | AC Impedance | 6 | AC Impedance, End-winding, Gooseneck, Main Lead, Stator Winding, Wedges | Table 6 Recommended Rotor Test Rotor Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescope Robotic Rotor-In Winding Copper Resistance Rotor Winding Checks for poor connections and breaks X X X O X X In; If flux probe is not installed, another method is the use of RSO (Recurrent Surge Oscillography) and AC Impedance testing.; Table 7 Recommended Brushless Exciters Test Brushless exciter (stator & rotor) Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Rotor-In Visual inspection All Visible Components | GEK 116362 | AC Impedance ¦ End-winding ¦ Gooseneck ¦ Main Lead ¦ Stator Winding ¦ Wedges ¦ GEK 116362 | . GEK 103566M Creating a More Effective Generator Maintenance 13 without prior permission of the copyright owner. Table 6 Recommended Rotor Test Rotor Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescope Robotic Rotor-In Winding Copper Resistance Rotor Winding Checks for poor connections and breaks X X X O X X Insulation Resistance (aka Megger™) Rotor Winding Contamination and/or deterioration of insulation X X X X X X Shorted Turn Test Flux probe, RSO & A
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 857782ba1487bc7809d15ab2599dc9b7 | 322 | 2023-05-16 | Electrical | Field, Stator | DC Leakage | 5 | DC Leakage, Retaining Rings, Stator Winding, Wedge Looseness, Wedges | Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened materia |  | DC Leakage ¦ Retaining Rings ¦ Stator Winding ¦ Wedge Looseness ¦ Wedges | . GEK 103566M Creating a More Effective Generator Maintenance 6 without prior permission of the copyright owner. Table 2 Recommended Inspection and Maintenance Intervals 1,2,3,4,5 First Inspection Inspection and Maintenance Intervals All Units not listed below 8,000 Turbine Hours; 250 Starts; 4,000 Turning Gear Hours 24,000 to 32,000 Turbine Hours; 900 to 1,250 Starts; 30,000 to 32,000 Turning Gear Hours H55 (330H) Generators 6 H73 (390H) Generators 6 H75 (450H) Generators 6 WX/Y 16..18..21..23.
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 91e05e5699d50d53ebc75e097aa85da3 | 239 | 2023-05-16 | Inspection | Stator | Wedge Tightness Test | 4 | Focused Generator Inspection, Greasing, Wedge Tightness Test, Wedges | The wedges in the stator were inspected for greasing and outward migration.; There were no signs of dusting or greasing on any of the wedges, only a minor amount of oil on their surfaces.; 25 slots had wedges removed in order to inspect the severity of the corona damage.; These wedges were replaced with new ones and installed according to GE procedure.; See the "Stator Repairs" and "Wedge Tightness Test" section of this report for further details on wedges and slot support repairs. |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ Wedges | Part Condition: Fair Part Description: The wedges in the stator were inspected for greasing and outward migration. There were no signs of dusting or greasing on any of the wedges, only a minor amount of oil on their surfaces. 25 slots had wedges removed in order to inspect the severity of the corona damage. These wedges were replaced with new ones and installed according to GE procedure. Numerous slot exit locations were experiencing bottom and middle filler migration, specifically 30 locations
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | a5f164ba767e1e568e3c214d37b2639d | 322 | 2023-05-16 | Inspection | Hydrogen Seals, Stator | Focused Generator Review | 4 | Core, End Shield, End-winding, Wedges | The upper end shields or end plates do not require removal to permit inspection of the end winding area and the rotor remains in place.; The upper end shields or end plates may not need to be removed to permit inspection of the end winding area and the rotor remains in place.; The inspection includes a series of inspections and test (including visual, electrical, wedges assessment).; Note that this inspection may not eliminate the need to remove the rotor if an issue is discovered that requires rotor removal to correct, such as loose stator core wedges or significant end winding maintenance or repairs. |  | Focused Generator Review ¦ Core ¦ End Shield ¦ End-winding ¦ Wedges | . In addition to offline inspections and maintenance, there are online tests that can be performed to provide insight to the unit health and scope of upcoming outages. One such test is the use of flux probes to monitor the relative magnetic flux and determine if the field winding has experience shorted turns. If equipped with flux probes, at minimum a flux probe test should be performed in the planning stages for an inspection outage to help define the outage scope. Additionally, it is recommend
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 117ad9a9a7b79c458d7e489b3d4522f7 | 246 | 2023-05-16 | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | The results of the DC Leakage test are an excellent indicator of contamination levels of the windings and stator bar end turns.; DC Leakage tests should be performed on regular scheduled maintenance intervals to access the insulation condition and contamination level of the generator windings.; GE recommends performing the DC Leakage test at 2E, where E is the rated line voltage, because it is a more rigorous test to determine suitability for service of the generator.; Each phase of the stator winding was tested at 27.6 kV and the leakage current results were satisfactory.; Armature Insulation DC Leakage Test Collector End Date (dd-mmm-yyyy) Gen SN Prepared by Manufacturer Turbine SN Equipment Data set Project ID A 10 KV DC voltage was applied to each phase with the other two phases grounded for a period of 10 |  | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding | Part Description: The direct current leakage test can be considered a series of high voltage insulation resistance measurements taken at increasing steps of test voltage on a scheduled time basis (R=E/I). The time schedule is based on a preliminary di-electric absorption test to determine the absorption ratio of the winding insulation. The absorption ratio is then used to determine the time schedule for the step-voltage test (Schleif Method). The test results obtained using this method are the s
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 467d4ae5e0079bb00fbbdba1757a08fc | 242 | 2023-05-16 | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | Each phase was tested at 5000 V DC and a Polarization Index (PI) was calculated after a 10-minute charging period.; Stator Winding Insulation Resistance / HV Proof Tests Date 4.16.23 Generator No.:; Left (CE) Center (CE) Right (CE) 24 21 34% Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Description: The purpose of the megger & PI test is to determine the integrity of the insulation system without risking damage to the unit during high voltage testing. Each phase was tested at 5000 V DC and a Polarization Index (PI) was calculated after a 10-minute charging period. The insulation resistances of the individual phases were measured, and the results corrected to 25 degrees C for comparison to the previous values found in the past report for this unit. The insulation resistance
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 502939467346eee7b8aacbca6a8f4dba | 23 | 2023-05-16 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | End Shield, Oil Deflector Alignment, Oil Deflectors | The inner and outer oil deflectors were installed and set along with the bearing caps.; The end shields were set with all vent hoses verified attached and clear silicone utilized as a sealant. |  | Oil Deflector Alignment ¦ End Shield ¦ Oil Deflectors | . The CE bearing cap was turned upside down and then the UH CE bearing was set in it to megger test. Test was satisfactory to continue assembly. The inner and outer oil deflectors were installed and set along with the bearing caps. The end shields were set with all vent hoses verified attached and clear silicone utilized as a sealant. A closeout was performed with customer representative and manway covers installed with new gaskets. On 20 Apr 2023 the preparations to test lube oil and perform co
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | 4743a28a76fab35577d15a59eefadf91 | 250 | 2023-05-16 | Inspection | Stator | Wedge Tightness Test | 3 | Focused Generator Inspection, Wedge Tightness Test, Wedges | 784 806 804 839 790 789 803 792 764 742 804 783 766 812 42 43 786 811 799 807 835 820 795 813 812 808 779 830 817 834 808 821 818 814 789 780 825 43 44 824 784 784 805 825 813 824 795 800 814 801 837 813 775 823 801 815 800 808 816 786 44 4 |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Wedges | 784 806 804 839 790 789 803 792 764 742 804 783 766 812 42 43 786 811 799 807 835 820 795 813 812 808 779 830 817 834 808 821 818 814 789 780 825 43 44 824 784 784 805 825 813 824 795 800 814 801 837 813 775 823 801 815 800 808 816 786 44 45 824 830 825 823 833 836 818 836 806 808 805 839 828 830 803 801 828 814 805 801 783 45 46 817 771 788 824 818 805 815 818 825 813 794 791 831 814 814 807 809 832 802 810 808 46 47 830 830 831 840 827 827 829 816 823 814 822 825 771 839 863 831 802 821 768 77
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | a9f34365f4c9b4ed19fee56824e616ac | 249 | 2023-05-16 | Inspection | Stator | Wedge Tightness Test | 3 | Focused Generator Inspection, Wedge Tightness Test, Wedges | The wedge tightness test was conducted with an Equotip 2 testing unit and each wedge was tapped three times for an accurate averaged value.; Taking a look at the wedge map attached below, one can see that all of the wedges in the unit are tight.; This unit’s wedge tightness test results pass the acceptable threshold for air cooled in- service units |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Wedges | Part Description: Correctly evaluating wedge tightness data is important for the continued, long-term, reliable operation of generators. The wedge tightness test was conducted with an Equotip 2 testing unit and each wedge was tapped three times for an accurate averaged value. Taking a look at the wedge map attached below, one can see that all of the wedges in the unit are tight. This unit’s wedge tightness test results pass the acceptable threshold for air cooled in- service units
UNI036579 | OUACHITA GENERATING PLANT | Field_Service_Report_ProjectID_A-1361420_EV-122503_C-10346358.pdf | 270T505 | Steam Turbine | b29e2f7083ffce0bcbe0280d1945532f | 21 | 2023-05-16 | Inspection | Field, Hydrogen Seals | Field Findings Review | 3 | End Shield, Fan Blades, Greasing | The GS had performed a borescope inspection utilizing the manway covers prior to the removal of the end shields.; The generator upper end shields on the TE and CE of the generator were removed and placed in storage for inspection and cleaning.; The GS was notified of the removal of the end shields while he was preparing for electrical testing.; Upon the removal of the end shields it was discovered that there were indications of dislodged leads on the generator field.; During the reevaluation of the stator and field numerous indications of Corona and greasing was noted. |  | Field Findings Review ¦ End Shield ¦ Fan Blades ¦ Greasing | . With no indications noted at this time. T-5 CE bearing of the generator was tested by electricians and found that the thermocouple was working but 1 zone was not working. At this time, the decision to send the bearing to JD’s Babbitt Bearing was made, to replace the faulty thermocouple and perform bearing inspection and contact check. The GS had performed a borescope inspection utilizing the manway covers prior to the removal of the end shields. The generator upper end shields on the TE and CE
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 5e04dec4d0d3e3033dcefb77c8504923 | 16 | 2023-01-11 | Electrical | Field, Hydrogen Seals, Stator | DLRO; Polarization Index | 14 | AC Impedance, DC Leakage, DLRO, End-winding, Focused Generator Inspection, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Retaining Rings, Sub-slots, Wedge Tightness Test, Wedges | • MAGIC visual inspection, wedge tightness • Borescope under Retaining Rings (RR) of the Field • Visual inspection of End Winding Support System • RTDs • Visual inspection • Resistance measurement • Megger test • Stator Electrical testing • | ER-20221010-0663 | DLRO; Polarization Index ¦ AC Impedance ¦ DC Leakage ¦ DLRO ¦ End-winding ¦ Focused Generator Inspection ¦ Generator Pressure Test ¦ ER-20221010-0663 | . All fuel flex lines were inspected per TIL. All fuel piping was reinstalled see piping for details • Recorded ALL opening / closing clearances. • Steam cleaned compressor cases and visually inspected ALL stator Vanes for damage, the S5,and S14-16 vanes were removed and new vanes were installed per FMI. • Checked stator vane drops at horizontal joints. Performed shim pinning on required drop adjustments. • Removed and replaced both generator lift oil lines. • Removed, visually inspected and mea
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | d44ef462fd07edd5c03d7e2bd58c4bb1 | 246 | 2023-01-11 | Inspection | Field, Stator | MAGIC Inspection | 11 | Core, End-winding, Field Body, Gooseneck, Greasing, Loose End-winding Blocking, MAGIC Inspection, Retaining Rings, Step Iron, Sub-slots, Wedges | A visual inspection of the Stator Core and Field was performed using MAGIC Jr.; • Stator wedges and core iron • Flux Probe • Field • Field Body • Field wedges • Balance weights • Vent holes • Retaining Rings • Borescope Inspection • Coil-to-Coil jumpers • Pole-to-Pole jumpers • Gooseneck assemblies • Coil Stucks and In; • Stator • Dusting/greasing found on core packages, wedges and step iron • Foreign material between core stator vent slots • Field • Scratches on the Field body • Red dusting on Field • Partially blocked vent holes While inspecting the Fiel | ER-20221007-0888, ER-20221010-0663 | MAGIC Inspection ¦ Core ¦ End-winding ¦ Field Body ¦ Gooseneck ¦ Greasing ¦ Loose End-winding Blocking ¦ ER-20221007-0888 ¦ ER-20221010-0663 | Part Condition: Fair Part Description: A visual inspection of the Stator Core and Field was performed using MAGIC Jr. A view of the flux probe is also shown and appears to be in working condition. The following were inspected visually: • Stator wedges and core iron • Flux Probe • Field • Field Body • Field wedges • Balance weights • Vent holes • Retaining Rings • Borescope Inspection • Coil-to-Coil jumpers • Pole-to-Pole jumpers • Gooseneck assemblies • Coil Stucks and Insulation • End Winding b
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | ee8b89fe7c1c43b15d0cb2f4eb1fc6aa | 249 | 2023-01-11 | Inspection | Field, Stator | MAGIC Inspection | 8 | Gooseneck, Greasing, High Voltage Bushings, MAGIC Inspection, Main Lead, Pole Jumper, Sub-slots, Wedges | (518) 385-3178 Generator Specialist Homer Solis Slot 5 View of greasing between package and wedge ~ 3” from CE RR Image 43 Slot 2 View of foreign material ~ 22” from CE RR Image 44 Slot 56 View of foreign material ~ 45” from CE RR Image 45 |  | MAGIC Inspection ¦ Gooseneck ¦ Greasing ¦ High Voltage Bushings ¦ Main Lead ¦ Pole Jumper | . 55 Rm. 263 Generator # 337X788 Schenectady, New York 12345 Date 10-09-2022 Office: (518) 385-1751, 8*235-1751 Operator Kopetchny Fax: (518) 385-3178 Generator Specialist Homer Solis Slot 5 View of greasing between package and wedge ~ 3” from CE RR Image 43 Slot 2 View of foreign material ~ 22” from CE RR Image 44 Slot 56 View of foreign material ~ 45” from CE RR Image 45 186 deg View of scratches on the field ~ 37” from CE RR Image 46 Slot 36 View of the flux probe ~ 12” from CE RR Image 47 CE
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 2002716e78744e8586a36071d6e22166 | 20 | 2023-01-11 | Electrical | Field, Stator | DC Leakage | 7 | Collector Rings, Core, DC Leakage, End-winding, Greasing, MAGIC Inspection, Step Iron | Stator End Winding Assembly Next Outage A visual inspection of the stator core should be performed in accordance with the schedule recommendations in GEK-103566.; For the greasing found on the step iron and slot exits, perform TIL-2260R1.; Should removed Field to gain access to Stator step iron and slot exits, clean greased areas.; If found loose core iron then perform requirements in TIL.; Field Visual Inspection Next Outage Recommend getting the collector rings machined and resurfaced to increase conductivity of rings. | ER-20221031-1000, ER-20221103-0767, GEK-103566 | DC Leakage ¦ Collector Rings ¦ Core ¦ End-winding ¦ Greasing ¦ MAGIC Inspection ¦ ER-20221031-1000 ¦ ER-20221103-0767 | Generator Misalignment Immediate Services The customer to hire a competent third party that specializes in foundation analysis and repair to see if the foundation has an issue or not, as GE does not have any capability to evaluate this portion of trouble shooting and there is no findings so far to other explain how the misalignment occurred.. ER case # ER-20221031-1000 - Additionally per ER-20221103-0767 it is recommended to monitor the bearing metal temperatures along the entire rotor train (ge
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | e9f00855e6e38a11bea1e901566c8ddc | 6 | 2023-01-11 | Electrical | Stator | Polarization Index; DC Leakage | 6 | DC Leakage, End-winding, Focused Generator Inspection, Polarization Index, Wedge Tightness Test, Wedges | MAJOR INSPECTION (MI) - 297866 COTTONWOOD ENERGY COMPANY, LP COTTONWOOD 3.8.6 Armature Insulation Resistance with Polarization Index (PI) Test __________ 273 3.8.7 DC Leakage & Hipotential (HiPot) __________ 275 3.8.8 Wedge Tightness Test _ |  | Polarization Index; DC Leakage ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ Polarization Index ¦ Wedge Tightness Test ¦ Wedges | . Not to be copied, reproduced, or distributed without GE prior written consent. MAJOR INSPECTION (MI) - 297866 COTTONWOOD ENERGY COMPANY, LP COTTONWOOD 3.8.6 Armature Insulation Resistance with Polarization Index (PI) Test __________ 273 3.8.7 DC Leakage & Hipotential (HiPot) __________ 275 3.8.8 Wedge Tightness Test __________ 279 3.8.9 Resistance Test on RTDs __________ 281 3.8.10 Megger Test on RTDs __________ 283 3.8.11 End Winding Repairs __________ 286 3.8.12 Field Visual Inspection _____
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 4f26630503c25072ab9e27ba180002ac | 239 | 2023-01-11 | Inspection | Stator | Stator Findings Review | 5 | Core, End-winding, Greasing, Step Iron, Wedges | • All ties and blocking were inspected for dusting and/or greasing • Axial support hardware were inspected for signs of looseness • Core compression nuts were inspected for signs of looseness • Bar and connection ring insulation were inspec; Recommended end winding repair and customer agreed to repair (End Winding Repairs) There was also medium to heavy greasing step iron and end wedges.; A visual inspection of the stator core should be performed in accordance with the schedule recommendations in GEK-103566.; For the greasing found on the step iron and slot exits, perform TIL-2260R1.; Should removed Field to gain access to Stator step iron and slot exits, clean greased areas. | GEK-103566 | Stator Findings Review ¦ Core ¦ End-winding ¦ Greasing ¦ Step Iron ¦ Wedges ¦ GEK-103566 | Part Condition: Fair Part Description: A visual inspection of the TE and CE winding was performed. This included, but was not limited too: • All ties and blocking were inspected for dusting and/or greasing • Axial support hardware were inspected for signs of looseness • Core compression nuts were inspected for signs of looseness • Bar and connection ring insulation were inspected for signs of overheating or damage • All Stator wedges/slot support were inspected for any wedge movement • General c
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 3b3aaf6060d61c881c0f75cdef94ad50 | 286 | 2023-01-11 | Inspection | Stator | Wedge Tightness Test | 5 | Focused Generator Inspection, MAGIC Inspection, Wedge Looseness, Wedge Tightness Test, Wedges | There were no loose or hollow wedges.; Cottonwood Energy Project Number of Wedges:; Solis W E D G E S W E D G E S W E D G E S W E D G E S CE 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 TE S 1 99 97 88 82 98 99 98 97 97 98 97 95 1 S L 2 91 96 99 100 91 99 99 96 98 97 100 94 2 L O 3 98 90 95 97 |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Wedge Looseness ¦ Wedges | Part Condition: Fair Part Description: The partial wedge tightness was performed by MAGIC Tech. There were no loose or hollow wedges. The flux probe was not inspected as shown on the wedge map. Customer: Cottonwood Energy Company, LP Number of Slots: 60 Hollow Wedge Lowest Value: 34 Site/Unit: Cottonwood Energy Project Number of Wedges: 28 Tight Wedge Lowest Value: 67 Generator #: 337X788 Test Specialist: Kopetchny Test Date: Generator Specialist: Solis W E D G E S W E D G E S W E D G E S W E D
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 5766c3d56a75dd3f557e99f484ee6966 | 2 | 2023-01-11 | Inspection | Field, Stator | Generator Pressure Test | 5 | End-winding, Fan Blades, Generator Pressure Test, High Voltage Bushings, MAGIC Inspection | MAJOR INSPECTION (MI) - 297866 COTTONWOOD ENERGY COMPANY, LP COTTONWOOD 3.6 Exhaust Section __________ 185 3.6.1 Exhaust Casing __________ 185 3.6.2 T2 Journal Bearing __________ 196 3.7 Generator __________ 200 3.7.1 Generator bearings, se |  | Generator Pressure Test ¦ End-winding ¦ Fan Blades ¦ High Voltage Bushings ¦ MAGIC Inspection | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 GAS TURBINE (297866 ¦ SY0047463) __________ 7 1 Summary __________ 7 1.1 Timers and Counters __________ 7 1.2 Executive Summary __________ 7 1.3 Work Scope __________ 12 2 Technical __________ 13 2.1 Recommendations __________ 13 3 Turbine __________ 16 3.1 Auxiliaries __________ 16 3.1.1 Hydraulic Pumps and Motors __________ 16 3.1.2 Turning Gear __________ 17 3.1.3 Blowers and Motors __________
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | e95141b190c940cfc593dabe8cecc4ea | 231 | 2023-01-11 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The excitation fan blades were not removed during this outage.; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA NA NA NA NA Fan Blade J 0.043 0.026 0.030 0.031 0.050 0.045 Inner O |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Part Condition: Fair Part Description: The excitation fan blades were not removed during this outage. They were cleaned and visually inspected during the alignment process and there were no abnormal findings. The shrouds were found to be slotted to achieve alignment in a past outage, pictures attached. The Fan and shaft shrouds were realigned and data is attached. IMG 0986 IMG 1774 IMG 1776 IMG 1933 IMG 1934 IMG 2004 IMG 2006 IMG 2008 Generator Field Clearance Equip Code: Collector End (Axial Fa
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 360ae4489c0b9c256add244c96b7b7bd | 303 | 2023-01-11 | Electrical |  | DLRO; Winding Resistance | 4 | AC Impedance, DLRO, Polarization Index, Winding Resistance | • Winding (copper) resistance DLRO • AC Impedance • 500V Megger/PI The results of these tests were satisfactory.; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 9.89 1.80 5.49 20.66 3.70 5.58 30.27 5.30 5.71 40.50 7.00 5.79 49.95 8.60 5.81 60.01 10.20 5.88 69.94 11.70 5.98 80.14 13.00 6.16 90.18 14.50 6.22 100.54 15.80 6.36 110.65 17.00 6.51 120.34; CAL Date 1212042 05/02/2023 2254336 05/25/2023 2251449 04/05/2023 1216781 07/19/2023 Reading Checks per TM4010 Previous Test Correct to 25 ºC Prior Test @25 ºC Historical Resistance Readings Instrument Description 7FH2 Number of Starts Fact | GEK-103566, TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ AC Impedance ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ GEK-103566 ¦ TM4010 | Part Condition: Fair Part Description: The following electrical test were performed on the Field: • Winding (copper) resistance DLRO • AC Impedance • 500V Megger/PI The results of these tests were satisfactory. Recommendation Description: Electrical testing should be performed in accordance with the schedule recommendations outlined in GEK-103566. Field Measurements Date Turbine No.: 297866 Prepared by: Equipment Generator No.: 337X788 Project ID: OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohm
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 3dd8e79f4ce9827a1e0b5981a2aead4a | 247 | 2023-01-11 | Inspection | Stator | MAGIC Inspection | 4 | Greasing, MAGIC Inspection, Step Iron, Wedges | (518) 385-3178 Generator Specialist Homer Solis Location Comments Photo Identification Slot 34 View of end wedge dowel pin Image 01 Slots 34-30 View of stator Image 02 72 deg View of TE RR Image 03 Slot 33 View of greasing on packages/wedge |  | MAGIC Inspection ¦ Greasing ¦ Step Iron ¦ Wedges | . g GE Power Inspection & Life Extension Services Magic Photo I.D.Worksheet Job # 10366363 1 River Road, Bldg. 55 Rm. 263 Generator # 337X788 Schenectady, New York 12345 Date 10-09-2022 Office: (518) 385-1751, 8*235-1751 Operator Kopetchny Fax: (518) 385-3178 Generator Specialist Homer Solis Location Comments Photo Identification Slot 34 View of end wedge dowel pin Image 01 Slots 34-30 View of stator Image 02 72 deg View of TE RR Image 03 Slot 33 View of greasing on packages/wedge ~ 64” from CE
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | feb8a507ae0861c67b575281fe66d926 | 217 | 2023-01-11 | Mechanical | Hydrogen Seals | Generator Pressure Test; Blue Check | 4 | Blue Check, Generator Pressure Test, Hydrogen Seal Assembly, Seal Rings | All seals were lapped and blue checked to ensure proper contact and was witnessed by Fieldcore and the customer.; TE Air seal as found TE Gas Blue check IMG 1250 TE Air blue check CE gas blue check CE Air blue check Hydrogen Seal Date(m/d/y) 10/20/2022 Generator Serial No.; 297866 Units recorded in INSPECTIONS & CHECKS CODE Review EM 3404 and FP x Measure Resistance x X Work Carried Out Blue Check x Measure Seal Oil Flow N Not Done Seal Joint Check x Inspect Insulation x NA Not Applicable Measure Rings x Inspe | EM 3404 | Generator Pressure Test; Blue Check ¦ Blue Check ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Seal Rings ¦ EM 3404 | Part Condition: Good Part Description: Both the TE and CE seals and casings were removed and inspected during this outage. The CE seal case had a step out of tolerance, plant sent it to JD bearings and had it skim cut to remove the step. Both the Air and Gas seals were replaced by seals from JD bearings supplied by the customer. All seals were lapped and blue checked to ensure proper contact and was witnessed by Fieldcore and the customer. The CE springs were changed out during this outage as we
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 97401286588b57402f1486cc36211851 | 250 | 2023-01-11 | Inspection | Field | Focused Generator Review | 4 | Gooseneck, Main Lead, Pole Jumper, Sub-slots | (518) 385-3178 Generator Specialist Homer Solis 180 deg View of main lead hardware (nut side) and gooseneck Image 87 180 deg View of main lead hardware (head side) and gooseneck Image 88 180 deg View of 2-3 coil to coil jumper Image 89 180 |  | Focused Generator Review ¦ Gooseneck ¦ Main Lead ¦ Pole Jumper ¦ Sub-slots | . 55 Rm. 263 Generator # 337X788 Schenectady, New York 12345 Date 10-09-2022 Office: (518) 385-1751, 8*235-1751 Operator Kopetchny Fax: (518) 385-3178 Generator Specialist Homer Solis 180 deg View of main lead hardware (nut side) and gooseneck Image 87 180 deg View of main lead hardware (head side) and gooseneck Image 88 180 deg View of 2-3 coil to coil jumper Image 89 180 deg Opposite view of 2-3 coil to coil jumper Image 90 180 deg View of 4-5 coil to coil jumper Image 91 180 deg Opposite view
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 50f34d99f38b0fa89ef2d804f908127b | 284 | 2023-01-11 | Electrical |  | Polarization Index; DC Leakage | 3 | DC Hipot, DC Leakage, Polarization Index | (a) Rev 1.6 - 28 Feb 2022 Armature Insulation DC Leakage Test Collector End Date (dd-mmm-yyyy) Gen SN Prepared by Manufacturer Turbine SN Equipment Data Set Project ID Comments:; 377X288 297866 10 Oct 2022 GE Comments As Found DC Hipot 2253925 7/25/2023 Calibration Exp.; 0.0 2.0 4.0 6.0 8.0 10.0 12.0 14.0 16.0 10 20 30 40 50 60 70 m A KV DC Leakage Test Left Center Right GE Proprietary – Non-Public Not to be distributed or reproduced to third parties without prior GE approval. |  | Polarization Index; DC Leakage ¦ DC Hipot ¦ DC Leakage ¦ Polarization Index | . The current readings are plotted as a function of voltage to determine if a nearly linear relationship exist, indicating a constant insulation resistance as a function of voltage. Time Left: T3 Center: T2 Right: T1 (Minutes) μA Megohm μA Megohm μA Megohm 0.50 5.00 3000 6.00 2500 6.50 2300 1.00 3.20 4700 4.00 3800 4.00 3800 Temp Units : 1.50 2.70 5600 2.50 6000 2.80 5400 Metrics 2.00 2.20 6800 2.10 7100 1.60 9400 3.00 1.50 10000 1.60 9400 1.50 10000 3.16 1.30 12000 1.50 10000 1.40 11000 4.00 1.
UNI025979 | COTTONWOOD | Field_Service_Report_ProjectID_A-1633510_EV-116799_C-10366363.pdf | 297866 | Gas Turbine | 5f40f5731835a8bb5205bb737f490dd9 | 280 | 2023-01-11 | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | Stator Winding Insulation Resistance / HV Proof Tests Date 10/10/2022 Generator No.:; Left (CE) Center (CE)Right (CE) 28 28 30% Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC L | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Condition: Fair Part Description: A Megger/PI test were completed per phase, with phases not under test grounded. These test evaluates insulation integrity and GE recommended values for proceeding o High Voltage testing or return to service. Performed 5KV Megger/PI test. The results of these tests were satisfactory. Stator Winding Insulation Resistance / HV Proof Tests Date 10/10/2022 Generator No.: Prepared by: Equipment OEM GE Stator Voltage (kV): Project ID: DC INSULATION RESISTANCE (Meg
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | af9e24d90fcf1b9dc0c2b47db60a20e0 | 492 | 2022-05-22 | Electrical | Stator | Winding Resistance; Polarization Index | 8 | AC Impedance, End-winding, Greasing, Polarization Index, Wedge Looseness, Wedge Tightness Test, Wedges, Winding Resistance | We did find one area of light greasing between the end wedge and the package iron (photo 8 on page 26).; The greasing in this area can be the result of a hollow or loose wedge.; Since the greasing is occurring on an end wedge - recommend a wedge tap to ensure the wedge is within acceptable hardness criteria.; No dusting or greasing found on the bar to bar ties.; No dusting or greasing found at the slot exits. |  | Winding Resistance; Polarization Index ¦ AC Impedance ¦ End-winding ¦ Greasing ¦ Polarization Index ¦ Wedge Looseness ¦ Wedge Tightness Test | . The outer sheath on the core ground cable is starting to wear (page 4 of photos). This condition will not affect the operation of the generator as the ground conductor is still intact. The wear is most likely the result of personnel accessing the end winding compartment through the side inspection door. Example photos accompany this report for your inspection and records. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written c
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 46c8717c7dd99bfd98b582c385e1fe6e | 475 | 2022-05-22 | Inspection | Hydrogen Seals, Stator | MAGIC Inspection | 6 | End Shield, End-winding, Greasing, MAGIC Inspection, Step Iron, Wedges | GTG1 Mahkeses Stator End Winding … Since the end shields were not removed during this inspection, the inner basket of the end winding was viewed with a borescope which was snaked around the series end caps.; No dusting or greasing found on the bar to bar ties.; No dusting or greasing found at the slot exits.; Removing the paint drips was performed to allow for future MAGIC inspections.; CI - 297716 GE Power Inspection & Life Extension Services Section Collector End Sub-Section Stator End Windings Component Stator End Windings Location Step Iron Sub-Location General Observation Typical Comments Reference Photo – no problems |  | MAGIC Inspection ¦ End Shield ¦ End-winding ¦ Greasing ¦ Step Iron ¦ Wedges | . Anchor points secure. Staking on the core flange nuts is acceptable. Binding band ties are acceptable. Connection Ring blocking and ties are acceptable. Core flange seal are in acceptable condition. Example photos accompany this report for your inspection and records. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. CI - 297716 Mahkeses – GTG1 – Stator End Winding - CE P a g e 1 ¦ 8 Dusting observed between the b
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 10e8e334d359376653922f731072495d | 518 | 2022-05-22 | Inspection | Field | Field Findings Review | 6 | Gooseneck, Pole Jumper, Retaining Rings, Sub-slots, Turn Insulation Migration, Turn Jumper | Photo 11 and 12 are closer to the gooseneck.; Collector_End-Field_taining_Ring_General_010.JPG Borescope Field CE GE Power Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Retaining Ring Location Gooseneck – Pole 2 Observation Typical Comment; Collector_End-Field_taining_Ring_General_013.JPG Section Collector End-Field Sub-Section Field Component Retaining Ring Location Gooseneck – Pole 2 Observation Typical Comments No problems observed.; Collector_End-Field_taining_Ring_General_018.JPG Borescope Field CE GE Power Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Retaining Ring Location Turn to Turn Jumper Observation Typical Commen; Copper stack uniform, no evidence of turn to turn insulation migration. |  | Field Findings Review ¦ Gooseneck ¦ Pole Jumper ¦ Retaining Rings ¦ Sub-slots ¦ Turn Insulation Migration ¦ Turn Jumper | . Photo 11 and 12 are closer to the gooseneck. These are reference photos. No problems observed. Collector_End-Field_taining_Ring_General_010.JPG Borescope Field CE GE Power Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Retaining Ring Location Gooseneck – Pole 2 Observation Typical Comments Reference Photo Collector_End-Field_taining_Ring_General_011.JPG Section Collector End-Field Sub-Section Field Component Retaining Ring Location Gooseneck – Pole
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | ce6ee8d7f4b20fd78e4432eb82defb11 | 510 | 2022-05-22 | Inspection | Field | Field Findings Review | 5 | Gooseneck, Greasing, Retaining Rings, Sub-slots, Turn Jumper | Turbine_End_Stator__Inner_Basket_General_023.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Bar to Bar Ties Observation Typical Comments No dusting or greasing observ; CI - 297716 GE Power Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Retaining Ring Location Gooseneck Pole 1 Observation Typical Comments Particulate accumulation observed.; Collector_End-Field_taining_Ring_General_001.JPG Section Collector End-Field Sub-Section Field Component Retaining Ring Location Turn to Turn Jumpers - Pole 1 Observation Typical Comments Particulate accumulation observed.; Collector_End-Field_taining_Ring_General_004.JPG Borescope Field CE GE Power Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Retaining Ring Location Gooseneck – Pole 2 Observation Typical Comment; Collector_End-Field_taining_Ring_General_007.JPG Section Collector End-Field Sub-Section Field Component Retaining Ring Location Turn to Turn Jumper – Pole 2 Observation Typical Comments Some distortion of the jumper observed, possibly from |  | Field Findings Review ¦ Gooseneck ¦ Greasing ¦ Retaining Rings ¦ Sub-slots ¦ Turn Jumper | . Turbine_End_Stator__Inner_Basket_General_023.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Bar to Bar Ties Observation Typical Comments No dusting or greasing observed. Turbine_End_Stator__Inner_Basket_General_024.JPG Borescope Stator TE Inspect the field end turns for worsening conditions at regular scheduled outages. In particular, watch for increased particulate accumulations. GEGEGE GE Confidential and Proprietary I
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 9035ac45eb09991d08d20d24fbec96da | 3 | 2022-05-22 | Electrical | Stator | Winding Resistance; Polarization Index | 5 | AC Impedance, DC Leakage, End-winding, Polarization Index, Winding Resistance | CI - 297716 IMPERIAL OIL RESOURCES Mahkeses Project 3.4 Inlet Section __________ 434 3.4.1 Inlet Duct, Filters and Bleed Heat Piping __________ 434 3.5 Exhaust Section __________ 439 3.5.1 Exhaust Casing Slippage __________ 439 3.5.2 Exhaus; CI - 297716 IMPERIAL OIL RESOURCES Mahkeses Project 3.8.3 Stator End Winding Inspection (TE) __________ 483 3.8.4 Stator End Winding Inspection (TE) Borescope __________ 489 3.9 Generator Field Electrical Testing __________ 502 3.9.1 IR/PI, |  | Winding Resistance; Polarization Index ¦ AC Impedance ¦ DC Leakage ¦ End-winding ¦ Polarization Index ¦ Winding Resistance | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 3 1.3 EHS __________ 5 1.4 Quality __________ 5 GAS TURBINE (297716 ¦ SY0070886) __________ 7 1 Summary __________ 7 1.1 Timers and Counters __________ 7 1.2 Work Scope __________ 7 2 Technical __________ 8 2.1 Recommendations __________ 8 3 Turbine __________ 12 3.1 Combustion Section __________ 12 3.1.1 Piping and Flexible Metal Hoses __________ 12 3.1.2 Primary
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 7fafb0015e412a0cd94016138c55e8a9 | 511 | 2022-05-22 | Electrical | Field | DLRO; Winding Resistance | 5 | AC Impedance, DLRO, Polarization Index, Turn Jumper, Winding Resistance | OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.42 1.16 8.98 19.90 2.21 9.00 30.06 3.30 9.11 40.24 4.37 9.21 50.00 5.36 9.33 60.43 6.39 9.46 70.21 7.32 9.59 79.99 8.20 9.75 90.27 9.13 9.89 100.44 9.99 10.05 INSULATION RESISTANCE AT 50; CAL Date 1212837 10/19/2021 2249949 10/19/2021 202764 09/07/2021 1212408 08/11/2021 Insulation Resistance - PASS, PI = PASS, Winding Resistance = PASS, AC Impedance = PASS Date NA Turning Gear Hrs Check per TM4010 8 Point Resistance Check (; One of the turn to turn jumpers did appear to be distorted (photo 8) and could also be the result of elevated heating.; No cracks or mechanical damage was observed on the turn to turn jumper and the winding resistance values are within acceptable tolerance.; The turn to turn jumper is in acceptable condition for continued operation. | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ AC Impedance ¦ DLRO ¦ Polarization Index ¦ Turn Jumper ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | . The resultant plot of the impedance measurements taken this year, shows that the turn to turn insulation of the field is in acceptable condition for continued operation. Test Result = PASS A copy of the test results accompanies this report for your inspection and records. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. CI - 297716 IOR Mahkeses Field Measurements Date Turbine No.: Prepared by: Equipment Generator
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 2c1951c58b67785a62a1caa7af3d442b | 451 | 2022-05-22 | Inspection | Stator | Wedge Tightness Test | 4 | Greasing, MAGIC Inspection, Wedge Tightness Test, Wedges | CI - 297716 g Alignment Recommend stator wedge tap the next time the field is removed from the stator due to light greasing found between an end wedge and the package iron.; Please note that the identified area is on an end wedge, the field will have to be removed for a wedge tap to be performed as the MAGIC junior robot will not be able to tap the end wedges due to its physical construction.; Turbine_End_Stator__Inner_Basket_General_001.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Bar to Bar Ties Observation Typical Comments No evidence of dusting or gre; Turbine_End_Stator__Inner_Basket_General_007.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location End Wedge Observation Greasing Comments Light greasing observed between we |  | Wedge Tightness Test ¦ Greasing ¦ MAGIC Inspection ¦ Wedges | . Exhaust Frame Strut Cracks GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. CI - 297716 Shafts 3A and 3B of the accessory gearbox are used to drive liquid fuel components that are not present on this unit. There is a modification available to remove the #3 shafts and cap their associated oil spray nozzles and bearing supply galleries. This would remove unused components from the gearbox and eliminate a potential
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 69ff6c3646a7f8a32f56aaa00528110d | 469 | 2022-05-22 | Electrical |  | Winding Resistance; Polarization Index | 4 | DC Hipot, DC Leakage, Polarization Index, Winding Resistance | (a) Rev 1.6 - 28 Feb 2022 336X919 Mahkeses DC Leakage April … Armature Insulation DC Leakage Test Collector End Date (dd-mmm-yyyy) Gen SN Prepared by Manufacturer Turbine SN Equipment Data Set Project ID Comments:; I01-064977 336X919 297716 10 Apr 2022 Comments As Found 80 kV DC Hipot 1212677 4/4/2023 Calibration Exp.; 0.0 0.5 1.0 1.5 2.0 2.5 10 15 20 25 30 35 40 45 m A KV DC Leakage Test Left Center Right GE Proprietary – Non-Public Not to be distributed or reproduced to third parties without prior GE approval.; (b) Rev 1.6 - 28 Feb 2022 336X919 Mahkeses DC Leakage April … The winding resistance was measured on each of the three phases.; CI - 297716 Armature Winding Resistance Equip Code Date (m/d/y) 4/10/2022 Turbine Serial No. |  | Winding Resistance; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ Polarization Index ¦ Winding Resistance | . The current readings are plotted as a function of voltage to determine if a nearly linear relationship exist, indicating a constant insulation resistance as a function of voltage. Time Left: T3/T6 Center: T2/T5 Right: T1/T4 (Minutes) μA Megohm μA Megohm μA Megohm 0.50 4.90 2000 4.80 2100 4.10 2400 1.00 3.00 3300 2.90 3400 2.70 3700 Temp Units : 1.50 2.30 4300 2.10 4800 1.80 5600 Metrics 2.00 1.80 5600 1.60 6300 1.40 7100 3.00 1.35 7400 1.20 8300 1.10 9100 3.16 1.30 7700 1.15 8700 1.00 10000 4.
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 4adca0f6ffb8208ac484a695ee81389e | 485 | 2022-05-22 | Inspection | Field, Stator | MAGIC Inspection | 4 | End-winding, MAGIC Inspection, Retaining Rings, Step Iron | Collector_End_Stato_Inner_Basket_General_009.JPG Section Collector End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Step Iron Observation Typical Comments No problems observed. |  | MAGIC Inspection ¦ End-winding ¦ Retaining Rings ¦ Step Iron | . Collector_End_Stato_Inner_Basket_General_002.JPG Borescope Stator CE GE Power Inspection & Life Extension Services Section Collector End Sub-Section Stator End Windings Component Stator End Windings Location Core Sub-Location General Observation Typical Comments Reference Photo – No problems observed. Collector_End_Stato_Inner_Basket_General_003.JPG Section Collector End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Slot Exit Observation Typic
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | c5ef006dd1a51ca5cb01c3894cdb1964 | 18 | 2022-05-22 | Inspection | Stator | Wedge Tightness Test | 4 | Greasing, MAGIC Inspection, Wedge Tightness Test, Wedges | Next Outage Services Recommend stator wedge tap the next time the field is removed from the stator due to light greasing found between an end wedge and the package iron.; CI - 297716 Next Outage Services have to be removed for a wedge tap to be performed as the MAGIC junior robot will not be able to tap the end wedges due to its physical construction. |  | Wedge Tightness Test ¦ Greasing ¦ MAGIC Inspection ¦ Wedges | Next Outage Services Recommend stator wedge tap the next time the field is removed from the stator due to light greasing found between an end wedge and the package iron. Please note that the identified area is on an end wedge, the field will GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. CI - 297716 Next Outage Services have to be removed for a wedge tap to be performed as the MAGIC junior robot will not be able
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 55a4f9967f961fc3045bffbab982ddf8 | 526 | 2022-05-22 | Inspection | Field | Focused Generator Review | 3 | Pole Jumper, Retaining Rings, Sub-slots | Collector_End-Field_taining_Ring_General_029.JPG Section Collector End-Field Sub-Section Field Component Retaining Ring Location Pole to Pole Jumper #2 Observation Typical Comments No problems observed. |  | Focused Generator Review ¦ Pole Jumper ¦ Retaining Rings ¦ Sub-slots | . Collector_End-Field_taining_Ring_General_025.JPG Section Collector End-Field Sub-Section Field Component Retaining Ring Location Copper Stack Observation Typical Comments Reddish hue to copper. Collector_End-Field_taining_Ring_General_026.JPG Borescope Field CE GE Power Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Retaining Ring Location Copper Stack Observation Typical Comments Reddish hue to copper Collector_End-Field_taining_Ring_General_027.J
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | c0485a7727c433a1ac5d4b09dfc5ce8f | 460 | 2022-05-22 | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | CI - 297716 Ground wall insulation resistance and polarization index was measured and found to be within acceptable condition for continued service.; Left Phase = 4.32 Gigohms at 1 minute, PI = 12.2 Test Result = PASS Center Phase = 4.43 Gigohms at 1 minute, PI = 12.9 Test Result = PASS Right Phase = 4.34 Gigohms at 1 minute, PI = 13.2 Test Result = PASS A copy of the test results accomp; CI - 297716 Stator Winding Insulation Resistance / HV Proof Tests Date 04/10/2022 Generator No.:; Left (CE) Center (CE) Right (CE) Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Te; (a) Rev 2.1 - 08/05/2020 336X919 Mahkeses Stator HV proof A… DC Leakage test with a maximum voltage of 24 kV DC was applied to each phase of the generator. | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | . After the horizontal alignment was completed, the locating pin was still able to be installed into the alignment plate attached to the foundation. This indicates that there is excessive wear to either the alignment pin or plate as there should only be 0.005" diametrical clearance between these components. The sloppy fit between the alignment pin and plate is likely allowing the accessory compartment to shift horizontally during operation causing the repeated horizonal alignment moves on the 0.
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 750cf3310e68d63df169a01d350ee310 | 502 | 2022-05-22 | Inspection | Stator | Stator Findings Review | 2 | Greasing, Wedges | Turbine_End_Stator__Inner_Basket_General_021.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Bar to Bar Ties Observation Typical Comments No dusting or greasing observ |  | Stator Findings Review ¦ Greasing ¦ Wedges | . Turbine_End_Stator__Inner_Basket_General_008-FLAG.J Borescope Stator TE GE Power Inspection & Life Extension Services Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location Retainting Ring Air Gap Observation Typical Comments No problems observed. Turbine_End_Stator__Inner_Basket_General_009.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Inner Basket Sub-Location End Wedge Observation
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 3ac21adc92c0de5d7b757d2b6642579d | 467 | 2022-05-22 | Electrical |  | DC Leakage; DC Hipot | 2 | DC Hipot, DC Leakage | 13.8 KV STATOR TESTING (Put an "X" in the box(s) of the test(s) to be performed) X 1) DC Leakage Test 2) AC Hipotential Test (60 Hz) 3) AC Hipotential Test (0.1 Hz) 4) DC Hipotential Test Multiplier DC Leakage Test:; 1.5 1.414 1.15 KV AC DC Hipot Test:; CUSTOMER REQUESTED VALUE (Multiplier) FOR DC LEAKAGE TESTING:; 1.74 CUSTOMER REQUESTED VALUE (Multiplier) FOR AC/DC HIPOT TESTING:; Multiplier DC Leakage Test: |  | DC Leakage; DC Hipot ¦ DC Hipot ¦ DC Leakage | . A copy of the test results accompanies this report for your inspection and records. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. CI - 297716 g Hipotential Testing Agreement Stator Date: 2/26/2022 Generator Serial No. 336X919 Prepared by: Khurram Maqbool Customer: IOR Mahkeses Turbine Serial No. 297716 Generator Rated Voltage (E): 13.8 KV STATOR TESTING (Put an "X" in the box(s) of the test(s) to be performed)
UNI036492 | Mahkeses Project | Field_Service_Report_ProjectID_A-1408806_FSP-284128_C-10345569.pdf | 297716 | Gas Turbine | 6f18f9f66fec66856eccae5eceaadbbc | 529 | 2022-05-22 | Electrical | Hydrogen Seals | AC Impedance | 2 | AC Impedance, End Shield | AC impedance test result does not indicate shorted turns, so it appears this material is not affecting the performance of the Field at this time.; Attempt to remove the tape could not be performed as the end shields were not removed during this inspection. |  | AC Impedance ¦ End Shield | . There is a piece of material stuck between a block and one of the copper stacks (photo 2 and photo 3). It is hard to tell what the material is, but it does appear to be plastic, possibly tape. AC impedance test result does not indicate shorted turns, so it appears this material is not affecting the performance of the Field at this time. The report from the last inspection was reviewed and found that this piece of material was observed at that time as well. Attempt to remove the tape could not
UNI222464 | SALALAH | Field_Service_Report_ProjectID_A-1372244_FSP-271172_C-10335477.pdf | 875059 | Gas Turbine | 11b8a3049c77733df10b378841a5cfcb | 43 | 2021-11-07 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | New Floating ring installed on all flow sleeves Installation of the new floating ring on flow sleeves g Combustion Section MS6001F Flow Sleeve - General Inspection Date 8 -10-2021 Turbine S/N 875059 Prepared by Al-Muntaser Al-Ha Photos Enclosed? yes Chamber # S/N # Inspected Defect Code and Location Seal Condition Seal Diameter Disposition 1 Slight wear on the spring seal 428.000 N 2 Slight wear on the spring seal 428.000 N 3 Slight wear on the spring seal 428.000 N 4 Slight wear on the spring s
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 772747dedd80c9a297b0a826b9c4ca34 | 166 | 2021-10-25 | Inspection | Field, Stator | Wedge Tightness Test | 11 | Core, End-winding, Field Body, Focused Generator Inspection, Greasing, High Voltage Bushings, Loose End-winding Blocking, Retaining Rings, Sub-slots, Wedge Tightness Test, Wedges | Body wedges did not have visual indications of looseness or damage.; Final Report_GE Generator SN 337X5… 7 High Voltage Bushings:; High Voltage Bushings:; Light greasing found on bar tie.; Light greasing on connection ring tie. |  | Wedge Tightness Test ¦ Core ¦ End-winding ¦ Field Body ¦ Focused Generator Inspection ¦ Greasing ¦ High Voltage Bushings | . Body wedges did not have visual indications of looseness or damage. No blocked ventilation ducts were found but small pieces of foreign material were observed in some locations. Final Report_GE Generator SN 337X5… 7 High Voltage Bushings: Cracks on terminal insulation tape. End Winding Support System: Hardware. No indications. End Winding Support System: 9 o’clock position axial support. Missing bolt. (9A) End Winding Support System: 9 o’clock position axial support. Loose bolt. (9B) Generator
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | ddda350a82e0157d5aec766ead6b8230 | 161 | 2021-10-25 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 10 | Core, End Shield, End-winding, Focused Generator Inspection, Greasing, High Voltage Bushings, MAGIC Inspection, Step Iron, Wedge Tightness Test, Wedges | Generator Visual Inspection MAGIC Inspection Central Nuevo Puerto– Argentina Equipment Serial No:; For this Generator Inspection, collector end gas shields and upper end shield were removed to gain access to stator end-windings area and generator field.; A visual inspection of stator core and a wedge tightness assessment using the MAGIC Senior crawler were performed by On Site Services Specialists.; Work in Generator was performed by GE and FieldCore personnel during day shift from September 20th to September 28th, 2021.; 2.1.2 High Voltage Bushings (HVB’s) No cracked or damage porcelain were found on the HVB’s on the gas side. |  | Wedge Tightness Test ¦ Core ¦ End Shield ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ High Voltage Bushings | Generator Visual Inspection MAGIC Inspection Central Nuevo Puerto– Argentina Equipment Serial No: 337X510 September 2021. Prepared by Maria Tarhan Generator Specialist Final Report_GE Generator SN 337X5… 3 1. SUMMARY EXECUTIVE SUMMARY This report documents the work scope associated with Generator Inspection for GE generator SN 337X510, during a HGP outage of Central Nuevo Puerto powerplant unit TG#11 for CPSA located in Argentina. For this Generator Inspection, collector end gas shields and uppe
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 8eccbf08fecb0d5172954fe6343596d2 | 273 | 2021-10-25 | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 10 | Core, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges | Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Pre-outage test:; Partial Discharge 1 Stator Winding Insulation Localized deterioration X X X O 1 O-R 2 O-R 2 Visual Inspection All Visible Components within the End Winding Compartment Cleanliness, foreign material, loose or displaced parts, damage, wear, d; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) ; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In 1 DC Leakage and Partial Discharge testing are optional but high |  | Polarization Index; DC Leakage ¦ Core ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings ¦ Hydrogen Seal Assembly | . Generator Turbine Generator Turbine Final Report_GE Generator SN 337X5… GEK 103566M Creating a More Effective Generator Maintenance 9 without prior permission of the copyright owner. Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Pre-outage test: H2 sniff test Generator Check any H2 leaks when unit under the H2 pressure X X X-R X-R X-R Pre-outage test: Partial Discha
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | badaf2e662db67b8d65c538d11461a41 | 181 | 2021-10-25 | Mechanical | Field, Hydrogen Seals, Stator | Oil Deflector Alignment | 9 | Centering Ring, Collector Rings, End-winding, Fan Blades, Greasing, Oil Deflector Alignment, Oil Deflectors, Retaining Rings, Wedges | greasing (dust + oil) 5.; greasing (dust + oil) - Blocking locations are typical for both leads-up and leads-down units.; Particle PT - Penetrant NA - Not Applicable S - Satisfactory Z - Zyglo INSPECTIONS & CHECKS ROTATING FIELD Physical Appearance of Visible Overheating at End - Field Forging (Body) S Wedges & Retaining Rings S - Retaining Rings S Physical Co; Grooving, Retaining Rings Burning, and Brush Film S - Spindle Mounted Verify Correct Radial - Body Mounted X & Axial Position of Brush Rigging C - Cylinder Mounted Verify Brush Holders for Wear, - Magnetic Arcing & Burning S - Non-Magnetic ; Retaining Rings 2. | TM2010 | Oil Deflector Alignment ¦ Centering Ring ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ Greasing ¦ TM2010 | . 3. No indications were found on connection rings blocks. 4. Indications found on Conn Ring Axial Support Ties: greasing (dust + oil) 5. Indications found on Bar-to-Bar Ties: greasing (dust + oil) - Blocking locations are typical for both leads-up and leads-down units. - Connection rings have been expanded outward for clarity purposes. - Record locations on Data (a) and Data (b) tab(s), as applicable. A U T R P N M B C D E F G H J K L D316224 Sheet: 324 Rev 0.0 - 12/01/04 GE Energy Proprietary
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | c7126804a7bd0b99888ba334bd24db31 | 129 | 2021-10-25 | Mechanical | Field, Hydrogen Seals | Generator Pressure Test; Blue Check | 8 | Blue Check, Collector Rings, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | 297011 Units recorded in INSPECTIONS & CHECKS CODE Review EM 3404 and FP Measure Resistance X Work Carried Out Blue Check Measure Seal Oil Flow N Not Done Seal Joint Check Inspect Insulation NA Not Applicable Measure Rings Inspect Seal Ring; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (mm) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA NA NA NA NA Fan Blade J 0.740 0.800 1.480 1.640 2.200 1.070 Inner Oil D | EM 3404 | Generator Pressure Test; Blue Check ¦ Blue Check ¦ Collector Rings ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ EM 3404 | . 287011 Prepared by Generator Serial No. 337X510 ERP Project ID Equip Code: Units recorded in Data set SEAL THICKNESS 'A' MEASUREMENTS (mm) TURBINE END COLL. END POSITION AIR HYD AIR HYD 1 31.81 31.86 2 31.84 31.90 3 31.89 32.01 4 31.91 32.01 5 31.87 31.92 6 31.83 31.80 7 31.83 31.80 8 31.86 31.92 9 31.92 32.01 10 31.92 32.03 11 31.88 31.94 12 31.82 31.87 AVERAGE 31.87 31.92 Note: All values must be entered for average value to be calculated. SEAL WIDTH 'B' MEASUREMENTS (mm) TURBINE END COLL. E
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 4b197c659a0b76fd465865dacc4624d9 | 271 | 2021-10-25 | Electrical | Field, Stator | DC Leakage | 7 | Core, DC Leakage, Focused Generator Inspection, Retaining Rings, Stator Winding, Wedge Looseness, Wedges | Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened materia; As the stator core is exposed during a rewind, a detailed inspection of the core is recommended including at minimum a visual inspection, EL-CID (or low flux test) and core tightness testing.; However, this is also an opportune time to perform a Core Ring Test (High Induction Test/ Core Ring Test or PULSAR) and to retighten the core compression features if/where applicable. |  | DC Leakage ¦ Core ¦ Focused Generator Inspection ¦ Retaining Rings ¦ Stator Winding ¦ Wedge Looseness | . Final Report_GE Generator SN 337X5… GEK 103566M Creating a More Effective Generator Maintenance 7 without prior permission of the copyright owner. Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened material Rotor vibration trends coupled with flux probe shorted turns or blocked ventilation passages May range from r
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 52d98e5014ac52019528f99484278033 | 280 | 2021-10-25 | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically constructed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . Many of the tests require special equipment that has been properly maintained and calibrated to ensure accurate results. 5 . Visual Inspection A visual inspection, performed at every inspection by an experienced individual, can uncover unit conditions previously undetected or can validate monitoring findings. In some instances, electrical testing will only detect issues when the stator and rotor insulation systems have been significantly compromised. For example, there is no definitive test fo
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 2f6c2e6c8e8cea69fd78c3e4250c51d1 | 175 | 2021-10-25 | Electrical | Stator | DC Leakage; DC Hipot | 5 | DC Hipot, DC Leakage, End-winding, Greasing, Stator Winding | To verify the integrity of the stator bar insulation DC leakage test and DC Hipot are recommended.; Light greasing was found on Conn Ring Axial Support Ties and on Bar-to-Bar Ties:; greasing (dust + oil) 3.; Blocking Light greasing found 2.; Ties Light greasing found 3. | GEK103566 | DC Leakage; DC Hipot ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ Greasing ¦ Stator Winding ¦ GEK103566 | .  For the next planned outage: properly clean TE end winding area with GE recommended solvents and apply Astro 6250 Red Eyed epoxy on ties.  Continue monitoring and inspecting for any sign of slot insulation migration that could lead to bar abrasion. To verify the integrity of the stator bar insulation DC leakage test and DC Hipot are recommended. Field:  There are no temporary on-site repairs for the main terminal studs’ damage. GE recommends shipping the rotor to a GE repair shop for a par
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 3e35f29e512ee17fbccb0c832e4c638d | 6 | 2021-10-25 | Inspection | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 5 | Fan Blades, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | Unit Serial Number 297011 was scheduled for Hot Gas Path Inspection and Generator Serial Number 337X510, for MAGIC Inspection.; Furthermore, NDT inspections were scheduled for IGVs, compressor rotor blades, turbine rotor, combustion manifolds, generator bearing, generator fan blades, among others.; Generator oil deflectors and hydrogen and air seals were also changed. |  | Generator Pressure Test; Oil Deflector Alignment ¦ Fan Blades ¦ Generator Pressure Test ¦ MAGIC Inspection ¦ Oil Deflector Alignment ¦ Oil Deflectors | Unit Serial Number 297011 was scheduled for Hot Gas Path Inspection and Generator Serial Number 337X510, for MAGIC Inspection. This report describes outage for frame 9FA.03 and 324 generator at Central Puerto SA, Buenos Aires, Argentina. FieldCore was responsible for the execution of maintenance activities of assembly, cleaning, inspection and reassembly. A borescope inspection of compressor section, bearing #2, bearing #1 lift hoses and combustion piping was carry out by FieldCore borescope spe
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 7836e9891af5512fc2ae244b84cabfee | 189 | 2021-10-25 | Inspection | Field, Stator | MAGIC Inspection | 5 | Greasing, MAGIC Inspection, Main Lead, Step Iron, Wedges | (518) 385‐3178 Generator Specialist Maria Tarhan Slots 25 to 28 Over view of core packages missing paint ~ 64” from CE RR Image 43 Slot 25 View of bent punching ~ 118” from CE RR Image 44 Slot 25 View of bent punching on TE step iron Image ; (518) 385‐3178 Generator Specialist Maria Tarhan Slot 68 Greasing on baffle tie Image 86 Slot 62 CE end wedge dowel pin.; No epoxy on it, Image 87 CE RR View of damaged main lead @ 0 deg.; Image 88 CE RR View of damaged main lead @ 0 deg.; Image 89 CE RR View of damaged main lead @ 0 deg. |  | MAGIC Inspection ¦ Greasing ¦ Main Lead ¦ Step Iron ¦ Wedges | . 55 Rm. 263 Generator # 337X510 Schenectady, New York 12345 Date 09‐28‐2021 Office: (518) 385‐1751, 8*235‐1751 Operator Higgins/Hernandez Fax: (518) 385‐3178 Generator Specialist Maria Tarhan Slots 25 to 28 Over view of core packages missing paint ~ 64” from CE RR Image 43 Slot 25 View of bent punching ~ 118” from CE RR Image 44 Slot 25 View of bent punching on TE step iron Image 45 Slots 26-28 Overview of TE step iron Image 46 Slot 60 View of greasing on wedges~192” from CE RR Image 47 Slot 61
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | c52d451ad54fc68e85edbe90837bc0c3 | 276 | 2021-10-25 | Electrical | Field, Stator | AC Impedance | 5 | AC Impedance, End-winding, Gooseneck, Main Lead, Stator Winding | Phos-Free 3 H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Test Inspection Objectives and Assessment Borescope Robotic Rotor-In Borescope Robot; Table 6 Recommended Rotor Test Rotor Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescope Robotic Rotor-In Winding Copper Resistance Rotor Winding Checks for poor connections and breaks X X X O X X In |  | AC Impedance ¦ End-winding ¦ Gooseneck ¦ Main Lead ¦ Stator Winding | . Test requires rotor removal. Final Report_GE Generator SN 337X5… GEK 103566M Creating a More Effective Generator Maintenance 12 without prior permission of the copyright owner. Table 5 Recommended Water-Cooled Stator Leak Tests for High Oxygen Systems 1,2 What about legacy Alstom stainless steel windings?? Stator Clip-Strand Braze: Phos Containing Global Epoxy Injection or Clip-Strand Braze: Phos-Free 3 H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig S
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | d675db013418df68c1225e5589fae870 | 276 | 2021-10-25 | Electrical | Stator | DC Hipot | 5 | DC Hipot, End-winding, High Voltage Bushings, Stator Winding, Wedges | 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 5 This test does not apply to units with asphalt stator windings, GVPI windings (Global Vacuum Pressure Impregnated) or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds.; 13 Alfa coefficient test is applicable to stator winding with the flat lateral support system. |  | DC Hipot ¦ End-winding ¦ High Voltage Bushings ¦ Stator Winding ¦ Wedges | . 2 For hydrogen cooled generators Off-Line Partial Discharge Testing with the unit open to air may provide additional diagnostic information. 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators. 4 An equivalent inspection via digital trending and analysis may be suitable; contact your local GE Service Representative. Dimensional and NDT test are recommended o
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | a2662854b616d0c022526555def59ba2 | 281 | 2021-10-25 | Inspection | Field, Stator | Focused Generator Review | 4 | Centering Ring, Collector Rings, Retaining Rings, Wedges | All structural components removed as part of the rewind (wedges, retaining rings, centering rings, radial fans, axial fan hubs, collector rings, coupling rings, etc.) should also be inspected. |  | Focused Generator Review ¦ Centering Ring ¦ Collector Rings ¦ Retaining Rings ¦ Wedges | . Earlier generators may have had different start/stop configuration criteria, particularly large fossil & nuclear units. For older (25+ years) generators that have changed operating profile (base load to cyclic / peaking duty), GE Product Service should be contacted for an appropriate inspection plan. However, with proper inspections and maintenance, generators may last much longer. Common issues with aged rotor forgings are typically related to the number of start/stop cycles. Several Technica
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 637a908d614daf62ac8e503f724ef769 | 278 | 2021-10-25 | Electrical | Stator | AC Impedance | 4 | AC Impedance, End-winding, Stator Winding, Wedges | If flux probe is not installed, another method is the use of RSO (Recurrent Surge Oscillography) and AC Impedance testing.; Table 7 Recommended Brushless Exciters Test Brushless exciter (stator & rotor) Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Rotor-In Visual inspection All Visible Components; Brushless exciter (stator & rotor) Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Rotor-In Electrical test Rectifier (Diodes) Forward/ Reverse voltage X X X X3 Electrical test | GEK 116362 | AC Impedance ¦ End-winding ¦ Stator Winding ¦ Wedges ¦ GEK 116362 | . O – Optional Final Report_GE Generator SN 337X5… GEK 103566M Creating a More Effective Generator Maintenance 14 without prior permission of the copyright owner. Rotor Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescope Robotic Rotor-In 1 The preferred method for shorted turn testing is the flux probe. If flux probe is not installed, another method is the use of RSO (Recurrent Surge Oscillography) and AC Impedance testing. Flux probe testing is performed
UNI034468 | CENTRAL NUEVO PUERTO | Field_Service_Report_ProjectID_A-1543562_FSP-273554_C-10348997.pdf | 297011 | Gas Turbine | 162a087d43aabd808baa55093e0f9cfc | 123 | 2021-10-25 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | Part Description: After the disassembly of the hydrogen seal casing, the air and the hydrogen seals were cleaned and visually inspected. They were in good condition. However, customer decided to change seals and springs by new ones. New seals and springs were measured and found within drawing specifications. They were also dye penetrant inspected and ultrasonic tested. The hydrogen seal casing was cleaned, assembled, visually inspected and no signs of issues could be observed. The casing was mea
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | bda22bbe316b662447f29c73f4701fdf | 12 | 2021-05-31 | Repair | Hydrogen Seals, Stator | Red Eye Repair | 11 | Core, End Shield, End-winding, Greasing, High Voltage Bushings, Keybars, Lamination Damage, Red Eye Repair, Stator Winding, Step Iron, Wedges | In accordance with TIL-2260, a borescope inspection was performed on the generator stator Air Gap region with careful attention and focus on finding visual evidence of TE step iron core damage or greasing/red dusting.; In addition, the core compression nuts were inspected for visual signs of movement that could indicate a possible loose core.; Greasing, that was noted mostly within the CE end wedge/step-iron area, appeared to be signs of typical slot support movement when introduced to oil.; There were no signs of Red Oxide along the core iron and no signs of movement around the core compression nuts.; In accordance with TIL-2260, if no evidence of core looseness is seen, repeat this borescope inspection after 16,000 fired hours until such a time as the following inspections/ repairs can be completed at a planned outage. | GEK103566 | Red Eye Repair ¦ Core ¦ End Shield ¦ End-winding ¦ Greasing ¦ High Voltage Bushings ¦ Keybars ¦ GEK103566 | - 338X424 2.1.1 GT 1 - TIL-2260 Inspection - 338X424 Part Condition: Good Part Description: In accordance with TIL-2260, a borescope inspection was performed on the generator stator Air Gap region with careful attention and focus on finding visual evidence of TE step iron core damage or greasing/red dusting. In addition, the core compression nuts were inspected for visual signs of movement that could indicate a possible loose core. Greasing, that was noted mostly within the CE end wedge/step-iro
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 2f459e22c4d03e26312ac80a2779f484 | 5 | 2021-05-31 | Inspection | Field, Hydrogen Seals, Stator | Stator Findings Review | 10 | Core, End Shield, End-winding, Field Body, Greasing, Lamination Damage, Stator Winding, Step Iron, Turn Insulation Migration, Wedges | Recently, during planned outages, three 7FH2 generators were found with broken core laminations and loose core teeth in the turbine end (TE) step iron area, one of which also had loose core teeth at the collector end (CE).; Two other 7FH2 generators were forced from service in 2020 due to a stator ground issue caused by portions of the core lamination fingers breaking off and compromising the stator bar insulation.; Greasing was also observed at the CE & TE step iron area and first body package.; In total, there have now been six such findings of core damage reported, all on 7FH2s built by the same 3rd party.; During this outage, the Collector End (CE) & Turbine End (TE) outer end shield manway covers were removed to facilitate the borescope inspection of the accessible areas of the Stator Core, Stator End Winding Assembly, Stator End Winding Sup | ER-20210401-0868 | Stator Findings Review ¦ Core ¦ End Shield ¦ End-winding ¦ Field Body ¦ Greasing ¦ Lamination Damage ¦ ER-20210401-0868 | and operation. Recently, during planned outages, three 7FH2 generators were found with broken core laminations and loose core teeth in the turbine end (TE) step iron area, one of which also had loose core teeth at the collector end (CE). Two other 7FH2 generators were forced from service in 2020 due to a stator ground issue caused by portions of the core lamination fingers breaking off and compromising the stator bar insulation. Greasing was also observed at the CE & TE step iron area and first
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 12a9c48c5c3fe36e1bffc26eb6cdce18 | 269 | 2021-05-31 | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 10 | Core, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges | Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Pre-outage test:; Partial Discharge 1 Stator Winding Insulation Localized deterioration X X X O 1 O-R 2 O-R 2 Visual Inspection All Visible Components within the End Winding Compartment Cleanliness, foreign material, loose or displaced parts, damage, wear, d; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) ; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In 1 DC Leakage and Partial Discharge testing are optional but high |  | Polarization Index; DC Leakage ¦ Core ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings ¦ Hydrogen Seal Assembly | . Generator Turbine Generator Turbine GEK103566_M GEK 103566M Creating a More Effective Generator Maintenance 9 without prior permission of the copyright owner. Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Pre-outage test: H2 sniff test Generator Check any H2 leaks when unit under the H2 pressure X X X-R X-R X-R Pre-outage test: Partial Discharge 1 Stator Winding Ins
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 3325a96b10a450d2c00adf81e9389706 | 34 | 2021-05-31 | Inspection | Field, Stator | Stator Findings Review | 8 | End-winding, Field Body, Greasing, High Voltage Bushings, Retaining Rings, Stator Winding, Step Iron, Wedges | High Voltage Bushings (HVBs):; GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.2 GT 2 - Stator Visual Inspection - 338X427 CE Stator Bar-to-Bar Tie Greas ing GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.2 GT 2 - Stator Visual Inspection - 338X427 CE Stator Bar-to-Ba; For the field, the areas of interest consist of the field body, field wedges, field body plugs, field ventilation passages and the accessible areas of the retaining rings.; Field Body:; The accessible areas of the field body was inspected for contamination of rust or oil. |  | Stator Findings Review ¦ End-winding ¦ Field Body ¦ Greasing ¦ High Voltage Bushings ¦ Retaining Rings ¦ Stator Winding | . Loose stator end winding axial supports could result in GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.2 GT 2 - Stator Visual Inspection - 338X427 loose or broken ties between connection rings. This may lead to chafing with the “dusting” appearing on the connection rings. Excessive dusting may require replacing connection ring ties. Thru Bolts: This unit has a total of 22 axial support through bolts on the CE only. All bolts accessible for inspecting showed no signs of movement. All bolts ap
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 25bb05c4db94bf0649b8a8c528ef1d53 | 52 | 2021-05-31 | Inspection | Field, Hydrogen Seals, Stator | Stator Findings Review | 8 | Core, End Shield, End-winding, Field Body, Greasing, Retaining Rings, Step Iron, Wedges | Unit Access The left/right end shield inspection plates were removed from the turbine/collector end.; Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 2260 End-step iron 4.; Stator End Wedges b.; Core Step Iron Region c.; Limited Viewing Areas of the Stator Core e. |  | Stator Findings Review ¦ Core ¦ End Shield ¦ End-winding ¦ Field Body ¦ Greasing ¦ Retaining Rings | See content below. GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 GE Power Inspection & Life Extension Services Gas Turbine Generator Borescope Inspection Report DOMINION POWER Columbia GASTON, SC Unit Serial #: 338X424 Site Unit #: 1 May 31ST, 2021 GE Power Inspection & Life Extension Services Site and Unit Inspection Information Serial Number 338X424 Customer Dominion Site Columbia Location Gaston Unit Number 1 Equipment Model GE/ Hitachi CPM/Site Contact Kwan Inspector Chris Jenkins Generator S
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | f3ed1b1e81ca51203098fc568d3335b7 | 46 | 2021-05-31 | Inspection | Field, Stator | MAGIC Inspection | 8 | Amortisseur, End-winding, Field Body, MAGIC Inspection, Retaining Rings, Sub-slots, Turn Insulation Migration, Wedges | Field Body Plugs:; The accessible field body plugs were inspected for proper seating.; Continue to inspect the axial alignment of the field body wedges, slot amortisseur, and creepage blocks when the field is removed or via remote means i.e., [MAGIC Insitu (Robotics) or borescope).; Using a high-resolution borescope, a thorough visual inspection was performed on the field end-winding region underneath the CE Retaining Ring.; Each coil stack was inspected for elongation, distortion, signs of overheating, and turn-to- GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.4 GT 2 - Field Visual Inspection - End Windings - 338X427 turn insulation migration. | GEK 103566 | MAGIC Inspection ¦ Amortisseur ¦ End-winding ¦ Field Body ¦ Retaining Rings ¦ Sub-slots ¦ GEK 103566 | . Field Body Plugs: The accessible field body plugs were inspected for proper seating. All body plugs accessible appeared to be properly staked and secured with no signs of movement. Field Ventilation Passages: The field ventilation passages were inspected for obstruction from either debris or internal components such as creepage block migration that could effect proper cooling of the field during operation. This event can also result in thermal sensitivity that could cause overheating, bowing o
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | ac2c79ab753bf33996f87a6f33d5e465 | 23 | 2021-05-31 | Repair | Hydrogen Seals, Stator | Red Eye Repair | 8 | Core, End Shield, Greasing, Keybars, Lamination Damage, Red Eye Repair, Step Iron, Wedges | In accordance with TIL-2260, a borescope inspection was performed on the generator stator Air Gap region with careful attention and focus on finding visual evidence of TE step iron core damage or greasing/red dusting.; In addition, the core compression nuts were inspected for visual signs of movement that could indicate a possible loose core.; There was substantial greasing seen within the TE step iron region that indicated possible looseness of the stator core.; Some step-iron packages were seen with heavy greasing oozing from between the laminations.; Also, there was consistent greasing within the same laminates in the 4th package from the TE from the 3 o'clock position to the 9 o'clock position which indicates looseness in that section of the core. | ER-20210401-0868, GEK103566 | Red Eye Repair ¦ Core ¦ End Shield ¦ Greasing ¦ Keybars ¦ Lamination Damage ¦ ER-20210401-0868 ¦ GEK103566 | - 338X427 GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.1 GT 2 - TIL-2260 Inspection - 338X427 Part Condition: Poor Part Description: In accordance with TIL-2260, a borescope inspection was performed on the generator stator Air Gap region with careful attention and focus on finding visual evidence of TE step iron core damage or greasing/red dusting. In addition, the core compression nuts were inspected for visual signs of movement that could indicate a possible loose core. There was substanti
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 31de7b08410bc31d9d536c10f93a2fdf | 17 | 2021-05-31 | Inspection | Field, Stator | MAGIC Inspection | 7 | Amortisseur, End-winding, Field Body, MAGIC Inspection, Retaining Rings, Sub-slots, Wedges | For the field, the areas of interest consist of the field body, field wedges, field body plugs, field ventilation passages and the accessible areas of the retaining rings.; Field Body:; The accessible areas of the field body was inspected for contamination of rust or oil.; The general condition of the field body was satisfactory.; Field Wedges: |  | MAGIC Inspection ¦ Amortisseur ¦ End-winding ¦ Field Body ¦ Retaining Rings ¦ Sub-slots | . GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.1.2 GT 1 - Stator Visual Inspection - 338X424 CE Blue Water Based Paint Didn 't Adhere GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.1.2 GT 1 - Stator Visual Inspection - 338X424 CE Blue Water Based Paint Didn 't Adhere GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.1.2 GT 1 - Stator Visual Inspection - 338X424 CE Blue Water Based Paint Didn 't Adhere GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.1.3 GT 1 - Field Visual Inspection - Air Gap - 33
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 0193d85d43dbf1a0894d16ba8e083829 | 267 | 2021-05-31 | Electrical | Field, Stator | DC Leakage | 7 | Core, DC Leakage, Focused Generator Inspection, Retaining Rings, Stator Winding, Wedge Looseness, Wedges | Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened materia; As the stator core is exposed during a rewind, a detailed inspection of the core is recommended including at minimum a visual inspection, EL-CID (or low flux test) and core tightness testing.; However, this is also an opportune time to perform a Core Ring Test (High Induction Test/ Core Ring Test or PULSAR) and to retighten the core compression features if/where applicable. |  | DC Leakage ¦ Core ¦ Focused Generator Inspection ¦ Retaining Rings ¦ Stator Winding ¦ Wedge Looseness | . 6 Subject to change based on risk mitigation actions. Any questions should be discussed with the local GE service representative. In the absence of operating experience and resulting condition assessments, Table 2 lists the recommended inspection intervals for turbo- generators. Generators can be inspected commensurate with the associated turbine inspection outage. These initial intervals should be reviewed and adjusted as operating and inspection experiences are accumulated. GEK103566_M GEK 1
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 066f516e0654d2b2627e29d288570741 | 276 | 2021-05-31 | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically constructed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . Many of the tests require special equipment that has been properly maintained and calibrated to ensure accurate results. 5 . Visual Inspection A visual inspection, performed at every inspection by an experienced individual, can uncover unit conditions previously undetected or can validate monitoring findings. In some instances, electrical testing will only detect issues when the stator and rotor insulation systems have been significantly compromised. For example, there is no definitive test fo
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | a3874e9099a59330d5d363f609069dd7 | 260 | 2021-05-31 | Repair | Hydrogen Seals, Stator | Red Eye Repair | 5 | Core, End Shield, Keybars, Red Eye Repair, Step Iron | If no evidence of core looseness is seen, repeat this borescope inspection after 16,000 fired hours until such a time as the following inspections/repairs can be completed at a planned outage.; With field removed from stator, test tightness of the Core ID (knife check) Based on Core ID tightness checks, install shims, as required.; Apply red eye epoxy to step iron CE and TE.; The above inspections will require end shields, gas shields, generator field and three coolers to be removed.; At the current time, recommended follow-up scope for significant findings could potentially include core shim repairs or, in some cases, a partial restack and a full stator rewind. | GEK103566 | Red Eye Repair ¦ Core ¦ End Shield ¦ Keybars ¦ Step Iron ¦ GEK103566 | . If no evidence of core looseness is seen, repeat this borescope inspection after 16,000 fired hours until such a time as the following inspections/repairs can be completed at a planned outage. At the next planned major outage, in addition to standard scope per GEK103566, perform the following inspections and repairs: With field removed from stator, test tightness of the Core ID (knife check) Based on Core ID tightness checks, install shims, as required. Visually inspect for clearance between f
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 25618c0123a8116991a3bce72ab85f3d | 258 | 2021-05-31 | Inspection | Stator | Stator Findings Review | 5 | Core, Greasing, Lamination Damage, Stator Winding, Step Iron | 18 FEBRUARY 2021 TIL-2260r1 Recently, during planned outages, three 7FH2 generators were found with broken core laminations and loose core teeth in the turbine end (TE) step iron area, one of which also had loose core teeth at the collector; Two other 7FH2 generators were forced from service in 2020 due to a stator ground issue caused by portions of the core lamination fingers breaking off and compromising the stator bar insulation.; Greasing was also observed at the CE & TE step iron area and first body package.; In total, there have now been six such findings of core damage reported, all on 7FH2s built by the same 3rd party.; Heavy greasing and slit iron punching damage at turbine end (TE) The root cause analysis (RCA) concluded that the core lamination damage and looseness was caused by a combination of the below contributors: |  | Stator Findings Review ¦ Core ¦ Greasing ¦ Lamination Damage ¦ Stator Winding ¦ Step Iron | . direct, consequential or special that may be alleged to have been incurred as result of applying this information regardless of whether it is claimed that GE is strictly liable, in breach of contract, in breach of warranty, negligent, or is in other respects responsible for any alleged injury or damage sustained by your organization as a result of applying this information. This Technical Information Letter contains proprietary information of equipment described. This document shall not be rep
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | fe251ae533f964f60f278844950b4ad9 | 272 | 2021-05-31 | Electrical | Stator | DC Hipot | 5 | DC Hipot, End-winding, High Voltage Bushings, Stator Winding, Wedges | 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 5 This test does not apply to units with asphalt stator windings, GVPI windings (Global Vacuum Pressure Impregnated) or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds.; 13 Alfa coefficient test is applicable to stator winding with the flat lateral support system. |  | DC Hipot ¦ End-winding ¦ High Voltage Bushings ¦ Stator Winding ¦ Wedges | . 2 For hydrogen cooled generators Off-Line Partial Discharge Testing with the unit open to air may provide additional diagnostic information. 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators. 4 An equivalent inspection via digital trending and analysis may be suitable; contact your local GE Service Representative. Dimensional and NDT test are recommended o
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | d7fd5f53e908555ae72efbed88b7bef6 | 25 | 2021-05-31 | Inspection | Stator | Stator Findings Review | 5 | Core, End-winding, Greasing, High Voltage Bushings, Stator Winding | GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.1 GT 2 - TIL-2260 Inspection - 338X427 TE_Core Iron Greasing - 4th Pa ckage In GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.1 GT 2 - TIL-2260 Inspection - 338X427 TE_Core Iron Greasing - ; The areas of interest, within the end winding region consist of the following, accessible areas of the inner/outside diameter of the stator end winding, accessible areas of the inner/outside diameter of the stator end winding support system; The inner/outside diameter sections of the stator end windings were visually inspected for general cleanliness, dirt/oil contamination, foreign material, and obvious damage to the stator winding insulation.; No obvious damage was seen on the accessible areas of the stator winding insulations.; Dusting, greasing, and bar abrasion are indications of movement during operation. |  | Stator Findings Review ¦ Core ¦ End-winding ¦ Greasing ¦ High Voltage Bushings ¦ Stator Winding | . This TIL can be considered complete when the above recommendations have been completed or a partial restack and full stator rewind have been performed. GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.1 GT 2 - TIL-2260 Inspection - 338X427 TE_Core Iron Greasing - 4th Pa ckage In GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.1 GT 2 - TIL-2260 Inspection - 338X427 TE_Core Iron Greasing - 4th Pa ckage In GEGEGE CALL-OUT - 297842, CALL-OUT - 338X424 2.2.1 GT 2 - TIL-2260 Inspection - 338X427 TE
UNI035490 | COLUMBIA | Field_Service_Report_ProjectID_A-1656272_FSP-305442_C-10358711.pdf | 297842 | Gas Turbine | 559f0d63256f4286ef6a3e268aa0ac17 | 272 | 2021-05-31 | Electrical | Field, Stator | AC Impedance | 5 | AC Impedance, End-winding, Gooseneck, Main Lead, Stator Winding | Phos-Free 3 H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Test Inspection Objectives and Assessment Borescope Robotic Rotor-In Borescope Robot; Table 6 Recommended Rotor Test Rotor Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescope Robotic Rotor-In Winding Copper Resistance Rotor Winding Checks for poor connections and breaks X X X O X X In |  | AC Impedance ¦ End-winding ¦ Gooseneck ¦ Main Lead ¦ Stator Winding | . Test requires rotor removal. GEK103566_M GEK 103566M Creating a More Effective Generator Maintenance 12 without prior permission of the copyright owner. Table 5 Recommended Water-Cooled Stator Leak Tests for High Oxygen Systems 1,2 What about legacy Alstom stainless steel windings?? Stator Clip-Strand Braze: Phos Containing Global Epoxy Injection or Clip-Strand Braze: Phos-Free 3 H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig SLMS, Bagged Vent, or No
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | aefc947cbd72f2878d99546018aed4a7 | 206 | 2021-04-21 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | (a) Rev 0.0 - 10/01/04 GE Energy Proprietary Information D316512 - H2 Seal Casing -338X390 T… Section of damaged thread – due to the location in the lower half end shield it will require the removal of the lower half bearing, drilling out a | EM3404 | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . 15.999 15.999 15.999 15.999 CLEARANCE 0.012 0.008 0.009 H2 SEAL SPRING MEASUREMENTS TURBINE END COLL. END UPPER LOWER UPPER LOWER LENGTH (±1/16 in.) WIRE DIA. COIL DIA. GRADIENT (#/in) Testing Data a. Seal Oil Flow G.P.M. b. Hydrogen Pressure P.S.I. c. Unit Speed R.P.M. Scavenging 338X390 Tom Mulvey English - inches 1 2 3 4 5 6 COIL DIA. WIRE DIA. LENGTH ST00066 D316501 Sheet: (a) Rev 0.0 - 10/01/04 GE Energy Proprietary Information D316501 - H2 Seals - As Left -338X390 g Hydrogen Seal Casing
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | dad5fa4eb1ab21973f982f6a89b48cc3 | 201 | 2021-04-21 | Mechanical | Hydrogen Seals | Generator Pressure Test; Blue Check | 3 | Blue Check, End Shield, Generator Pressure Test | · Gas side H2 seal was above tolerance and replaced · Air side H2 seal was within tolerance and reused · Both H2 seals springs were replaced with new parts · Damaged Bolt hole was identified on lower half end shield – required drilling and ; It was replaced · Both H2 seals springs were replaced with new parts CE - Air Side Blue check 2 CE - Air Side Blue check CE gas side blue check 2 CE gas side blue check GEGEGE HGP - 298936 |  | Generator Pressure Test; Blue Check ¦ Blue Check ¦ End Shield ¦ Generator Pressure Test | All seals were lapped to the associated housing prior to installation. An air test was conducted by the customer and deemed satisfactory prior to unit start up. CE: · Gas side H2 seal was above tolerance and replaced · Air side H2 seal was within tolerance and reused · Both H2 seals springs were replaced with new parts · Damaged Bolt hole was identified on lower half end shield – required drilling and heli- coil install TE · Gas side H2 seal was above tolerance and was replaced · Air side seal w
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | d4b4f987e4be1701518d7b363afde1f4 | 6 | 2021-04-21 | Mechanical | Hydrogen Seals | Generator Pressure Test | 3 | End Shield, Generator Pressure Test, Hydrogen Seal Assembly | · CE bearing is within tolerance from a clearance perspective and has passed NDE – bearing was reused · Gas side H2 seal was above tolerance and replaced · Air side H2 seal was within tolerance and reused · Both H2 seals springs were replac |  | Generator Pressure Test ¦ End Shield ¦ Hydrogen Seal Assembly | On March 25th, 2021, FieldCore mobilized, field engineering, labor and tooling to support the planned hot gas path inspection on Unit 401 (SN: 298936). LOTO was walked down prior to the commencement of work. During the outage all capital components were removed and inspected. The turbine compartment roofing was removed. The turbine casing was removed, cleaned and inspected. The exhaust flex seals were inspected and replaced per customer request during the outage. Opening clearances were recorded
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | 74cf2bacac176a879c65069ffdaecb17 | 2 | 2021-04-21 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 GAS TURBINE (298936 ¦ SY0098444) __________ 2 1 Summary __________ 2 1.1 Timers and Counters __________ 2 1.2 Executive Summary __________ |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 GAS TURBINE (298936 ¦ SY0098444) __________ 2 1 Summary __________ 2 1.1 Timers and Counters __________ 2 1.2 Executive Summary __________ 2 1.3 Work Scope __________ 4 2 Technical __________ 5 2.1 TIL/ETC __________ 5 2.2 Recommendations __________ 10 3 Turbine __________ 14 3.1 Inlet Section __________ 14 3.1.1 Inlet Guides Vanes __________ 14 3.2 Combustion Section __________ 18 3.2.1 Gas and
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | e46d96afd38ec92c28a3947950d17d89 | 202 | 2021-04-21 | Mechanical | Hydrogen Seals | Blue Check | 2 | Blue Check, Hydrogen Seal Assembly | TE air LH blue check TE air UH blue check TE gas LH blue check TE gas UH blue check GEGEGE HGP - 298936 Generator typical Hydrogen Seal Casing - typical GEGEGE HGP - 298936 Hydrogen Seal Oil System Date(m/d/y) 4/7/2021 Generator Serial No. |  | Blue Check ¦ Hydrogen Seal Assembly | TE air LH blue check TE air UH blue check TE gas LH blue check TE gas UH blue check GEGEGE HGP - 298936 Generator typical Hydrogen Seal Casing - typical GEGEGE HGP - 298936 Hydrogen Seal Oil System Date(m/d/y) 4/7/2021 Generator Serial No. Prepared by Units recorded in INSPECTIONS & CHECKS Main Seal Oil Pump Seal Oil Press. Gages CODE Emerg. Seal Oil Pump at Unit Centerline X - Work Carried Out Gas Side Drain Float, High Level Alarm on Hydrogen N - Not Done Trap and Valves Detraining Tank NA - N
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | e02e960c8d38586a1f2cc8458b351612 | 180 | 2021-04-21 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Out board oil deflectors were removed and inspected. |  | Oil Deflector Alignment ¦ Oil Deflectors | Out board oil deflectors were removed and inspected. All components were reused during this interval. GEGEGE HGP - 298936 Oil Deflector
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | 262e29d18c12a19cacc3413a147bd054 | 181 | 2021-04-21 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Max Top Bottom Sides CE Outer 10 8 11 11 30 10 11 8 30 25 13 11 CE Inner 9 5 10 10 20 10 10 5 20 17 8 10 TE Outer 9 7 9 9 28 8 9 7 28 23 12 9 TE Innner 10 5 10 11 21 12 11 5 21 17 9 11 Comments Recommend Replacing OB oil deflectors at next |  | Oil Deflector Alignment ¦ Oil Deflectors | Date (m,d,y) 4/14/2021 Turbine Serial No. 338X390 Prepared by Tom Mulvey Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Median Min. Max Top Bottom Sides CE Outer 10 8 11 11 30 10 11 8 30 25 13 11 CE Inner 9 5 10 10 20 10 10 5 20 17 8 10 TE Outer 9 7 9 9 28 8 9 7 28 23 12 9 TE Innner 10 5 10 11 21 12 11 5 21 17 9 11 Comments Recommend Replacing OB oil deflectors at next planned outage ST00381 2 OIL DEFLECTOR LEFT RIGHT 6 1 4 3 5 ROTOR D309302 Sheet: (a) Rev 0.0 - 09/03/93
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | 32b47ed39ff0230f0395d8d63cfb7993 | 185 | 2021-04-21 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | Date 4/9/2021 Turbine S/N 338X390 Prepared by Tom Mulvey FSR # Inspected by TM Photos Enclosed? No Inspection type Found/ As Left Bearing Bearing Forward or Turbine End Aft or Generator End Journal Vertical Clearan No. Type A-Dia B-Dia C-Dia A-Dia B-Dia C-Dia Dia. Mils Mils/In T3 (TE) - Removed Elip. 16.041 16.042 16.0230 16.041 16.042 16.023 15.999 24 1.5 T4(CE) - Removed/Installed Elip 16.038 16.039 16.024 16.039 16.038 16.023 15.999 24 1.5 T3(TE) - Installed Elip. 16.039 16.040 16.020 16.040
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | c035f11fb11907229a857e47f0b20a63 | 14 | 2021-04-21 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Next Outage Parts All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Next Outage Parts All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. GEGEGE HGP - 298936
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | 19e0501c27189c979ce33ca492043f04 | 27 | 2021-04-21 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted.
UNI048334 | Astoria Energy, LLC | Field_Service_Report_ProjectID_A-1377422_FSP-280265_C-10348120.pdf | 298936 | Gas Turbine | bbec3a553d5083d9c88a9b834705304d | 8 | 2021-04-21 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | Outage Type: Planned Outage Turbine Hot Gas Path Inspection Generator Bearings, Hydrogen Seals GEGEGE HGP - 298936
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | b96643ca5a172678e224c78b1744a599 | 2 |  | Electrical | Field, Hydrogen Seals, Stator | Winding Resistance; Polarization Index | 17 | Collector Rings, Core, End Shield, End-winding, Fan Blades, Field Body, Focused Generator Inspection, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 3 1.4 Work Scope __________ 8 1.5 Quality __________ 8 2 Technical __________ 9 2.1 Recommendatio |  | Winding Resistance; Polarization Index ¦ Collector Rings ¦ Core ¦ End Shield ¦ End-winding ¦ Fan Blades ¦ Field Body | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 3 1.4 Work Scope __________ 8 1.5 Quality __________ 8 2 Technical __________ 9 2.1 Recommendations __________ 9 3 Turbine __________ 10 3.1 Inlet Section __________ 10 3.1.1 T1 Journal Bearing __________ 10 3.1.2 Thrust Bearing __________ 13 3.1.3 Inlet Bellmouth __________ 13 3.1.4 Inlet Guides Vanes __________ 14 3.1.5 Inlet Bleed Heat __________ 18 3.
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 1e998f5099260a3bd041714d826de30e | 65 |  | Electrical | Field, Stator | Winding Resistance; Polarization Index | 12 | AC Impedance, Core, End-winding, Field Body, Focused Generator Inspection, Greasing, MAGIC Inspection, Polarization Index, Retaining Rings, Wedge Tightness Test, Wedges, Winding Resistance | The intent was to carry out magic inspection and provide condition assessment of the generator mechanical parts ,stator and field.; The inspection plan included complete visual inspection of the stator core and field body, wedge map, end winding inspection, electrical tests to assess condition of winding insulation and borescope inspection under retaining ring of the fi; The activities were carried out by generator collector end end- shield and associated component dis- assembled to facilitate full inspection of the stator and the field through MAGIC Inspection.; Stator slot wedges were tested for tightness.; Noticed minor level greasing in CE and TE end winding ties. | GEK 103566 | Winding Resistance; Polarization Index ¦ AC Impedance ¦ Core ¦ End-winding ¦ Field Body ¦ Focused Generator Inspection ¦ Greasing ¦ GEK 103566 | Part Description: This report documents the Generator major Inspection with MAGIC and associated activities performed on the Gas Turbine Generator (338X600) GT#11 at DHURUMA O & M COMPANY, Saudi Electricity PP11 Plant from 05th Oct 2020 to 30th Oct 2020. The intent was to carry out magic inspection and provide condition assessment of the generator mechanical parts ,stator and field. The inspection plan included complete visual inspection of the stator core and field body, wedge map, end winding
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 14fb5adab470a95f5f0b3898978ff857 | 107 |  | Inspection | Field, Stator | MAGIC Inspection | 6 | MAGIC Inspection, Main Lead, Pole Jumper, Step Iron, Sub-slots, Wedges | (518) 385-3178 Operator Marian Generator Specialist Saravanakumar Location Comments Photo Identification Tape Counter TE 0 DEG TE RR NOSE Image 01 0DEG BALANCE WEIGHT Image 02 TE SLOT 20 END WEDGE TYPICAL Image 03 TE SLOT 20 STEP IRONS Imag; (518) 385-3178 Operator Marian Generator Specialist Saravanakumar TERR INSULATION STACKING Image 45 TERR TYPICAL RR NOSE Image 46 TERR INSULATION BLOCKS Image 47 TERR INSULATION STACKING Image 48 TERR SUBSLOT Image 49 TERR SUBSLOT Image 50 |  | MAGIC Inspection ¦ Main Lead ¦ Pole Jumper ¦ Step Iron ¦ Sub-slots ¦ Wedges | g GE Energy Services Inspection & Repair Services Magic Photo I.D.Worksheet Job # 1 River Road, Bldg. 55 Rm. 263 Generator # GT 11 (338X600) (518) 385-1751 , 8*235-1751 Date 12-Oct-2020 Fx: (518) 385-3178 Operator Marian Generator Specialist Saravanakumar Location Comments Photo Identification Tape Counter TE 0 DEG TE RR NOSE Image 01 0DEG BALANCE WEIGHT Image 02 TE SLOT 20 END WEDGE TYPICAL Image 03 TE SLOT 20 STEP IRONS Image 04 SLOT 17 STATOR OVERVIEW Image 05 SLOT 19 AIR VENT Image 06 SLO20
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 3dc1ff5bc1d6de35c1352cebf855fa9d | 67 |  | Repair | Field, Stator | Red Eye Repair | 5 | Collector Rings, End-winding, Fan Blades, Greasing, Red Eye Repair | •CE and TE minor greasing noticed in end winding ties.; Red eye repair carried out during this outage.; Minor Polishing carried out •Bearings and Fan blades NDT inspection carried out and found in good in condition. |  | Red Eye Repair ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ Greasing | Part Description: •Oil leak noticed from piping flange, CE Sight Glass, CE and TE bearing TC Gland. All oil leaks fixed during this outage. • Minor oil leak noticed from CE sight glass. Replaced CE sight glass O ring during this outage. •Oil leaks noticed from CE and TE bearing TC glands. Replaced CE and TE bearing TC glands. CE bearing TC gland connection head found damaged condition. Replaced CE TC gland connection head during this outage. •CE and TE seals were found in good condition. CE and
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 8cce36385cc47f57e8954a826079a822 | 90 |  | Inspection | Stator | Wedge Tightness Test | 4 | Focused Generator Inspection, Greasing, Wedge Tightness Test, Wedges | Stator slot wedges were checked for migration, red dusting , looseness and abnormality.; There were no indications of migration of wedges or red dusting.; Minor Greasing were noticed in slot exits.; Wedge tightness test revealed wedges to be.; Wedges marked green were tight and those marked yellow were found hollow. |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ Wedges | Part Description: Stator slot wedges were checked for migration, red dusting , looseness and abnormality. There were no indications of migration of wedges or red dusting. Minor Greasing were noticed in slot exits. Wedge tightness test revealed wedges to be. Wedges marked green were tight and those marked yellow were found hollow. Red marked are loose.
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | ef890c7c45ac0174f230822ad8962c76 | 78 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | Collector and Turbine end seal housing, seal rings and springs were inspected during this outage. | EM3404 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings ¦ EM3404 | Part Description: Collector and Turbine end seal housing, seal rings and springs were inspected during this outage. No abnormalities noticed. CE and TE H2 seals were replaced by new one during this outage. New seals lapping and blue contact check carried out during this outage. g Hydrogen Seal Casing Collector End Casing Date (m/d/y) Turbine Serial No. Prepared by Generator Serial No. 338X600 Units INSPECTIONS & CHECKS CODE Cleaned Joints X X Work Carried Out Dowels X N Not Done Assembly per NA
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 80bc5a4c3eabc14bab647fc1671d7fb1 | 10 |  | Inspection | Field, Stator | MAGIC Inspection | 4 | Core, End-winding, MAGIC Inspection, Retaining Rings | · MCC (Motor control center) PM · Battery charger PM and Discharge test · Water Injection PM · Water Wash Skid PM · Air Processing Unit PM 3- Generator MAGIC Inspection:; The intent was to carry out MAGIC inspection and provide condition assessment of the generator mechanical parts, stator and field.; The inspection plan included complete visual inspection of the stator core and field, body, end winding inspection, electrical tests to assess condition of winding insulation and borescope inspection under retaining ring of the field |  | MAGIC Inspection ¦ Core ¦ End-winding ¦ Retaining Rings | This report describes the MI activities performed on GT-11 unit SN 299014 at PP11, Riyadh, Saudi Arabia. MI activities main permit was received on 5th of October at 20:52 hrs. Lock- out/ Tag-out walk down was performed by GE Mechanical TFA and DHOM O&M team. GE provided the parts and manpower for the outage and customer provided the crane and scaffolding. As per the CSA contract the outage scope was defined mainly GT Major inspection ,Gen magic and Auxiliary scope. It is detailed below and in re
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 3f8100777429e6c63408d6672ceea3db | 6 |  | Inspection | Stator | Wedge Tightness Test | 4 | Focused Generator Inspection, MAGIC Inspection, Wedge Tightness Test, Wedges | __________ 99 4.7.1 MAGIC Inspection Pictures __________ 99 4.7.2 Visual Inspection Pictures __________ 116 5 Controls System __________ 121 6 Quality Checkpoint (QCP) __________ 122 GE Power Power Services GEGEGE 299014 SAUDI ELECTRICITY C |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Wedges | __________ 99 4.7.1 MAGIC Inspection Pictures __________ 99 4.7.2 Visual Inspection Pictures __________ 116 5 Controls System __________ 121 6 Quality Checkpoint (QCP) __________ 122 GE Power Power Services GEGEGE 299014 SAUDI ELECTRICITY COMPANY CENTRAL REGION RIYADH PP11 6.1 Attachments __________ 122 7 PIPO __________ 140 7.1 Combustion __________ 140 7.2 Hot Gas Path __________ 143 7.3 Rotor __________ 164 8 Appendix __________ 165 8.1 Attachments __________ 165 GE Power Power Services GEGEG
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | b6cafcdc8307e0a7d97944072b7c3f35 | 13 |  | Mechanical | Field, Stator | Blue Check | 4 | Blue Check, Collector Rings, End-winding, Greasing | Blue check failed and replaced with another bearing.; Repaired · Minor end winding ties greasing noticed in 49 & 50 ,13&14 and 15&16 Corrective action:; Greasing cleaned · 2,3,4,5,6,7,8,9 and 11 end winding support hardware’s found loose Corrective action: | ER-20201010-0283, ER-20201012-0547, ER-20201012-0613, ER-20201013-0132, ER-20201014-0066, ER-20201014-1095, ER-20201017-0063, ER-20201022-0342, ER-20201025-0124, ER-20201027-0126, ER-20201027-0130 | Blue Check ¦ Collector Rings ¦ End-winding ¦ Greasing ¦ ER-20201010-0283 ¦ ER-20201012-0547 | . Corrective action: This is due to sand coming inside the load compartment area. Seals replaced. · Bearing-2 UT and PT found acceptable. Minor pitting marks on one LH pad observed. Corrective action: Engineering case was opened, approved to install back. · Bearing-02 Proximity cable found stuck inside the drain pipe conduit. Corrective action: Rectified . · Bearing-1 UT and PT is completed. One Lift oil diamond pocket corner have some erosion. Corrective action: Engineering case was opened. Blu
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 9c8c3e55a2be4ca88b9b1cfff2b0159f | 124 |  | Repair | Field, Stator | Red Eye Repair | 4 | Collector Rings, Greasing, Keybars, Red Eye Repair | Oil Leak noticed from CE sight glass Oil leak noticed from porting valve Inspection Pictures Oil Leak noticed from TE sight glass CE bearing drain TC leak CE Bearing TC Gland As found CE journal Visual Inspection Pictures TE Bottom Bearing |  | Red Eye Repair ¦ Collector Rings ¦ Greasing ¦ Keybars | Oil Leak noticed from CE sight glass Oil leak noticed from porting valve Inspection Pictures Oil Leak noticed from TE sight glass CE bearing drain TC leak CE Bearing TC Gland As found CE journal Visual Inspection Pictures TE Bottom Bearing As found condition CE Bottom Bearing as found condition Inspection Pictures H2 seal Blue contact check CE Bearing IR Check Final cleaning between shields CE H2 seal Visual Inspection Pictures CE Corona Indication TE Corona indication Inspection Pictures Axial
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | a5a8040cd2a9de1fbbf565ac263419b8 | 94 |  | Electrical | Stator | DLRO; Winding Resistance | 3 | DLRO, Stator Winding, Winding Resistance | The test is carried out using a Digital Low Resistance Ohmmeter (DLRO).; g Armature Winding Resistance Equip Code Single Terminal Date (m/d/y) 10/18/2020 Turbine Serial No.; (a) Rev 1.1 - 04/28/2017 D3162041 Stator winding resistance |  | DLRO; Winding Resistance ¦ DLRO ¦ Stator Winding ¦ Winding Resistance | Part Description: Winding DC resistance Purpose: DC resistance of a winding is a measure of abnormalities arising from loose connections, broken connections, high contact resistance at brazed joints. Interpretation of results is usually based on comparison of measurements made at site to data of tests carried out at factory or during previous shutdown. Agreement within 2-3% of any of the above comparisons is usually considered satisfactory. Resistance being temperature specific, it is required t
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | 2cc2eab74dda3f9633cd3633a10afc42 | 103 |  | Electrical |  | DLRO; Winding Resistance | 3 | DLRO, Polarization Index, Winding Resistance | The readings of insulation resistance and polarization index were good, indicating healthiness of the insulation system.; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 11.32 1.70 6.66 20.22 3.00 6.74 30.26 4.50 6.72 42.96 6.30 6.82 50.12 7.30 6.87 60.46 8.60 7.03 70.00 9.90 7.07 80.00 11.20 7.14 90.01 12.30 7.32 100.40 13.50 7.44 INSULATION RESISTANC AT 5; CAL Due Date 1000-387/1111 21-07-2021 809 20-06-2021 5297-1211 20-06-2021 Date NA Turning Gear Hrs Check per TM4010 8 Point Resistance Check (Optional - Except for 390H and certain 450H & 9A5 units) - TM4010 and TM4030 Factory @25 ºC Variac | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | Part Description: IR & PI test was carried out on generator field at various stages. The readings of insulation resistance and polarization index were good, indicating healthiness of the insulation system. The results of final IR & PI test data, are tabulated and plotted in the attached data sheet . Impedance readings taken during the outage are at field in standstill position. The test data is recorded in form D316303. The curve obtained is consistent throughout. This suggests that there are no
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | e20283fe43df67f1e3e0ea6de9dc51de | 91 |  | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | Insulation Resistance and Polarization Index Test (IR & PI) Purpose:; On generator stator winding, a 5000 V DC is applied to the individual phase with respect to ground, with other two phases grounded.; The readings of insulation resistance and polarization index were satisfactory, indicating healthiness of the insulation system.; Stator Winding Insulation Resistance / HV Proof Tests Generator Test and Inspections Date 10/30/2020 Turbine No.:; Failed test at [KV/Time(sec)] Excitation Voltage (Volts) NA Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044. | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Description: Insulation Resistance and Polarization Index Test (IR & PI) Purpose: IR/PI test is the simplest test to assess the condition of insulation of a winding. The IR test measures the resistance of electrical insulation between the copper conductors and the core of the stator. PI test is a variation of the IR test. PI is the ratio of IR measured after voltage has been applied for 10 minutes to the IR measured after one minute. Low IR & PI value indicate that tested winding may be con
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | e4d6932e34f73cbda4e0be68324b9d65 | 90 |  | Repair | Stator | Red Eye Repair | 3 | End-winding, Greasing, Red Eye Repair | Minor level greasing was noticed on CE and TE some end winding ties.; CE and TE End winding oil and greasing was cleaned with GE recommended solvent .; Minor greasing was noticed in CE and TE bar ties .; All greasing area cleaned and red eye repair was carried out during this outage. |  | Red Eye Repair ¦ End-winding ¦ Greasing | Part Description: Minor level greasing was noticed on CE and TE some end winding ties. End winding ties were found in good condition. TE two end winding ties were found loose in 2 clock position. Both ties were removed and replaced by new one during this outage. CE and TE End winding oil and greasing was cleaned with GE recommended solvent . Minor greasing was noticed in CE and TE bar ties . All greasing area cleaned and red eye repair was carried out during this outage. Minor corona indication
UNI076270 | RIYADH PP11 | Field_Service_Report_ProjectID_A-1492570_FSP-245670_C-10326741.pdf | 299014 | Gas Turbine | e4214a1cd7237eafd8eb531378924d2b | 102 |  | Electrical |  | Flux Probe Resistance | 2 | Flux Probe Resistance, Flux probe resistance | 1 - 2 ohms 1 - 3 ohms 2 - 3 ohms 208.6 208.8 208.5 206.9 207.1 207.8 128.1 127.7 127.8 23 HG-2 18900 Flux Probe Resistance measure by Multimeter 8.3 Ohm Heater Resistance between Phases IR @ 500v @ 1min MOhms 23 HG-1A 474 23 HG-1B 446 Space |  | Flux Probe Resistance ¦ Flux probe resistance | . 338X600 Prepared by Saravana Turbine Serial No. 299014 As Left: 1 - 2 ohms 1 - 3 ohms 2 - 3 ohms 208.6 208.8 208.5 206.9 207.1 207.8 128.1 127.7 127.8 23 HG-2 18900 Flux Probe Resistance measure by Multimeter 8.3 Ohm Heater Resistance between Phases IR @ 500v @ 1min MOhms 23 HG-1A 474 23 HG-1B 446 Space Heater_D316401 Page 95 of 287 0 Table of Contents 1- MCC (Motor control center) PM 2- Battery charger PM and Discharge test 3- Valves Removal and Installation Photo 4- Motors and Pumps Removal
UNI235470 | Ninemile Point | Field_Service_Report_ProjectID_A-1617124_FSP-295687_C-10351294.pdf | 299140 | Gas Turbine | 5871537afe2b7f33b12c7eb1b38dfbf4 | 36 |  | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | . GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the The S16 vanes that were inspected along the lower half of the unit contain signs of twisting (.030”) on the base of the vanes. A small gap (.115”) was also observed at the left horizontal joint. The R17 blades that were inspected contain a minor nick on the leading edge side of one blade. The S17 vanes that were

## Summary
Metric | Value
Trains Analyzed | 14
Train IDs | UNI025979, UNI034468, UNI035490, UNI035546, UNI036492, UNI036579, UNI036868, UNI048334, UNI067472, UNI072122, UNI076270, UNI222464, UNI235470, UNI235471
Seed ESNs | 290T505, 336X882, 337X788, 338X381, 337X661, 761X301, 337X474, 337X475, 338X424, 436X023, 336X919, 338X600, 338X340, 338X390, 337X510
Total ESNs Resolved | 28
Unique PDFs Scanned | 80
Metadata Gaps Found | 60
Confirmed by Keyword | 9
Unconfirmed (GT-only reports) | 51
Events Matched by Date | 46
Generator Scope Candidate Chunks | 125
Generator Scope Candidate PDFs | 16