## FSR Tagging Gaps
Train ID | Plant Name | Tagged ESN | Tagged Equipment Type | Missing ESN | Missing Equipment Type | PDF Name | Document ID | Report Issued Date | Matched Event Date | Event Type | Sibling Event Type | Sibling Event ID | Field Scope | Days After Event | Gap Confirmed | Keyword Matches | Keywords Found | Sample Excerpt
UNI036482 | Moss Landing | 270T484 | Steam Turbine | 290T484 | Generator | Field_Service_Report_ProjectID_A-1939570_EV-181176_EVP-552961.pdf | a63b915b-2c2f-4f7e-9753-13d9edfd138d | 2025-06-23 | 2025-05-03 | Call-Out | Major Inspection (Robotic) | 177101 | TA & Craft Labor | 51 | NO | 1 | Seal Rings | . Particle Main Seat Inspection X Inspection of Equalizer UT Ultrasonic Intercept Valve Disc PT Penetrant Pressure Seal Head X VALVE CLEARANCE LEFT RIGHT Before After Before After Cleaning Cleaning Cleaning Cleaning L Bushing ID 10.135 10.135 TRY BAR. Crosshead OD 10.126 10.126 Clearance 0.009 0.009 B Bushing ID 2.753 2.753 TRY BAR Stem OD 2.741 2.742 Clearance 0.012 0.011 Bushing ID 2.753 2.753 D Stem OD 2.741 2.742 Clearance 0.012 0.011 H Bushing ID TRY BAR Stem OD Clearance Bushing ID J Stem
UNI036482 | Moss Landing | 270T484 | Steam Turbine | 290T484 | Generator | Field_Service_Report_ProjectID_A-1937452_EV-180503_EVP-552737.pdf | a96d026f-51ec-472e-8b22-c696c2e62e2c | 2025-04-25 | 2025-04-11 | Call-Out |  |  | TA & Craft Labor | 14 | NO | 0 |  | nd Date: 11 Apr 2025 ESN/SY: 270T484 ¦ SY0073323 Generator Field Serial Number: 290T484 Oracle Project ID: A-1937452 ¦ EV-180503 ¦ EVP-552737 Report Issued: 25 Apr 202
UNI036482 | Moss Landing | 270T484 | Steam Turbine | 290T484 | Generator | Field_Service_Report_ProjectID_A-1613270_FSP-294850_C-10350768.pdf | a4d96c19-6bf4-47ea-996c-196bf467ea9a | 2021-06-14 | 2021-05-08 | Call-Out |  |  | TA & Craft Labor | 37 | NO | 2 | Blue Check, Seal Rings | Part Description: Reheat Stop Valve’s Combined Intercept Valve’s. Disassembled, cleaned, and inspected. Pressure seal head back seats were lapped and blue checked. Bushing were honed and try bar check. All components were NDE’ed. The seats were stoned with cracking stones heavily and required many hours of lapping. Blue contact checks on seat to dics showed good. The left side Intercept valve had thread damage on 7 studs that were removed and replaced with new studs by UPS Machining. The actuato
UNI035965 | Hanging Rock Energy Facility | 298128 | Gas Turbine | 338X728 | Generator | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 5e145034-0ed5-49fd-bb20-222d18e7d970 | 2024-12-20 | 2024-10-04 | Major Inspection (MI) | Major Inspection (Rotor Out) | 131523 | TA & Craft Labor | 77 | YES | 10 | Oil Deflector Alignment, Oil Deflectors, Seal Rings, Fan Blades, Blue Check, Hydrogen Seal Assembly, End Shield, Wedges, Greasing, Retaining Rings | . Reproduction, use or disclosure to third parties without express authority is strictly forbidden. © GE 2019 QCP - Quality Control Plan 10366888 No. Checklist ID Checklist Name - Checklist Page Quality Check Remarks . Initial Date Initial Date Initial Date Outage ID: Craft Supervisor GE Field Engineer Customer (if applicable) Initial WD KH MB WD1 Full names and SSO of GE signatories Walter Darnell Kiah Hollenbeck Maverick Birch Walter Darnelll We reserve all rights in this document and the info
UNI035965 | Hanging Rock Energy Facility | 298128 | Gas Turbine | 338X728 | Generator | Field_Service_Report_ProjectID_A-1675158_EV-118580_C-10362918.pdf | 4bc695c5-70e6-4c01-8695-c570e68c01db | 2022-05-16 | 2022-04-06 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 40 | NO | 0
UNI035965 | Hanging Rock Energy Facility | 298128 | Gas Turbine | 338X728 | Generator | GAS_TURBINE_INSPECTION_REPORT_2GT2_Enhanced_Compressor_Package_2_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_HANGING_ROCK_LLC_Unit_2GT2_Gas_Turbine_298128_2010-05-01 | 090dbba1800b5fa2 | 2010-05-21 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X728;270T4 Accessory Gear S/N: Service Type: CS Cincinnati: CENT CS-ST. LOUIS FSR#:
UNI036242 | Liberty Electric Power Station | 297568 | Gas Turbine | 337X165 | Generator | Field_Service_Report_ProjectID_EV-121926_C-10355414.pdf | 38149a93-99fa-4893-949a-9399faa893ee_297568 | 2022-05-24 | 2022-04-08 | Upgrade - PMO Billing only |  |  | None | 46 | NO | 0 |  | ardware locations, IP addresses and port identifications. 4/10 A016 GAS TURBINE GENERATOR CONTROL AND PROTECTION PANEL DWG#: 302T7046-A016 Part #: NONE MLI A016 provides
UNI036242 | Liberty Electric Power Station | 297568 | Gas Turbine | 337X165 | Generator | Field_Service_Report_ProjectID_FSP-304208_C-10357845.pdf | 30c962a8-f517-4db5-8962-a8f5176db587 | 2021-06-17 | [6 empty] | NO | 0
UNI036335 | Casco Bay Power Station | 297198 | Gas Turbine | 337X063 | Generator | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | e7007d56-7b69-4258-ac69-a4b503e3b13c | 2025-10-14 | 2025-10-06 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 8 | YES | 7 | Core, Retaining Rings, Step Iron, Sub-slots, Main Lead, Greasing, High Voltage Bushings | Comments Turbine_End_Stator__nd-Step_Iron_General_010-FLAG.J Section Turbine End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Dusting Comments Turbine_End_Stator__nd-Step_Iron_General_011-FLAG.J Section Turbine End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Typical Comments Turbine_End_Stator__nd-Step_Iron_General_012.JPG Section Turbine End Sub-Section Stator Core Component Air Gap Locati
UNI036335 | Casco Bay Power Station | 297198 | Gas Turbine | 337X063 | Generator | Field_Service_Report_ProjectID_A-1909374_EV-174530_EVP-548993.pdf | 8ef44f6f-f9b0-4a38-a070-8916978d3b07 | 2025-03-19 | 2025-03-12 | Call-Out |  |  | TA Only | 7 | NO | 0 |  | End Date: 17 Mar 2025 ESN/SY: 297198 ¦ SY0070747 Generator Field Serial Number: 337X063 Oracle Project ID: A-1909374 ¦ EV-174530 ¦ EVP-548993 Report Issued: 19 Mar 202
UNI036335 | Casco Bay Power Station | 297198 | Gas Turbine | 337X063 | Generator | Field_Service_Report_ProjectID_A-1828072_EV-156897_C-10380822_EVP-536581.pdf | c37f12cb-5250-48f2-8973-39a9a9f2e832 | 2024-11-14 | 2024-10-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 38 | NO | 0
UNI036335 | Casco Bay Power Station | 297198 | Gas Turbine | 337X063 | Generator | Field_Service_Report_ProjectID_A-1819148_EV-155260_C-10377929.pdf | 3b27a8ba-9441-4089-a1e0-f433911d6c6e | 2023-12-11 | 2023-10-07 | Call-Out |  |  | TA & Craft Labor | 65 | NO | 0
UNI036335 | Casco Bay Power Station | 297198 | Gas Turbine | 337X063 | Generator | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 090dbba1800f25b1 | 2011-11-29 | [6 empty] | YES | 6 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test, Greasing | . END POSITION AIR HYD AIR HYD 1 16.0085 16.0045 16.0080 16.0055 2 16.0085 16.0045 16.0080 16.0055 3 16.0085 16.0060 16.0080 16.0060 4 16.0095 16.0075 16.0090 16.0060 5 16.0095 16.0075 16.0090 16.0060 6 16.0090 16.0060 16.0080 16.0050 AVERAGE 16.0089 16.0060 16.0083 16.0057 SHAFT DIA. 15.9995 15.9995 15.9990 15.9990 CLEARANCE 0.0094 0.0065 0.0093 0.0067 H2 SEAL SPRING MEASUREMENTS TURBINE END COLL. END UPPER LOWER UPPER LOWER LENGTH (±1/16 in.) 27.00 27.00 26.94 26.94 WIRE DIA. 0.12 0.12 0.12 0.
UNI036335 | Casco Bay Power Station | 297198 | Gas Turbine | 337X063 | Generator | GAS_TURBINE_INSPECTION_REPORT_CBM_Inspection_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-08-11 | 090dbba1800e713f | [7 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X063,270T4 Accessory Gear S/N: Service Type: Office Location: NE FS-MEDFORD (RW) Ora
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1815904_EV-154613_EVP-534945.pdf | f1b8425c-5c11-446e-a026-421587a08185 | 2025-04-22 | 2025-04-04 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 18 | NO | 0
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1847514_EV-161005_C-10379030_EVP-539583.pdf | d5079c31-050e-4997-85e8-408e3f19b6bc | 2024-05-08 | 2024-04-13 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 25 | NO | 0
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1796168_EV-150179_C-10378207_EVP-531951.pdf | c4af5eef-739a-4fb9-be94-0d381a42c5ac | 2023-12-19 | 2023-11-09 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 40 | NO | 0
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1698020_EV-114122_C-10366912.pdf | b70c6323-34ea-4d98-8c63-2334eaed989c | 2022-04-28 | 2022-04-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 21 | NO | 1 | Seal Rings | . - Rub on R3, R5-S9, R11-R13. - Corrosion on S3, S15, R9, R15-R17. - Discoloration on R4. - FOD on S6, R10, R12, R15, R17. - Rub on R15, R17. - Twisting on S15, R16. 2 Combustion Observed - Deposits on Can 1, Can 3-6, 8-14. - Wear on Can 2, 3 - Linear indication on Can 7 3 Hot Gas Path Observed -TBC spallation on S1N, S1B, S2B. - Discoloration on S1N. - S1N seal ring bolt 7 was missing but found and retrieved - Oxidation/erosion on S2N. - Deposits on S3N/S3B. Lower exhaust flex seals were found
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1676598_EV-114845_C-10363239.pdf | cfa311b9-81fd-4d05-a311-b981fd9d0574 | 2021-12-09 | 2021-11-08 | Call-Out |  |  | TA & Craft Labor | 31 | NO | 1 | Seal Rings | . 3. Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 1565 Safety Precautions to follow while working on Variable Guide Vanes TIL 2302 S1N Inner Support Rind Seal Housing Inspection TIL 1769 F Class Aft Stator Rocking Inspection TIL 1850-R2 F Class Shrouded Stator 17 Inspection TIL 2049-R2 F Class Inlet Guide Vane to Rub Ring Rubbing TIL 1582-R2 F and H Class Lift Oil Hose Inspection 4. Engineering Requests Engineering Requests (ER) GE Power Inspection & Life Extension Ser
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1636080_FSP-300585_C-10355244.pdf | 4d1ef0ac-b3c1-4007-9ef0-acb3c1b007f5 | 2021-06-14 | 2021-04-08 | Borescope Inspection (BI) | Large Call-Out | 123740 | TA & Craft Labor | 67 | NO | 1 | Seal Rings | . The technical data herein is the property Inspection Summary Inspection summary table: Percent Inspected defines the approximate inspection coverage for a section or stage. Since a portion of each component in a section or stage is not visible for inspection, 100 percent inspection coverage of every component is not feasible using remote visual inspection methods. Legend: NA – Parts were not inspected. NV – No visible indications. AF – Observed visible abnormal finding Compressor % Inspected T
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | GAS_TURBINE_INSPECTION_REPORT_SPRING_2010_ENHANCED_BORESCOPE_INSP._for_DOMINION_FAIRLESS_ENERGY_DOMINION_ENERGY_Unit_2A_GT_Gas_Turbine_298236_2010-05-03 | 090dbba1800b93de | 2010-06-29 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X743,270T625 Accessory Gear S/N: N/A Service Type: CONTRACT MAINT Office Location: N
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | Field_Service_Report_ProjectID_A-1815944_EV-154617_EVP-534949.pdf | 31c4c899-6e6a-47b0-8726-aac98f2667db |  | 2026-04-09 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI035717 | FAIRLESS ENERGY CENTER | 298236 | Gas Turbine | 338X743 | Generator | EBI_-_Unit_2B_Spring_April_2026_Provide_Mechanical_Support_for_EBI_FAIRLESS_ENERGY_CENTER_Gas_Turbine_298236_2026-04-09 | 5f2cd0f6-320f-4a06-8b34-eb74d62f0dd7 |  | 2026-04-09 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | Field_Service_Report_ProjectID_A-1828644_EV-156984_C-10378888_EVP-536651.pdf | 9e60e2e3-5e02-4d37-86c6-96f5bf683dce | 2024-04-07 | 2024-03-21 | Borescope Inspection (BI) |  |  | TA Only | 17 | NO | 0
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | Field_Service_Report_ProjectID_A-1722774_EV-132409_C-10369434.pdf | e7c88d01-78bd-484b-888d-0178bde84bca | 2022-04-25 | 2022-03-09 | Large Call-Out |  |  | TA & Craft Labor | 47 | NO | 0
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | Field_Service_Report_ProjectID_A-1682960_EV-114155_C-10364457.pdf | 679b0431-2256-48b5-9b04-31225668b532 | 2022-04-25 | 2022-03-09 | Large Call-Out |  |  | TA & Craft Labor | 47 | YES | 9 | End-winding, Fan Blades, Gooseneck, MAGIC Inspection, Pole Jumper, Retaining Rings, End Shield, Core, Wedges | The next six month periodic inspection can be skipped. Recommend to perform a full visual inspection of CE Field End turns and perform electrical testing of the field winding insulation at this time during the MAGIC inspection in the Spring of 2023. A retaining rings off inspection and repair of the damaged jumper is also recommended the next time the field is removed from the stator. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prio
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | Field_Service_Report_ProjectID_A-1640668_FSP-301915_C-10355925.pdf | 3e14a3ca-8cbb-4631-94a3-ca8cbb563184 | 2021-06-01 | 2021-04-12 | Call-Out |  |  | TA Only | 50 | NO | 0
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | Field_Service_Report_ProjectID_A-1629058_FSP-298683_C-10353375.pdf | aae16f68-0ee7-469f-a16f-680ee7b69f6d | 2021-05-19 | 2021-04-12 | Call-Out |  |  | TA Only | 37 | NO | 0 |  | n the protective functions in the EX2100e Exciter were confirmed to protect the generator by initiating a unit trip should one of the conditions be detected
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | GAS_TURBINE_INSPECTION_REPORT_ETS_Installation_and_DLN_Tuning_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT1_Gas_Turbine_297256_2011-12-17 | 090dbba1800f4d97 | 2011-12-28 | [6 empty] | NO | 0 |  | nic Mark Ve/TMR Frame Size: MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X709,270T4 Accessory Gear S/N: Service Type: Office Locati
UNI036591 | LAMAR POWER PARTNERS | 297256 | Gas Turbine | 337X708 | Generator | Field_Service_Report_ProjectID_A-1628248_FSP-298346_C-10353097.pdf | bc4ffb5d-7d8d-4993-8ffb-5d7d8df99367 |  | 2020-10-03 | Call-Out |  |  | TA & Craft Labor | 0 | YES | 7 | Core, Wedges, End-winding, Loose End-winding Blocking, Main Lead, Pole Jumper, Sub-slots | GE Power & Water Inspection & Life Extension Services 1. Foreword This report describes and documents the borescope examination of the unit that is described in the inspection details section listed on page 3; with respect to abnormal depositing, foreign object damage (FOD) and normal wear. A 4.5m X 6.1mm flexible videoscope was utilized for the examination. The interior of the unit was illuminated by employing fiberoptics to transmit light from an external light source. Color images were captur
UNI036153 | KENDALL POWER STATION | 297545 | Gas Turbine | 337X759 | Generator | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 6d33764e-9baf-46bf-a4a2-3a9e114b37fa | 2022-07-28 | [6 empty] | YES | 4 | Oil Deflector Alignment, Oil Deflectors, Seal Rings, Greasing | . The nominal design clearance is 41 to 46 mils. The minimum, average, and maximum as-found clearances were 45 mils, 55 mils, and 74 mils, respectively. Although the as-found vertical clearance was ~25 mils over the nominal design clearance, it was still within the 2X-design maintenance clearance normally allowed before component replacement. This oil seal was deemed suitable for continued service, but will probably need to be replaced during the next inspection of the #2 journal bearing. #2 For
UNI036153 | KENDALL POWER STATION | 297545 | Gas Turbine | 337X759 | Generator | Field_Service_Report_ProjectID_A-1586862_FSP-286527_C-10345104.pdf | 3886bfff-f3fd-4a5a-86bf-fff3fd1a5a5f | 2021-06-11 | 2021-05-08 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 34 | NO | 0
UNI036153 | KENDALL POWER STATION | 297545 | Gas Turbine | 337X759 | Generator | GAS_TURBINE_INSPECTION_REPORT_Hot_Gas_Path_Inspection_for_DYNEGY_KENDALL_ENERGY_LLC_DYNEGY_KENDALL_ENERGY_LLC_Unit_3_Gas_Turbine_297545_2011-10-10 | 090dbba1800ec0f6 | 2011-10-25 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X759 Accessory Gear S/N: Service Type: TECH DIRECTION Office Location: CENT CS-CINCI
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1838462_EV-158762_EVP-538034.pdf | 74d79634-5a94-4486-a06d-1d8c226bd444 | 2026-04-13 | 2026-04-01 | Call-Out |  |  | Craft Labor Only | 12 | NO | 0 |  | : 4/1/2026 I01-113366 Jason McDougall Luminant Forney Block 2 Forney, TX 298018 337X261 GT-21 96CD-1C 326T5390 Rev - Cool & Seal Air 0417 Turbine Enclosure Roof ROSEMO
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1941444_EV-181655_EVP-553239.pdf | 2772f842-77d3-477a-94e8-5c6114d7c21e | 2025-05-21 | 2025-05-13 | Call-Out | Minor Inspection | 140181 | TA Only | 8 | NO | 0
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1868702_EV-165590_EVP-543078.pdf | fd9a85d0-e820-49c7-b281-ab42d86b2c00 | 2025-04-29 | 2025-04-12 | Hot Gas Path Inspection (HGPI) | Minor Inspection | 140181 | TA & Craft Labor | 17 | NO | 0
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1828674_EV-156992_C-10378886_EVP-536654.pdf | 38d7e689-c8b4-4f05-a60c-540a2b16cee8 | 2024-04-09 | 2024-03-20 | Call-Out |  |  | TA & Craft Labor | 20 | NO | 0 |  | ft hoses are routed down the right side of the drain tunnel and the turbine and generator end connections appear intact. The upper and lower half flex seals were inspect
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1747384_EV-138969_C-10371457.pdf | 7ef061a9-6b73-4abf-b4c9-a881f4806571 | 2023-04-05 | 2023-03-01 | Call-Out |  |  | TA & Craft Labor | 35 | NO | 1 | Seal Rings | . Borescope ports in the turbine casing allowed viewing of the first stage nozzle, first stage buckets, second stage nozzle, second stage buckets, third stage nozzle, and third stage buckets. GE Power Inspection & Life Extension Services Technical Information Letters (TILs) Inspected TIL Number TIL Title 1108-R1 Cast Segmented Turbine Nozzle Acceptance Guidelines 1502-2R1 Active/open 7F AND 9F AFT END COMPRESSOR RUBS 1509-R4 Active/open F-Class Front End (R0, S0, and R1) Compressor Inspections 1
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1734332_EV-136170_C-10370464.pdf | 0b575363-35e2-4ed2-9654-01e53aaabbf8 | 2022-06-30 | 2022-05-19 | Call-Out |  |  | TA & Craft Labor | 42 | YES | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | . 337X263 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA 18.689 NA Shaft Grounding Brushes A NA NA NA Outer Oil Deflector B 0.009 0.007 0.009 0.009 0.022 0.009 Hydrogen Seal Casing
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1693592_EV-108196_C-10366341.pdf | b6b3c9d2-9167-4629-b3c9-d291671629dc | 2022-06-06 | 2022-05-19 | Call-Out |  |  | TA & Craft Labor | 18 | NO | 1 | Seal Rings | service is why they were reused.(inspection details attached below in attachments) All preexisting flow sleeves were installed at assembly. Recommendation Status: Should be planned for next available shut down Recommendation Type: Parts Recommendation Description: Recommendation is to replace all piston rings at the next opportunity. As Found & Reinstalled Flowsleeves (2) Heavy Wear on Piston Rings (4) Heavy Wear on Piston Rings (5) As Found & Reinstalled Flowsleeves (3) GEGEGE GE Confidential a
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1701050_EV-125248.pdf | 575a222f-a946-4f75-9a22-2fa9464f75ae | 2022-05-12 | 2022-04-30 | Call-Out |  |  | TA & Craft Labor | 12 | NO | 0 |  | Til #: 1108-R1 Date of Disposition: 4 May 2022 Recurring: No Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1707214_EV-126693.pdf | 22b2e047-4d42-4db8-b2e0-474d423db895 | 2022-03-09 | 2021-12-20 | Call-Out |  |  | TA Only | 79 | NO | 0 |  | Til #: 1108-R1 Date of Disposition: 9 Mar 2022 Recurring: No Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI035751 | FORNEY POWER PLANT | 298018 | Gas Turbine | 337X261 | Generator | Field_Service_Report_ProjectID_A-1606122_FSP-292749_C-10349255.pdf | 0cb23473-2d85-49f1-b234-732d8559f14f | 2021-03-25 | 2021-03-15 | Call-Out |  |  | TA & Craft Labor | 10 | NO | 0 |  | DS Til #: 1650 Date of Disposition: 25 Mar 2021 Recurring: No Name: GAS TURBINE GENERATOR EMERGENCY SEAL OIL PUMP MOTOR CONTROL CONFIGURATION Til #: 1646 Date of Disposi
UNI036592 | LAMAR POWER PARTNERS | 297255 | Gas Turbine | 337X709 | Generator | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 4b571da4-fd10-4d42-b810-c6a9c9ce9b21 | 2024-04-13 | 2024-03-21 | Borescope Inspection (BI) |  |  | TA Only | 23 | YES | 7 | Focused Generator Inspection, Greasing, Keybars, Step Iron, Wedge Tightness Test, Wedges, Core | . The plant decided to do an inspection of the generator due to a humming noise that has been present in the generator for a couple of weeks. The inspection consisted of a borescope on the CE and TE step iron looking for loose laminations. The borescope inspection was performed by the borescope technician Dillan Smith and Generator Specialist Franklin Wright. No laminations were found to be loose or damaged. Greasing was found on the step iron and end wedge locations. The unit had a field out in
UNI036592 | LAMAR POWER PARTNERS | 297255 | Gas Turbine | 337X709 | Generator | Field_Service_Report_ProjectID_A-1722784_EV-132410_C-10369435.pdf | cbb21c1f-d02b-4b32-b21c-1fd02bab3295 | 2022-05-03 | 2022-03-09 | Large Call-Out |  |  | TA & Craft Labor | 55 | NO | 2 | Core, Wedges | . Foreword This report describes and documents the borescope examination of the unit that is described in the inspection details section listed on page 3; with respect to abnormal depositing, foreign object damage (FOD) and normal wear. A 4.5m X 6.1mm flexible videoscope was utilized for the examination. The interior of the unit was illuminated by employing fiberoptics to transmit light from an external light source. Color images were captured with the GE Inspection Technologies/Everest Imaging
UNI036592 | LAMAR POWER PARTNERS | 297255 | Gas Turbine | 337X709 | Generator | Field_Service_Report_ProjectID_A-1664162_FSP-307505_C-10360445.pdf | ccc6f9e0-f2d7-404d-86f9-e0f2d7b04d5e | 2021-11-29 | 2021-11-06 | Call-Out |  |  | TA Only | 23 | NO | 0 |  | ge Pressure • Compressor Discharge Temperature • Compressor Inlet Temperature • Generator Power • Gas Fuel Pressure • Gas fuel system differential pressures • Gas Fuel F
UNI036592 | LAMAR POWER PARTNERS | 297255 | Gas Turbine | 337X709 | Generator | Field_Service_Report_ProjectID_A-1650990_FSP-304338_C-10357874.pdf | 433ae336-e79c-4200-bae3-36e79c02007d | 2021-04-19 | 2021-04-14 | Call-Out |  |  | TA Only | 5 | NO | 0 |  | Name Category Role PHILIP J. MAUS GE TFA - GENERATOR SPECIALIST
UNI036592 | LAMAR POWER PARTNERS | 297255 | Gas Turbine | 337X709 | Generator | Field_Service_Report_ProjectID_A-1644020_FSP-302776_C-10356630.pdf | 4a733343-a03e-494f-b333-43a03e194fac | 2021-01-06 | 2020-12-12 | Call-Out |  |  | TA Only | 25 | NO | 0
UNI036592 | LAMAR POWER PARTNERS | 297255 | Gas Turbine | 337X709 | Generator | Field_Service_Report_ProjectID_A-1559310_FSP-278113_C-10339012.pdf | 0be87536-276d-4f50-a875-36276dff50c6 | [7 empty] | NO | 0
UNI036661 | Pleasants County Peaking Power | 297784 | Gas Turbine | 337X185 | Generator | Field_Service_Report_ProjectID_A-1913514_EV-175392_EVP-549581.pdf | c0c5a8df-6e70-417a-8b2b-3065b9452c64 | 2025-02-08 | 2024-12-04 | Call-Out |  |  | TA & Craft Labor | 66 | NO | 0
UNI036661 | Pleasants County Peaking Power | 297784 | Gas Turbine | 337X185 | Generator | Field_Service_Report_ProjectID_A-1676360_EV-123737_C-10363200.pdf | 9b0c9613-a149-4022-8c96-13a149102216 | 2022-05-01 | 2022-03-19 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 43 | NO | 0
UNI036661 | Pleasants County Peaking Power | 297784 | Gas Turbine | 337X185 | Generator | Field_Service_Report_ProjectID_A-1586270_FSP-286391_C-10345023.pdf | 227a465b-9135-4e3d-ba46-5b91350e3d57 | 2021-06-23 | [6 empty] | NO | 0
UNI036661 | Pleasants County Peaking Power | 297784 | Gas Turbine | 337X185 | Generator | Field_Service_Report_ProjectID_EV-159640_EVP-538627.pdf | 6bcf86aa-ed11-4093-b790-03683afe431e |  | 2025-03-15 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 2 | Oil Deflector Alignment, Oil Deflectors | Mechanical Scope: 9/15/2025: • Mobilized to site. • LOTO on gas turbine at 1300 for EBI. Labor provided by customer. No APM involvement. • LOTO on generator at 1715. • Took opening clearances on CE outer oil seal. • Remove CE outer oil seal for inspection. • Found frayed wires on TC harness. • Customer will test the bearing and the harness. 9/16/2025: • Customer came in first thing this morning and tested the collector end bearing. • It was determined that the installed TC in the bearing was goo
UNI035752 | FORNEY POWER PLANT | 298019 | Gas Turbine | 337X262 | Generator | Field_Service_Report_ProjectID_A-1954970_EV-184320_EVP-554949.pdf | b0db7d3c-c20a-4024-97f6-be4e1cbf6d2f | 2025-07-28 | 2025-07-19 | Call-Out |  |  | TA & Craft Labor | 9 | NO | 0
UNI035752 | FORNEY POWER PLANT | 298019 | Gas Turbine | 337X262 | Generator | Field_Service_Report_ProjectID_A-1944180_EV-182147_EVP-553590.pdf | 32d0a2ea-656a-45bf-a753-76654114ed58 | 2025-06-09 | 2025-05-22 | Call-Out | Minor Inspection | 140183 | TA & Craft Labor | 18 | NO | 0 |  | End Date: 23 May 2025 ESN/SY: 298019 ¦ SY0070239 Generator Field Serial Number: 337X262 Oracle Project ID: A-1944180 ¦ EV-182147 ¦ EVP-553590 Report Issued: 09 Jun 202
UNI035752 | FORNEY POWER PLANT | 298019 | Gas Turbine | 337X262 | Generator | Field_Service_Report_ProjectID_A-1828882_EV-156993_C-10377659_EVP-536683.pdf | 21e9fafc-9e04-458e-b757-0e55421c8da7 | 2024-04-07 | 2024-03-12 | Borescope Inspection (BI) |  |  | TA Only | 26 | NO | 0 |  | are routed down the right and left side of the drain tunnel and the turbine and generator end connections appear intact. The upper and lower half flex seals were inspect
UNI035752 | FORNEY POWER PLANT | 298019 | Gas Turbine | 337X262 | Generator | GAS_TURBINE_INSPECTION_REPORT_UNIT_22_MAJOR_INSPECTION_for_FPLE_FORNEY_LP_FORNEY_POWER_PLANT_Unit_2-2_Gas_Turbine_298019_2011-03-08 | 090dbba1800ea31a | 2011-09-30 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X262 Accessory Gear S/N: Service Type: Office Location: SW CS-DALLAS 02 (DC) Oracle
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1815874_EV-154609_EVP-534941.pdf | 232d5d50-e459-4a5c-a5a6-6bbb641e1cef | 2025-04-22 | [6 empty] | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1846706_EV-153843_C-10379813_EVP-539483.pdf | ea32b0e0-761b-4ade-81eb-90723b287d5e | 2024-05-08 | 2024-04-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 31 | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1698000_EV-108234_C-10366910.pdf | dcf9b630-131e-44ef-b9b6-30131ea4efaf | 2022-04-27 | 2022-04-01 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 26 | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1676578_FSP-310969_C-10363235.pdf | 55f84ee1-9065-407c-b84e-e19065907c12 | 2021-12-09 | 2021-10-30 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 40 | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1636060_FSP-300580_C-10354855.pdf | 742b7d63-6f2e-47a0-ab7d-636f2ed7a0d0 | 2021-06-09 | 2021-04-01 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 69 | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | GAS_TURBINE_INSPECTION_REPORT_Dominion_Fairless_Spring_2011_HGP_1A_Outage_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1A_GT_Gas_Turbine_298178_2011-03-26 | 090dbba1800dbc53 | 2011-04-18 | [6 empty] | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | GAS_TURBINE_INSPECTION_REPORT_Fairless_Energy_Fall_2011_Enhanced_Borescope_Inspection_for_DOMINION_ENERGY_Fairless_Unit_298177178235236_Gas_Turbine_298178_2011-10-24 | 090dbba1800f141b | [7 empty] | NO | 1 | Collector Rings | . Continue to adhere to valve maintenance intervals as described in the service manual and applicable unit fuel system GEK's. GAS FUEL SYSTEM Excitation System System; The excitation systems on S1 and S2 were inspected. Customer was experiencing conduction alarms and an excitation engineer was brought on site to troubleshoot accordingly. Please see attached report for details of the inspections and recommendations. EXCITATION SYSTEM S1 and S2 EX2100 De-Excitation Conduction Alarm Troubleshooting
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1815914_EV-154614_EVP-534946.pdf | be79999e-dedc-491d-ae2a-953ee45b61f7 |  | 2026-04-04 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI035720 | FAIRLESS ENERGY CENTER | 298178 | Gas Turbine | 338X737 | Generator | Field_Service_Report_ProjectID_A-1749044_EV-139338.pdf | 99c9c155-40f3-481b-828a-7a579e62a344 | [7 empty] | NO | 1 | Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted.
UNI036596 | LAMAR POWER PARTNERS | 270T435 | Steam Turbine | 290T435 | Generator | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 7a3c360e-adb0-4682-ae02-f732770e39ac | 2026-03-30 | 2026-03-20 | Call-Out |  |  | TA & Craft Labor | 10 | YES | 8 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, End Shield, Seal Rings, Generator Pressure Test | . The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J Inner Oil Deflector K 0.011 0.011 0.012 0.020 0.010 Middle Oil Deflector L 0.018 0.013 0.013 0.018 0.018 Hydrogen Seal Casing M 0
UNI036596 | LAMAR POWER PARTNERS | 270T435 | Steam Turbine | 290T435 | Generator | Field_Service_Report_ProjectID_A-1974278_EV-187586_EVP-557256.pdf | 5436fbfc-b665-45e8-a398-ffab315f314b | 2025-11-18 | 2025-11-14 | Call-Out |  |  | TA & Craft Labor | 4 | NO | 0
UNI036596 | LAMAR POWER PARTNERS | 270T435 | Steam Turbine | 290T435 | Generator | Field_Service_Report_ProjectID_A-1881852_EV-168186_EVP-545083.pdf | de3dcf7f-890b-43be-9726-248c6f64f1a6 | 2025-04-08 | 2025-02-27 | Large Call-Out |  |  | TA & Craft Labor | 40 | YES | 4 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test, Collector Rings | . Removal of the L-1 TE, L-2 GE and TE buckets was performed at which time MPI Mag Particle Inspections was performed in the areas of the indications on the bucket wheels. LES team submitted data as needed be the engineering team and excavation of the indications was initiated. The OSS team utilized small burr bits to perform the removal of material at a minimal rate with constant MPI’s performed during the process to monitor excavation of indications. This evolution was performed on L-1 TE buck
UNI036596 | LAMAR POWER PARTNERS | 270T435 | Steam Turbine | 290T435 | Generator | g_GE_Energy_Services_TIL_1480-2_Implementation_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_ST2_Steam_Turbine_270T435_2005-04-04 | 090dbba18007565a | 2005-05-24 | [6 empty] | NO | 0
UNI036596 | LAMAR POWER PARTNERS | 270T435 | Steam Turbine | 290T435 | Generator | Field_Service_Report_ProjectID_A-1641964_FSP-302306_C-10356227.pdf | a55958fc-8516-4d6e-9958-fc8516cd6eef | [7 empty] | NO | 0
UNI036596 | LAMAR POWER PARTNERS | 270T435 | Steam Turbine | 290T435 | Generator | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 9a203661-fd58-49ae-a036-61fd5819aeb4 |  | 2020-10-22 | Minor Inspection |  |  | TA & Craft Labor | 0 | YES | 29 | AC Impedance, Collector Rings, Core, DC Leakage, DLRO, End Shield, Focused Generator Inspection, High Voltage Bushings, MAGIC Inspection, Polarization Index, Stator Winding, Wedges, Winding Resistance, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Generator Pressure Test, End-winding, Greasing, Sub-slots, Retaining Rings, Step Iron, Keybars, Main Lead, Pole Jumper, Wedge Looseness, Wedge Tightness Test | For Lamar Power Partners Generator Serial #: 290T435 Generator Test and Inspect MAGIC Stator Inspection: William Howard Generator Specialist: Dave Cathey, Steve Proctor Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • MAGIC robotic inspection • Stator slot RTD resistance measurement and megger 500vDC • Field AC Impedance, resistance, and 500 vDC megger • Stator resistance, megger/PI 5KvDC • Stator DC Leakage test at 36KvDC Jo
UNI026365 | INDEPENDENCE POWER STATION | 296300 | Gas Turbine | 337X009 | Generator | Field_Service_Report_ProjectID_A-1791754_EV-149144_EVP-531196.pdf | 36a50b8f-1d3b-40ae-8645-d5000e03d436 | 2025-05-01 | 2025-04-05 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 26 | NO | 0
UNI026365 | INDEPENDENCE POWER STATION | 296300 | Gas Turbine | 337X009 | Generator | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | b0bf4cd9-ded5-4bf6-9bd2-b3dda3f78876 | 2024-05-31 | 2024-04-06 | Major Inspection (MI) |  |  | TA & Craft Labor | 55 | YES | 28 | AC Impedance, Belly Bands, Belly band inspection, Core, DC Leakage, End-winding, Field Body, MAGIC Inspection, Polarization Index, Wedges, Focused Generator Inspection, High Voltage Bushings, Lamination Damage, Retaining Rings, Stator Winding, Wedge Tightness Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, DC Hipot, Fan Blades, Generator Pressure Test, Blocked Vent Ducts, Greasing, DLRO, Winding Resistance, Winding resistance DLRO, Wedge Looseness | . • Minor end-winding support system repairs were performed. • No loose stator wedges were detected. (Via MAGIC Insp.). • Electrical testing was satisfactory. • This Generator was found to have good amounts of oil in its belly area (in the cooler area). Major Inspection (Robotic) - 337X009 DYNEGY INC. 1.1 Generator Executive Summary FIELD: • Visual / MAGIC inspection was satisfactory. • Baseline electrical test results were satisfactory. INSTRUMENTATION: • RTD’s electrical tests were satisfactor
UNI026365 | INDEPENDENCE POWER STATION | 296300 | Gas Turbine | 337X009 | Generator | Field_Service_Report_ProjectID_A-1844260_EV-160324_C-10378089_EVP-539084.pdf | 486cd337-0c8f-412a-a2db-8a092a7c72ad | 2023-12-20 | 2023-12-04 | Call-Out |  |  | TA & Craft Labor | 16 | NO | 0 |  | SPECTION INDICATIONS ROTATING BLADE LOCATION KEY RESULTS OF: NOTED: VIEW FACING GENERATOR END COUPLING ROTOR SPINDLE Notch Bucket PACKING GROOVES CW BUCKET COUNT JOURNAL
UNI026365 | INDEPENDENCE POWER STATION | 296300 | Gas Turbine | 337X009 | Generator | Field_Service_Report_ProjectID_A-1714994_EV-130859_C-10371286.pdf | 584cbb14-0449-4d29-8f1f-9726fa3516b5 | 2023-06-01 | 2023-05-25 | Call-Out |  |  | TA & Craft Labor | 7 | NO | 0
UNI026365 | INDEPENDENCE POWER STATION | 296300 | Gas Turbine | 337X009 | Generator | Field_Service_Report_ProjectID_A-1570052_FSP-281810_C-10341869.pdf | 2b442629-19ac-4c01-8426-2919acfc0106 |  | 2020-10-10 | Call-Out |  |  | TA & Craft Labor | 2 | NO | 0
UNI036481 | Moss Landing | 297603 | Gas Turbine | 337X751 | Generator | Field_Service_Report_ProjectID_A-1841658_EV-156872_EVP-538623.pdf | b868e2ff-35c0-4e5b-b01f-3d31a8265e6b | 2025-05-20 | 2025-04-04 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 46 | NO | 0
UNI036481 | Moss Landing | 297603 | Gas Turbine | 337X751 | Generator | Field_Service_Report_ProjectID_A-1829462_EV-156861_C-10377198_EVP-536745.pdf | 2bf74922-5473-42f8-9419-0eb7cb07950d | 2024-06-28 | [6 empty] | NO | 0
UNI036481 | Moss Landing | 297603 | Gas Turbine | 337X751 | Generator | Field_Service_Report_ProjectID_A-1676490_EV-111980_C-10363261.pdf | 748382f1-a05f-4066-bc9f-877231408733 | 2022-06-30 | 2022-05-14 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 47 | NO | 0 |  | ines appear to be routed correctly; however, light chaffing was observed at the generator end and chaffing/fraying was observed at the turbine end. The lower bellmouth t
UNI036481 | Moss Landing | 297603 | Gas Turbine | 337X751 | Generator | Field_Service_Report_ProjectID_A-1375356_FSP-293536_C-10349934.pdf | ecb60ad9-f4dd-47d1-b60a-d9f4dd07d12f | 2021-05-25 | 2021-03-13 | Hot Gas Path Inspection (HGPI) |  |  | TA & Craft Labor | 73 | YES | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | . A review of post inspection results revealed significant cracking on the Stage 13, 15, 16, and 17 wheel slots. (A replacement Stage 14 wheel, with round bottom slots, had been previously installed on this rotor, and therefore did not require Ultrasonic Testing). The results have been submitted to GE engineering and resolution for these findings is still pending. See report attachment for further details. The removed rotor was packaged and shipped to the Vistra Energy storage facility. The inst
UNI036481 | Moss Landing | 297603 | Gas Turbine | 337X751 | Generator | Field_Service_Report_ProjectID_A-1598456_FSP-290138_C-10347529.pdf | 4312536f-9081-4b77-9253-6f90816b7702 |  | 2020-03-30 | Call-Out |  |  | TA Only | 1 | NO | 0
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1838482_EV-158764_EVP-538036.pdf | ea7f1218-8300-4733-a618-93f0906df72a | 2026-04-06 | 2026-03-20 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 17 | YES | 4 | Collector Rings, Fan Blades, Oil Deflector Alignment, Oil Deflectors | On 03/21/2026 GE Vernova (GEV) Craft personnel arrived onsite. Personnel consisted of one GEV Supervisor and 10 GEV Millwrights. The job trailer and site setup commenced and GEV tooling was received and staged near the units. On 03/24/2026 the GEV TFA arrived onsite and set up work trailer area. Scope of work was an annual borescope inspection on gas turbines CT-21 and CT-12 as well a T4 bearing swap on CT-21 and a T3 bearing swap on CT-22. The GEV Borescope Specialist arrived onsite on 03/25/20
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1828604_EV-156986_EVP-536645.pdf | 0df36928-19d8-4744-bf21-1ac30346b2d4 | 2025-04-29 | 2025-03-10 | Call-Out |  |  | TA Only | 50 | NO | 0
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 1cb39604-e7ba-4488-88f6-8185348ec7d5 | 2024-06-25 | 2024-04-13 | Major Inspection (MI) | Major Inspection (Rotor Out) | 140174 | TA & Craft Labor | 73 | YES | 19 | AC Impedance, DC Leakage, Focused Generator Inspection, Generator Pressure Test, Hydrogen Seal Assembly, Polarization Index, Wedge Tightness Test, Wedges, End Shield, Fan Blades, Oil Deflector Alignment, Oil Deflectors, Collector Rings, Core, Greasing, DC Hipot, DLRO, Stator Winding, Winding Resistance | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 3.1.3 Work Scope Completed __________ 124 3.1.4 Task identified for next Outage __________ 141 3.2 Mark Controller Status __________ 141 3.2.1 General Hardware __________ 141 3.3 Regulator Calibration __________ 141 3.3.1 GCV Calibration __________ 141 3.3.2 IGV Calibration __________ 147 3.3.
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1747354_EV-138947_C-10371455.pdf | 176fce55-82c2-4d02-ae7b-883c4e2c9b54 | 2023-10-05 | [6 empty] | NO | 0
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1682980_EV-114307_C-10364458.pdf | 0bf384e4-2695-491e-b384-e42695c91e3f | 2022-05-02 | 2022-03-29 | Call-Out |  |  | TA Only | 34 | NO | 0
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1676044_FSP-310861_C-10363189.pdf | ff7e3f89-8211-45bb-be3f-89821145bbd6 | 2021-07-08 | 2021-06-21 | Call-Out |  |  | TA Only | 17 | NO | 0
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 090dbba1800f7e67 | 2012-01-26 | [6 empty] | YES | 7 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Blue Check, Fan Blades | GAS TURBINE INSPECTION REPORT Major Inspection for LAMAR POWER PARTNERS, Unit GT3 Equipment Serial #: 297258 Job Start Date: October 28, 2011 Report Issued: January 26, 2012 Oracle Project Id: 10071621 Report Printed: January 31, 2012 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: MICHAEL RICHARDS Field Engineer Approved By: JAMES HEAD Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 PARTS USED & RECOMMENDED 6 COMPRESS
UNI036594 | LAMAR POWER PARTNERS | 297258 | Gas Turbine | 337X710 | Generator | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | d4c26002-ed9d-4043-8260-02ed9d504301 | [7 empty] | YES | 30 | AC Impedance, Belly Bands, Core, DC Hipot, DC Leakage, DLRO, End Shield, Focused Generator Inspection, Greasing, MAGIC Inspection, Polarization Index, Stator Winding, Wedges, Winding Resistance, Collector Rings, End-winding, High Voltage Bushings, Keybars, Retaining Rings, Main Lead, Pole Jumper, Step Iron, Sub-slots, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Wedge Tightness Test, Wedge Looseness | For Lamar Power Partners Generator Serial #: 337X711 Generator U21 Test And Inspect Report 11_2_20 REV1 Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • Core compression flange nut torque check • Removal of existing shim packs and re-torqueing of belly bands • MAGIC robotic inspection • Stator slot RTD measurement and megger • Field AC Impedance, resistance, and 500 vDC megger • Stator megger/PI 5KvDC prior to belly band tigh
UNI035728 | Fayette Energy Facility | 298159 | Gas Turbine | 338X731 | Generator | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 509ae080-f53f-43a2-95b5-17b642a0b279 | 2025-05-09 | 2025-03-01 | Major Inspection (MI) | Major Inspection (Rotor Out) | 131451 | TA & Craft Labor | 69 | YES | 28 | AC Impedance, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Greasing, Hydrogen Seal Assembly, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance, High Voltage Bushings, Loose End-winding Blocking, Sub-slots, Gooseneck, Main Lead, Step Iron, Pole Jumper, Fan Blades, Oil Deflector Alignment, Oil Deflectors, Wedge Looseness | This report is related with major outage of GT2( 338X732) generator, at Fayette station in PA between March 5-16 2025. The work scope included stator and field visual inspection, electrical testing and MAGIC I inspection including wedge tapping of stator wedges and ElCID integrity of stator iron. The other scope is additional block modification of connection ring and three winders mobilized for this modification. Stator end winding has repaired in previous outage. Some of connection ring ties ha
UNI035728 | Fayette Energy Facility | 298159 | Gas Turbine | 338X731 | Generator | Field_Service_Report_ProjectID_A-1717012_EV-131399_C-10375374_EVP-521411.pdf | 37ccac85-6b9d-4f26-875b-8122dd911a3b | 2023-11-06 | 2023-10-21 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 16 | NO | 0 |  | rly deep enough. We managed to re-insert the T/C to the proper depth. Fixed GT2 Generator Cold Gas Temperature #24. Helped troubleshoot two flame GEGEGE GE Confidential
UNI035728 | Fayette Energy Facility | 298159 | Gas Turbine | 338X731 | Generator | Field_Service_Report_ProjectID_A-1586310_FSP-286401_C-10345029.pdf | 1660200e-dcfd-4530-a020-0edcfdb530ad | 2021-12-07 | 2021-10-23 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 45 | NO | 0 |  | r the wheel speed pickup (GT2), a replacement of the seal oil regulator on both generators, and welding of cracks in the exhaust diffusers. Extra work for the ST involve
UNI035728 | Fayette Energy Facility | 298159 | Gas Turbine | 338X731 | Generator | GAS_TURBINE_INSPECTION_REPORT_Fayette_Energy_March_2012_outage_for_DUKE_ENERGY_NORTH_AMERICA_Fayette_Energy_Facility_Unit_GT2_Gas_Turbine_298159_2012-03-10 | 090dbba1800fd6d7 | 2012-03-21 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X731,338X732;270T 552 Accessory Gear S/N: N/A Service Type: CONTRACT MAINT Office Lo
UNI035728 | Fayette Energy Facility | 298159 | Gas Turbine | 338X731 | Generator | GAS_TURBINE_INSPECTION_REPORT_Fuel_nozzle_changeout_for_DUKE_ENERGY_NORTH_AMERICA_Fayette_Energy_Facility_Unit_GT2_Gas_Turbine_298159_2011-10-03 | 090dbba1800eb128 | 2011-10-19 | [6 empty] | NO | 0 |  | nic Mark VI/TMR Frame Size: MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X732;270T5 Accessory Gear S/N: Service Type: CONTRACT MAIN
UNI035961 | Hanging Rock Energy Facility | 298112 | Gas Turbine | 338X725 | Generator | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 6f86cc0e-be46-4e2d-a81b-53309dcc7f13 | 2024-06-13 | 2024-04-06 | Major Inspection (MI) | Major Inspection (Rotor Out) | 130904 | TA & Craft Labor | 68 | YES | 10 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, End Shield, Seal Rings, End-winding, Greasing, Wedges | . The H2 seal casing is in overall good condition Cleaned Joints Dowels Insp per GN-2151 Top T. Left B. Left T. Right B. Right "A" Gap "A" Gap dimensions Bottom C A B B C D E AIR SIDE HYDROGEN SIDE OIL DEFLECTOR A ST00065 D316512 Sheet: (a) Rev 2.2 - 08/28/2018 Generator Field Clearance Equip Code: Turbine End As Found Date(m/d/y) 4.10.2024 Turbine Serial No. 298112 Prepared by Generator Serial No. 338X725 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbe
UNI035961 | Hanging Rock Energy Facility | 298112 | Gas Turbine | 338X725 | Generator | Field_Service_Report_ProjectID_A-1674982_EV-108848_C-10362909.pdf | f44e1836-8651-45f2-8e18-36865125f2cb | 2022-05-13 | 2022-04-02 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 41 | NO | 0 |  | was completed along with assisting LOOK Technologies with the inspecting of the generator by removing the generator manways.
UNI035961 | Hanging Rock Energy Facility | 298112 | Gas Turbine | 338X725 | Generator | GAS_TURBINE_INSPECTION_REPORT_1GT1_Hot_Gas_Path_Inspection_Spring_2010_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_HANGING_ROCK_LLC_Unit_1GT1_Gas_Turbine_298112_2010-05-01 | 090dbba1800b8562 | 2010-06-23 | [6 empty] | NO | 1 | MAGIC Inspection | GAS TURBINE INSPECTION REPORT 1GT1 Hot Gas Path Inspection Spring 2010 for DUKE ENERGY HANGING ROCK LLC ,Unit 1GT1 Equipment Serial #:298112 Job Start Date :May 01,2010 Report Issued :June 23,2010 FSR #:97JD0730 Report Printed :June 23,2010 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: BRIAN TOOHEY Field Engineer Approved By: MARK RUEFER Mark A Ruefer PAGE JOB SUMMARY 1 PARTS USED & RECOMMENDED 4 ALIGNMENT & CLEARANCES OVERV
UNI000886 | INDEPENDENCE POWER STATION | 270T259 | Steam Turbine | 290T259 | Generator | Field_Service_Report_ProjectID_A-1874366_EV-166829_EVP-543930.pdf | 7cdef855-72ca-48c0-86fa-67e6089d89fa | 2024-06-05 | 2024-04-14 | Call-Out |  |  | TA & Craft Labor | 52 | NO | 2 | Oil Deflector Alignment, Oil Deflectors | Dynegy Independence Station, Unit ST-6, 270T259, was forced offline for high T4 bearing metal temperatures. On 4/16/2024, GE signed on LOTO to investigate and repair the unit. As found condition: T4 bearing cover was removed, rotor positions were measured, the rotor was found to be sitting 0.058” lower than the as-built data from 2023 major inspection. T4 bearing was rolled out and found to be wiped. T4 oil deflector and turning gear oil deflector were also found to be heavily damaged on the bot
UNI000886 | INDEPENDENCE POWER STATION | 270T259 | Steam Turbine | 290T259 | Generator | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 090dbba180078b20 | 2006-05-31 | [6 empty] | YES | 8 | Blue Check, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Hydrogen Seal Assembly, End Shield, Collector Rings, Fan Blades | (None this outage) BEARINGS Generator Journal Bearing Babbitt; 5,6 The T-5 and T-6 journal bearings were disassembled and inspected. A dye penetrant test was conducted on the babbitted tilt pads and crack-like indications were noted on the lower pads of both T-5 and T-6 bearings. The pads were removed from both bearing housings and prepped for shipping to an offsite repair facility. Spare bearing assemblies for both T-5 and T-6 were available from customer stock and were installed at assembly. R
UNI036595 | LAMAR POWER PARTNERS | 297257 | Gas Turbine | 337X711 | Generator | Field_Service_Report_ProjectID_A-1828614_EV-156987_EVP-536646.pdf | ae17226a-de2d-4c66-a0be-97def0423729 | 2025-04-23 | 2025-02-27 | Borescope Inspection (BI) | Call-Out | 175632 | TA Only | 55 | NO | 0 |  | Start Date: 27 Feb 2025 Outage End Date: 20 Mar 2025 ESN/SY: 297257 ¦ SY0070971 Generator Field Serial Number: 337X710 Oracle Project ID: A-1828614 ¦ EV-156987 ¦ EVP-536
UNI036595 | LAMAR POWER PARTNERS | 297257 | Gas Turbine | 337X711 | Generator | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 3565f050-8660-49d4-a4c6-9bffde64b3b5 | 2024-06-26 | 2024-04-13 | Borescope Inspection (BI) | Major Inspection (Rotor Out) | 140176 | TA Only | 74 | YES | 18 | AC Impedance, DC Leakage, Fan Blades, Focused Generator Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Wedge Tightness Test, Wedges, End Shield, Hydrogen Seal Assembly, Stator Winding, Core, Field Body, Greasing, Retaining Rings, DC Hipot, DLRO | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.7.2 Exhaust Diffuser __________ 219 2.7.3 T2 Journal Bearing __________ 220 2.8 Unit Rotor and Casing Alignment __________ 224 2.8.1 Turbine to Generator Alignment __________ 224 2.8.2 Unit Rotor __________ 226 2.8.3 Internal Casing Alignment __________ 230 2.8.4 Load Coupling and Coupling B
UNI036595 | LAMAR POWER PARTNERS | 297257 | Gas Turbine | 337X711 | Generator | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 090dbba1800f6a42 | 2012-01-04 | [6 empty] | YES | 9 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Blue Check, Seal Rings, Retaining Rings | . Section Location Description: Action: 60 Thrust Bearing Preventive Maintenance Replaced 61 #2 Bearing Cap Disassembled And Inspected Good Condition - No Visual Defects 62 #2 Journal Bearing #2 Journal Bearing Worn Repaired 63 #2 Bearing Seals Preventive Maintenance Cleaned 64 #2 bearing lift oil hoses TIL 1582-R2 Preventive Maintenance Replaced 65 TIL 1781 TIL TIL Satisfied 98 #3 & #4 Elliptical bearings #3 & #4 Elliptical bearings Worn Repaired 77 Load Coupling Guard Load Coupling Guard Disas
UNI036595 | LAMAR POWER PARTNERS | 297257 | Gas Turbine | 337X711 | Generator | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 2b481fe9-e539-415a-881f-e9e539215a89 | [7 empty] | YES | 27 | AC Impedance, Collector Rings, DC Leakage, DLRO, Greasing, High Voltage Bushings, Keybars, MAGIC Inspection, Polarization Index, Stator Winding, Wedges, Winding Resistance, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Main Lead, Pole Jumper, Step Iron, Sub-slots, End Shield, Wedge Looseness, Wedge Tightness Test, Inner Gas Shield, Focused Generator Inspection, Retaining Rings | For Lamar Power Partners Generator Serial #: 337X710 Generator Test and Inspect MAGIC Stator Inspection: William Howard Generator Specialist: Dave Cathey, Steve Proctor Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • MAGIC robotic inspection • Stator slot RTD resistance measurement and megger 500vDC • Field AC Impedance, resistance, and 500 vDC megger • Stator resistance, megger/PI 5KvDC • Stator DC Leakage test at 36KvDC Jo
UNI036593 | LAMAR POWER PARTNERS | 270T434 | Steam Turbine | 290T434 | Generator | STEAM_TURBINE_INSPECTION_REPORT_ST-10_MAJOR-Valve-_Calibrations_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_ST1_Steam_Turbine_270T434_2012-04-25 | 090dbba18011c980 | 2012-07-09 | [6 empty] | NO | 0 |  | ating: 202 Turbine Type: Service Year: 2000 GE Maint Dept: LST Event ID: 111111 Generator Code: Control System: Speedtronic Mark V/TMR LSB Length: 2X30 Generator Cooling
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1777770_EV-145778_EVP-529273.pdf | c0d10411-47dc-4f7c-81f5-8dcbd0414f57 | 2025-06-30 | [6 empty] | NO | 1 | Stator Winding | . 8. Personnel should wear the appropriate PPE and clothing. OSHA 29CFR part 1910.146(b) provides additional guidance on compartment entry safety. E. Confined Space Area Pursuant to OSHA 29CFR 1910.146(d)(3), the means, procedures, and practices necessary for safe permit space entry operations for confined spaces must be developed and implemented. If acceptable entry conditions cannot be maintained to protect the entrant from hazards during entry, then entry cannot be authorized. A gas turbine a
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1846746_EV-156871_EVP-539491.pdf | 8209471e-9f7b-4839-bff0-11fcc4abcc9f | 2025-05-20 | 2025-04-04 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 46 | NO | 0
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1835186_EV-156864_EVP-537593.pdf | 821f24b5-db6b-41e3-be0d-1f53e683721a | 2024-05-23 | 2024-04-20 | Call-Out | Major Inspection (Robotic) | 130852 | TA Only | 33 | NO | 0
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1716032_EV-131213.pdf | 655c2371-7ec0-41c8-b2f8-3ce44410abe5 | 2023-06-12 | 2023-05-13 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 30 | NO | 0
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1783916_EV-147090.pdf | 82ea68ff-b66b-482e-afc8-3a07f4ccac22 | 2023-01-27 | 2023-01-05 | Call-Out |  |  | TA Only | 22 | NO | 0
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1676480_FSP-310947_C-10363260.pdf | d26fdbf8-7d93-4c6e-be42-37f734cff4cc | 2022-06-30 | [6 empty] | NO | 0
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | Field_Service_Report_ProjectID_A-1672270_FSP-309888_C-10362236.pdf | 2419239b-09e8-4dbf-9923-9b09e8cdbfba | 2021-06-14 | 2021-05-19 | Call-Out |  |  | TA & Craft Labor | 26 | NO | 0
UNI036480 | Moss Landing | 297602 | Gas Turbine | 337X750 | Generator | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 090dbba1800fa73e | [7 empty] | YES | 5 | Oil Deflector Alignment, Oil Deflectors, Seal Rings, Wedges, Keybars | . New journal bearings come with new seal rings as part of the assembly. New oil seal rings and hardware installed. C C B B A A Bearing Oil Deflector Clearances Date 12/7/2011 Turbine Serial No. Prepared by C. Helget Data Type Final INSPECTIONS & CHECKS CODE Deflector Inspected X X Work Carried Out Journals Inspected X N Not Done NA Not Applicable X C See Comments X V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Location Oil Rings Journal Clearance Condition Number A-Dia B-Dia C
UNI035748 | FORNEY POWER PLANT | 298016 | Gas Turbine | 337X259 | Generator | Field_Service_Report_ProjectID_A-1909676_EV-174647_EVP-549080.pdf | 2d766855-7f77-4a20-98f5-800d77e3fcd8 | 2024-12-03 | 2024-11-07 | Call-Out |  |  | TA & Craft Labor | 26 | NO | 0 |  | ask the outage team was asked to remove the coupling guard to provide access to Generator N1 bearing for Luminant site personnel to clean the area. 1.3 EHS The EHS appro
UNI035748 | FORNEY POWER PLANT | 298016 | Gas Turbine | 337X259 | Generator | Field_Service_Report_ProjectID_A-1828654_EV-156989_C-10378885_EVP-536652.pdf | 3357380e-522e-47d1-aa13-be2498967feb | 2024-03-13 | 2024-03-01 | Borescope Inspection (BI) |  |  | TA Only | 12 | NO | 0 |  | are routed down the right and left side of the drain tunnel and the turbine and generator end connections appear intact. The upper and lower half flex seals were inspect
UNI035748 | FORNEY POWER PLANT | 298016 | Gas Turbine | 337X259 | Generator | Field_Service_Report_ProjectID_A-1835108_EV-158090.pdf | 648dd2a4-f866-435e-934b-a2034d4b6bf5 | 2023-09-22 | 2023-09-08 | Call-Out |  |  | TA Only | 14 | NO | 0
UNI035748 | FORNEY POWER PLANT | 298016 | Gas Turbine | 337X259 | Generator | Field_Service_Report_ProjectID_A-1655918_FSP-305393_C-10358660.pdf | 749af55e-b4ab-4ca5-9af5-5eb4abfca520 | 2021-04-28 | 2021-03-31 | Call-Out |  |  | TA & Craft Labor | 28 | YES | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | . 337X259 Prepared by J. Drumgole INSPECTIONS & CHECKS CODE Ball Contact Check Megger Bearing Insulation X Work Carried Out Ball Pinch Check Inspect Bearing Insulation N Not Done Ball Torque Check Inspect Pipe Flange Insulation NA Not Applicable Twist & Tilt Check C See Comments Journal Inspection V Visual Inspection Babbit Inspection MP Mag. Particle Screens & Orifices UT Ultrasonic T/C Calib. PT Penetrant Bearing Bearing Inboard Outboard Journal Vertical Clearance No. Type A-Dia B-Dia C-Dia A-
UNI035748 | FORNEY POWER PLANT | 298016 | Gas Turbine | 337X259 | Generator | Field_Service_Report_ProjectID_A-1797522_EV-150425.pdf | 220df9d6-700c-49de-a72d-676b842370ee |  | 2023-03-16 | Call-Out |  |  | TA & Craft Labor | 0 | NO | 0
UNI036241 | Liberty Electric Power Station | 297569 | Gas Turbine | 337X166 | Generator | Field_Service_Report_ProjectID_EV-121926_C-10355414.pdf | 38149a93-99fa-4893-949a-9399faa893ee | 2022-05-24 | 2022-04-08 | Stand Alone Large Upgrade |  |  | None | 46 | NO | 0 |  | ardware locations, IP addresses and port identifications. 4/10 A016 GAS TURBINE GENERATOR CONTROL AND PROTECTION PANEL DWG#: 302T7046-A016 Part #: NONE MLI A016 provides
UNI036241 | Liberty Electric Power Station | 297569 | Gas Turbine | 337X166 | Generator | Field_Service_Report_ProjectID_FSP-314304_C-10365842.pdf | 2e81650e-16df-4199-8165-0e16df0199e1 | 2021-11-09 | 2021-10-05 | Call-Out |  |  | TA Only | 35 | NO | 0
UNI036483 | Moss Landing | 297604 | Gas Turbine | 337X752 | Generator | Field_Service_Report_ProjectID_A-1841668_EV-156873_EVP-538624.pdf | bb3c8bff-5019-42fb-b342-d9338fda1da2 | 2025-06-11 | 2025-05-03 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 39 | NO | 0 |  | ft hoses are routed down the right side of the drain tunnel and the turbine and generator end connections appear intact. Compressor Section The bellmouth appears faded a
UNI036483 | Moss Landing | 297604 | Gas Turbine | 337X752 | Generator | Field_Service_Report_ProjectID_A-1829790_EV-156862_C-10377610_EVP-536772.pdf | 0d48ffff-f03c-4997-93f8-2174f8ec39a6 | 2024-06-28 | [6 empty] | NO | 0
UNI036483 | Moss Landing | 297604 | Gas Turbine | 337X752 | Generator | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 732f755b-38d3-4e7a-af75-5b38d34e7add | 2022-05-25 | 2022-04-01 | Hot Gas Path Inspection (HGPI) |  |  | TA & Craft Labor | 54 | YES | 56 | 10-minute 5000 VDC Megger PI, AC Impedance, Amortisseur, Amortisseur Migration, Belly Bands, Belly band inspection, Blocked Vent Ducts, Collector Rings, Core, Core Tightness Test, Core tightness test, DC Leakage, DLRO, End-winding, Field Body, Flux Probe Resistance, Flux probe resistance, Focused Generator Inspection, Greasing, HVB cleaning, High Voltage Bushings, Keybars, Loose End-winding Blocking, MAGIC Inspection, RTD Ohmic resistance and 1-minute Megger, Red Eye Repair, Red eye repair on end winding, Retaining Rings, Visual inspection using MAGIC robot and borescope, Winding Resistance, Winding resistance DLRO, End Shield, Fan Blades, Generator Pressure Test, Hydrogen Case, Hydrogen Seal Assembly, Inner Gas Shield, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Wedges, Bluing, Polarization Index, Turn Jumper, DC Hipot, Wedge Tightness Test, Water Ingress, Wet Tie Repair, Gooseneck, Main Lead, Pole Jumper, Step Iron, Sub-slots, Centering Ring, Stator Winding, Lamination Damage | The following report documents all work performed on unit 337X752 (GT3) at Dynegy Corporation, LLC – Moss Landing Power Plant located in Moss Landing, California. The scheduled outage was started on April 03, 2022 and finished April 13, 2022. The intent of this report is to assess the current generator condition and ensure it can safely return to service. Due to the findings of loose end-winding blocking and amortisseur migration in the field (generator rotor), engineering has deemed it not suit
UNI036483 | Moss Landing | 297604 | Gas Turbine | 337X752 | Generator | Field_Service_Report_ProjectID_A-1672096_FSP-309847_C-10362177.pdf | 3a6b9405-15af-496c-ab94-0515af496cf1 | 2021-07-16 | 2021-05-19 | Call-Out |  |  | TA & Craft Labor | 58 | NO | 0
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1828544_EV-156980_EVP-536639.pdf | f226fd54-9262-41e3-9342-68a6b74f292a | 2025-05-01 | 2025-04-20 | Borescope Inspection (BI) |  |  | TA Only | 11 | NO | 0
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1838406_EV-158746.pdf | e62422c7-768e-453c-989c-ff55df4a0f92 | 2023-10-21 | 2023-09-26 | Call-Out |  |  | TA Only | 25 | NO | 0
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1742716_EV-138064.pdf | 23720ab3-25c8-4741-a585-a709389646ba | 2023-06-13 | [6 empty] | NO | 0
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1693562_EV-110128_C-10366338.pdf | d28e20b0-2ff0-49ce-8e20-b02ff0a9ce6a | 2022-05-10 | 2022-04-03 | Call-Out |  |  | TA & Craft Labor | 37 | NO | 0 |  | Hours: - Per Diem: NO Technician Signature: Donavon Ross Computer and/or Camera Generator Misc. Markers: Cleaner: 1 Emulsifier: No. of Welds: 3 No. of Personnel: 2 Techn
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1676064_FSP-310859_C-10363140.pdf | 172d046f-98c8-4be8-ad04-6f98c8fbe8ea | 2021-08-02 | 2021-06-29 | Call-Out |  |  | TA Only | 34 | NO | 0
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1651010_FSP-304339_C-10357876.pdf | 09d53517-90ba-4133-9535-1790ba813392 | 2021-05-10 | 2021-04-04 | Call-Out |  |  | TA Only | 36 | NO | 0 |  | nant Unit Number: 3 Site: Odessa Ector Turbine S/N: 297492 Location: Odessa, TX Generator S/N: xxxxxx VGC-1 - PM1 Gas Control Valve Date Form Completed: 04/07/21 units:
UNI036548 | ODESSA ECTOR POWER PLANT | 297492 | Gas Turbine | 337X154 | Generator | Field_Service_Report_ProjectID_A-1625904_FSP-297690_C-10352577.pdf | 93fdfbbd-98b4-4297-bdfb-bd98b462976b | [7 empty] | NO | 0 |  | POWER HOLDINGS, LLC 3.1 TIL/ETC Completed for 297492 Compliance Required Name: GENERATOR VENTILATION TROUBLE SHUTDOWN FAILURE Til #: 1806 Date of Disposition: 17 Nov 20
UNI036662 | Pleasants County Peaking Power | 297785 | Gas Turbine | 337X186 | Generator | Field_Service_Report_ProjectID_A-1676372_EV-109418_C-10363201.pdf | 81a33780-0285-41c5-a337-800285a1c553 | 2022-05-09 | [6 empty] | NO | 0
UNI036662 | Pleasants County Peaking Power | 297785 | Gas Turbine | 337X186 | Generator | Field_Service_Report_ProjectID_A-1586280_FSP-286393_C-10345025.pdf | 357699c1-5a32-42bc-b699-c15a32b2bc7c | 2021-06-19 | [6 empty] | NO | 0
UNI036546 | ODESSA ECTOR POWER PLANT | 297491 | Gas Turbine | 337X153 | Generator | Field_Service_Report_ProjectID_A-1982160_EV-189339_EVP-558374.pdf | 090255b0-927a-4a2a-b5ba-de49da554114 | 2026-04-21 | 2026-04-14 | Call-Out |  |  | TA & Craft Labor | 7 | NO | 0
UNI036546 | ODESSA ECTOR POWER PLANT | 297491 | Gas Turbine | 337X153 | Generator | Field_Service_Report_ProjectID_A-1828524_EV-156978_EVP-536637.pdf | c96021c0-bbc4-4b84-812a-5610ae6afc54 | 2025-04-23 | 2025-04-13 | Borescope Inspection (BI) |  |  | TA Only | 10 | NO | 0
UNI036546 | ODESSA ECTOR POWER PLANT | 297491 | Gas Turbine | 337X153 | Generator | Field_Service_Report_ProjectID_A-1663170_FSP-307138_C-10360133.pdf | 8d3dc893-b1fb-4837-bdc8-93b1fb5837ca | 2021-04-28 | 2021-03-18 | Call-Out |  |  | TA & Craft Labor | 41 | NO | 0
UNI036546 | ODESSA ECTOR POWER PLANT | 297491 | Gas Turbine | 337X153 | Generator | Field_Service_Report_ProjectID_A-1643452_FSP-302637_C-10356478.pdf | 20e6d39f-b9ca-46fd-a6d3-9fb9ca26fd2f | 2020-12-16 | 2020-12-07 | Call-Out |  |  | TA Only | 9 | NO | 0 |  | M MODIFICATION Til #: 1844 Date of Disposition: 16 Dec 2020 Recurring: No Name: GENERATOR VENTILATION TROUBLE SHUTDOWN FAILURE Til #: 1806 Date of Disposition: 16 Dec 20
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1838094_EV-158694_EVP-537998.pdf | dee1fe38-98d9-4679-bdc4-71af77f64c3b | 2026-04-29 | 2026-04-19 | Borescope Inspection (BI) |  |  | TA Only | 10 | NO | 0
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1956482_EV-184587_EVP-555132.pdf | b327268e-dff3-4e77-ba1f-1453f133c1e2 | 2025-07-30 | 2025-07-25 | Call-Out |  |  | TA Only | 5 | NO | 0
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_NEX-P-220311_SP-ES0-014993.pdf | 11c5bc97-e77b-4e88-8cab-3260afc52d6e | 2024-06-06 | [6 empty] | NO | 0 |  | Outage Type: Planned Outage Turbine Major Generator Major (rotor out) GEGEGE GE Vernova Confidential and Proprietary Information. N
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1763450_EV-142782_C-10378974_EVP-527473.pdf | 0b922258-ebb7-400e-8cc2-2ab3f6537248 | 2024-03-13 | 2024-03-01 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 12 | NO | 0 |  | are routed down the right and left side of the drain tunnel and the turbine and generator end connections appear intact. The upper and lower half flex seals were inspect
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1749564_EV-139460_C-10374153_EVP-525749.pdf | c0d876e9-aeac-42ea-9d6b-e5a6d796598e | 2023-11-21 | 2023-11-02 | Hot Gas Path Inspection (HGPI) | Major Inspection (Robotic) | 140179 | TA & Craft Labor | 19 | NO | 0 |  | – Thickclient HMI Upgrade GT 1 SN:298015 GT 2 SN:298016 GT 3 SN:298017 GEN 1 SN:337X236 GEN 2 SN:337X259 GEN 3 SN:337X260
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1693582_EV-110985_C-10366340.pdf | c4060905-2501-4cfe-8609-052501bcfe91 | 2022-04-20 | 2022-03-15 | Call-Out |  |  | TA & Craft Labor | 36 | NO | 1 | Seal Rings | . Borescope ports in the turbine casing allowed viewing of the first stage nozzle, first stage buckets, second stage nozzle, second stage buckets, third stage nozzle, and third stage buckets. 3. Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 1108-R1 CAST SEGMENTED TURBINE NOZZLE ACCEPTANCE GUIDELINES TIL 1502-2R1 7F AND 9F AFT END COMPRESSOR RUBS TIL 1509-R4 F-CLASS FRONT END (R0, S0, AND R1) COMPRESSOR INSPECTIONS TIL 1562-R1 HEAVY DUTY GAS TURBINE SHIM MIGRATION AND LO
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1606112_FSP-292747_C-10349254.pdf | 6ede7ed3-8872-4336-9e7e-d388723336d3 | 2021-04-28 | 2021-03-30 | Call-Out |  |  | TA & Craft Labor | 29 | NO | 0
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | GAS_TURBINE_INSPECTION_REPORT_EX2100_Exciter__LCI_Checks_for_FPLE_FORNEY_LP_FPLE_FORNEY_LP_Unit_1_Gas_Turbine_298015_2010-04-05 | 090dbba1800bad81 | 2010-04-08 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X236 Accessory Gear S/N: Service Type: CONTRACT MAINT Office Location: FSR#: 426K011
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1546708_FSP-273129_C-10335675.pdf | cdc65bc5-c311-48c2-865b-c5c31188c2bf | [7 empty] | NO | 0 |  | r: LUMINANT Unit Number: GT11 Report Issued Date: FORNEY, TX USA Generator S/N: 337X236 Site: Turbine S/N: 02/24/20 1.1 GT11 Generator High Voltage Time Delay VHiTripS
UNI035747 | FORNEY POWER PLANT | 298015 | Gas Turbine | 337X236 | Generator | Field_Service_Report_ProjectID_A-1747374_EV-138968_C-10371456.pdf | b498618a-ffba-44a2-9d86-438f192a92f8 |  | 2023-03-13 | Call-Out |  |  | TA & Craft Labor | 0 | NO | 0
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1815894_EV-154612_EVP-534944.pdf | 0e7cafc6-7321-451a-a526-a1d318e02722 | 2025-04-21 | 2025-04-04 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 17 | NO | 0
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1731630_EV-135699.pdf | 4c817137-a46b-4e2d-a5a9-761cc617ec09 | 2022-06-22 | 2022-04-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 76 | NO | 1 | Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted.
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1698010_EV-115199_C-10366913.pdf | 95f01b2e-eea9-4969-b01b-2eeea9696961 | 2022-04-27 | 2022-04-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 20 | NO | 0
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1676608_EV-121640_C-10363240.pdf | 9e2e8a86-e06b-4ea6-ae8a-86e06beea620 | 2021-12-02 | 2021-11-08 | Call-Out |  |  | TA & Craft Labor | 24 | NO | 1 | Seal Rings | . 3. Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 1565 Safety Precautions to follow while working on Variable Guide Vanes TIL 2302 S1N Inner Support Rind Seal Housing Inspection TIL 1769 F Class Aft Stator Rocking Inspection TIL 1850-R2 F Class Shrouded Stator 17 Inspection TIL 2049-R2 F Class Inlet Guide Vane to Rub Ring Rubbing TIL 1582-R2 F and H Class Lift Oil Hose Inspection 4. Engineering Requests Engineering Requests (ER) GE Power Inspection & Life Extension Ser
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1636070_FSP-300586_C-10355243.pdf | 9c90e19f-53fa-4d5f-90e1-9f53fa4d5fd0 | 2021-06-10 | 2021-04-08 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 63 | NO | 1 | Seal Rings | . The technical data herein is the property of GE and Section HGP Stage 3 Component Blade Location Platform Sub-Location Leading Edge SS Observation Typical Comments HGP_3_Blade_Platform_Leading_Edge_SS001.JPG Section HGP Stage 3 Component Blade Location Platform Sub-Location Trailing Edge SS Observation Typical Comments HGP_3_Blade_Platform_Trailing_Edge_SS001.JPG GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclo
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | GAS_TURBINE_INSPECTION_REPORT_Unit_2B_Hot_Gas_Path_Inspection_for_DOMINION_ENERGY_Fairless_Unit_2B_GT_Gas_Turbine_298235_2012-03-24 | 090dbba180113bcf | 2012-05-17 | [6 empty] | YES | 5 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | GAS TURBINE INSPECTION REPORT Unit 2B Hot Gas Path Inspection for DOMINION ENERGY Fairless, Unit 2B GT Equipment Serial #: 298235 Job Start Date: March 24, 2012 Report Issued: May 17, 2012 FSR #: 10128810 Report Printed: June 15, 2012 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: DAVID HASSON Field Engineer Approved By: JOSEPH S DAMATO Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 RECOMMENDATIONS 7 PARTS USED & REC
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | GAS_TURBINE_INSPECTION_REPORT_SPRING_2010_ENHANCED_BORESCOPE_INSP._for_DOMINION_FAIRLESS_ENERGY_DOMINION_ENERGY_Unit_2B_GT_Gas_Turbine_298235_2010-05-05 | 090dbba1800b93dd | 2010-06-29 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X742,270T610 Accessory Gear S/N: N/A Service Type: CONTRACT MAINT Office Location: N
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | GAS_TURBINE_INSPECTION_REPORT_Unit_2B_Spring_CBMo_for_DOMINION_ENERGY_Fairless_Unit_2B_GT_Gas_Turbine_298235_2012-03-24 | 090dbba18010ae88 | [7 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X742,270T6 Accessory Gear S/N: Service Type: CONTRACT MAINT Office Location: NE FS-N
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1815934_EV-154616_EVP-534948.pdf | d4a1f313-ddd3-4447-92c4-bfd314f51119 |  | 2026-04-09 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI035721 | FAIRLESS ENERGY CENTER | 298235 | Gas Turbine | 338X742 | Generator | Field_Service_Report_ProjectID_A-1796158_EV-150178_C-10378206_EVP-531950.pdf | c6c0c9b3-71bf-49a5-8aee-a35642589212 | [7 empty] | NO | 0
UNI035749 | FORNEY POWER PLANT | 298017 | Gas Turbine | 337X260 | Generator | Field_Service_Report_ProjectID_A-1958974_EV-185100_EVP-555490.pdf | 41e8955b-ee25-4337-a633-eea618ee4772 | 2025-08-18 | 2025-08-15 | Call-Out |  |  | TA & Craft Labor | 3 | NO | 0
UNI035749 | FORNEY POWER PLANT | 298017 | Gas Turbine | 337X260 | Generator | Field_Service_Report_ProjectID_A-1858948_EV-163675_C-10379169_EVP-541704.pdf | 85001f86-411b-4e71-9a09-1668cead0740 | 2024-03-29 | 2024-03-18 | Call-Out |  |  | TA & Craft Labor | 11 | NO | 0
UNI035749 | FORNEY POWER PLANT | 298017 | Gas Turbine | 337X260 | Generator | Field_Service_Report_ProjectID_A-1870148_EV-165983_C-10379779_EVP-543334.pdf | 51d38d82-7dd8-42ec-b380-5ff0b6cf4099 | 2024-03-28 | 2024-03-18 | Call-Out |  |  | TA & Craft Labor | 10 | NO | 0
UNI035749 | FORNEY POWER PLANT | 298017 | Gas Turbine | 337X260 | Generator | Field_Service_Report_ProjectID_A-1828664_EV-156990_C-10378884_EVP-536653.pdf | 0398b44f-8804-40aa-9b58-dadb234e1bf5 | 2024-03-13 | 2024-03-01 | Borescope Inspection (BI) |  |  | TA Only | 12 | NO | 0 |  | ft hoses are routed down the right side of the drain tunnel and the turbine and generator end connections appear intact. The rubber hose that surrounds the lift hoses ap
UNI035749 | FORNEY POWER PLANT | 298017 | Gas Turbine | 337X260 | Generator | GAS_TURBINE_INSPECTION_REPORT_Unit_3_EX2100_Excitation_Checks_for_FPLE_FORNEY_LP_FPLE_FORNEY_LP_Unit_3_Gas_Turbine_298017_2010-04-05 | 090dbba1800b4c63 | 2010-04-08 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X260 Accessory Gear S/N: Service Type: Office Location: SW CM&U-DALLAS 02 (DC) FSR#:
UNI035749 | FORNEY POWER PLANT | 298017 | Gas Turbine | 337X260 | Generator | Field_Service_Report_ProjectID_A-1797512_EV-150424.pdf | 65e1a8a4-1b8d-47d9-9b67-d03b5de75bc0 |  | 2023-03-16 | Call-Out |  |  | TA & Craft Labor | 0 | NO | 0
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1941660_EV-181747_EVP-553292.pdf | 72fa4c47-df0a-48ac-b290-7e1d447bf834 | 2025-09-03 | 2025-08-01 | Call-Out |  |  | TA Only | 33 | NO | 0
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1926412_EV-177984_EVP-551273.pdf | 8786e76c-9671-4896-bcb5-d699c87c86db | 2025-06-10 | 2025-05-25 | Call-Out | Unusual | 182064 | TA Only | 16 | NO | 0 |  | By 04/18/25 ODESSA ECTOR POWER PLANT 297490 Location: ODESSA, TX Generator S/N: 337X152 Site: Turbine S/N: Rick Jesser 706 498 6356 Customer: Luminant Unit Number: GT1
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1917748_EV-176341_EVP-550190.pdf | 276f2ec6-56a0-4a6e-b696-71ce7a15a1c9 | 2025-01-22 | 2025-01-07 | Unusual | Minor Inspection | 142407 | TA Only | 15 | NO | 0
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1797912_EV-150512.pdf | 31913898-434a-434f-9f14-d26045522cdb | 2023-05-07 | 2023-03-20 | Call-Out |  |  | TA & Craft Labor | 48 | NO | 0 |  | isposition: 30 Mar 2023 Recurring: No Comment: Control Scope (extra work) Name: GENERATOR VENTILATION TROUBLE SHUTDOWN FAILURE Til #: 1806 Date of Disposition: 30 Mar 20
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1693542_EV-119622_C-10366335.pdf | 71e251a4-aeff-4759-a251-a4aeffc759b8 | 2022-04-25 | 2022-03-15 | Call-Out |  |  | TA & Craft Labor | 41 | NO | 0 |  | ROKE REFERENCE Til #: 2310 Date of Disposition: 17 Mar 2022 Recurring: No Name: GENERATOR VENTILATION TROUBLE SHUTDOWN FAILURE Til #: 1806 Date of Disposition: 17 Mar 20
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1683424_FSP-312724_C-10364546.pdf | 39207ebb-8bb0-4987-a07e-bb8bb0a98752 | 2021-08-30 | 2021-08-02 | Call-Out |  |  | TA Only | 28 | NO | 0
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1651000_FSP-304340_C-10357875.pdf | d396628e-1bfe-4733-9662-8e1bfe4733c7 | 2021-04-28 | 2021-03-14 | Call-Out |  |  | TA Only | 45 | NO | 0
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | GAS_TURBINE_INSPECTION_REPORT_Support_of_Forced_Outage_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2012-03-28 | 090dbba18010c494 | [7 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X152,270T4 Accessory Gear S/N: NA Service Type: TECH DIRECTION Office Location: SW F
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 090dbba1800f1be4 | [7 empty] | YES | 8 | End Shield, Generator Pressure Test, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Fan Blades, Collector Rings | . All of the shims that were less than 0.040” were removed and the unit was shimmed and the blades were machined to get the drops within specs. The shims that were installed were not pinned by request of the customer. The Combustion Section was disassembled and the coatings were examined for damage. There was not any extensive chipping, burning, or darkening of the coatings in the liners or TPs. The Fuel Nozzles had some deposits on the tips, but not any extensive damage or wear. The Fuel Nozzle
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | GAS_TURBINE_INSPECTION_REPORT_Support_of_Major_Inspection_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-01 | 090dbba1800f1758 | [7 empty] | NO | 1 | MAGIC Inspection | . For additional information on the gas stop ratio and control valve, refer to the Service Manual under the Fuel System tab. RECOMMENDATIONS Item InsRec PU RI QTY UM PartsDescription CustStk Catalog Drawing 1 7 X 3 EA Mark V Control,39v-t Vib Sensor (seismic) Tur,Turbine Bearing #2 G0415 329A3529P029 2 8 X 1 EA Mark V Control,39v-g Vib Sensor (seismic) Gen,Generator Brg # 3 G0440 329A3529 3 14 X 2 EA Mark V Control,26qt Lube Oil Header Temp,Accessory Module G0416 363A5545 4 26 X 2 EA Mark V Cont
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_FSP-289223_C-10346803.pdf | fdafad17-e8a9-4832-afad-17e8a93832c0 | [7 empty] | NO | 0
UNI036545 | ODESSA ECTOR POWER PLANT | 297490 | Gas Turbine | 337X152 | Generator | Field_Service_Report_ProjectID_A-1874826_EV-166968_C-10379955_EVP-544024.pdf | 06f97dbd-80e3-4f97-b910-d07475953cd2 |  | 2024-03-13 | Borescope Inspection (BI) |  |  | Craft Labor Only | 37 | NO | 0
UNI035753 | FORNEY POWER PLANT | 298020 | Gas Turbine | 337X263 | Generator | Field_Service_Report_ProjectID_A-1828892_EV-156994_C-10377658_EVP-536684.pdf | ca6ea17a-4271-4544-a8c4-f0c34c1db33b | 2024-04-07 | 2024-03-12 | Borescope Inspection (BI) |  |  | TA Only | 26 | NO | 0 |  | are routed down the right and left side of the drain tunnel and the turbine and generator end connections appear intact. The upper and lower half flex seals were inspect
UNI035753 | FORNEY POWER PLANT | 298020 | Gas Turbine | 337X263 | Generator | Field_Service_Report_ProjectID_A-1712714_EV-127597.pdf | 28e17946-5b16-43c5-a179-465b16e3c57d | 2022-02-14 | 2022-01-19 | Call-Out |  |  | TA & Craft Labor | 26 | NO | 0 |  | checks at Luminant Forney Power Station, Forney TX, on unit #23, serial number 337X263. The call-out work started on Wednesday January 19, 2020, FieldCore mobilized F
UNI026367 | INDEPENDENCE POWER STATION | 296301 | Gas Turbine | 337X003 | Generator | Field_Service_Report_ProjectID_A-1791794_EV-149147_EVP-531199.pdf | 31257c1d-f232-4dbf-b0e4-d654ade38657 | 2025-05-06 | 2025-04-05 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 31 | NO | 0
UNI026367 | INDEPENDENCE POWER STATION | 296301 | Gas Turbine | 337X003 | Generator | GAS_TURBINE_INSPECTION_REPORT_BORESCOPE_INSPECTION_AND_LINER_CHANGE_OUT_for_DYNEGY_INC_DYNEGY_INDEPENDENCE_Unit_3_Gas_Turbine_296301_2011-05-15 | 090dbba1800de22b | 2011-05-27 | [6 empty] | NO | 0 |  | : MS7001FA Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X003 Accessory Gear S/N: Service Type: CONTRACT MAINT Office Location: NE FS-SYRACUS
UNI026367 | INDEPENDENCE POWER STATION | 296301 | Gas Turbine | 337X003 | Generator | Field_Service_Report_ProjectID_A-1570254_FSP-281861_C-10341867.pdf | 1e93c896-1f89-4ed2-93c8-961f894ed2d2 |  | 2020-10-17 | Call-Out |  |  | TA & Craft Labor | 7 | NO | 0
UNI037112 | Washington Energy Facility | 297624 | Gas Turbine | 337X767 | Generator | Field_Service_Report_ProjectID_A-1883364_EV-168485_C-10380473_EVP-545326.pdf | 9caff5d3-b014-40bd-8094-063522420445 | 2024-07-12 | 2024-06-08 | Call-Out |  |  | TA & Craft Labor | 34 | NO | 0 |  | consists of the following equipment: • (2) GE 7FA.04 Gas Turbines • (2) GE 7FH2 Generators • (1) GE D11 Steam Turbine • (1) GE 324 Generator GT2 is a GE Frame 7FA.04 Gas
UNI037112 | Washington Energy Facility | 297624 | Gas Turbine | 337X767 | Generator | Field_Service_Report_ProjectID_A-1716970_EV-131391_C-10373055.pdf | 2f792349-4dd3-4aea-8c2e-d4003e6bae26 |  | 2023-04-15 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI037112 | Washington Energy Facility | 297624 | Gas Turbine | 337X767 | Generator | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | c65fa801-134d-4fdf-9fa8-01134d9fdfc8 |  | 2020-10-10 | Hot Gas Path Inspection (HGPI) |  |  | TA & Craft Labor | 0 | YES | 33 | DC Leakage, End-winding, Focused Generator Inspection, Greasing, High Voltage Bushings, MAGIC Inspection, Polarization Index, Red Eye Repair, Stator Winding, Visual inspection using MAGIC robot and borescope, Wedge Tightness Test, Wedges, Winding Resistance, Core, DC Hipot, Hydrogen Seal Assembly, Amortisseur, Centering Ring, Collector Rings, Fan Blades, Field Body, Retaining Rings, Oil Deflector Alignment, Oil Deflectors, End Shield, Main Lead, Sub-slots, Turn Insulation Migration, Wedge Looseness, Step Iron, AC Impedance, Gooseneck, Blocked Vent Ducts | Generator components tested and inspected during this outage period are discussed, in detail, within the body of this report. Photos and data sheets relevant to this outage inspection are attached to this report as well. GENERATOR STATOR VISUAL INSPECTION (Performed): 1 - Visual Inspection on Stator Air-Gap Region using the MAGIC Robot 2 - Visual Inspection on Stator End Winding Assembly (Visual and Magic Borescope) 3 - Visual Inspection on Generator Stator Frame 4 - Visual Inspection on High Vo
UNI036485 | Moss Landing | 270T483 | Steam Turbine | 290T483 | Generator | Field_Service_Report_ProjectID_A-1694598_EV-116650_C-10366425.pdf | 4e588cce-4964-46bd-8c0a-8bed1f6276da | 2022-06-30 | 2022-05-14 | Call-Out |  |  | TA Only | 47 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1941518_EV-181351_EVP-553249.pdf | 9f463fdb-1e84-44d4-bf88-88d19fb47e8d | 2025-06-02 | 2025-05-16 | Call-Out |  |  | TA & Craft Labor | 17 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1815884_EV-154611_EVP-534943.pdf | ca5b220a-2067-40b6-a237-fca7d60d6654 | 2025-04-22 | 2025-03-29 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 24 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1846696_EV-153844_C-10379028_EVP-539482.pdf | a0fda7d3-db4f-4d2d-97ef-68d4aa6f2d41 | 2024-05-08 | 2024-04-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 31 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1697990_EV-122680_C-10366911.pdf | 939e619e-639d-4b66-9e61-9e639deb66f4 | 2022-04-27 | 2022-04-01 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 26 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1722040_EV-132310_C-10369389.pdf | 31476842-fb4f-42f0-8768-42fb4f32f0c6 | 2022-04-01 | 2022-04-01 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1676588_FSP-310968_C-10363236.pdf | e18f8243-0818-4772-8f82-430818a772af | 2021-12-09 | 2021-10-30 | Call-Out | Call-Out | 125445 | TA & Craft Labor | 40 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1636050_FSP-300581_C-10354825.pdf | 14f3d43f-9e5b-4aec-b3d4-3f9e5beaec27 | 2021-06-09 | 2021-04-01 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 69 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 090dbba1800dbd32 | 2011-05-06 | [6 empty] | YES | 6 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, Retaining Rings | GAS TURBINE INSPECTION REPORT GAS TURBINE MAJOR INSPECTION for DOMINION RESOURCES, INC DOMINION ENERGY, Unit 1B GT Equipment Serial #: 298177 Job Start Date: March 26, 2011 Report Issued: May 06, 2011 FSR #: 10075682 Report Printed: May 18, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: SANG S LEE Field Engineer Approved By: JOSEPH S DAMATO Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 6 RECOMMENDATIONS 9 PARTS U
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | GAS_TURBINE_INSPECTION_REPORT_SPRING_2010_ENHANCED_BORESCOPE_INSP._for_DOMINION_FAIRLESS_ENERGY_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2010-04-27 | 090dbba1800b93d9 | 2010-06-29 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X738,270T610 Accessory Gear S/N: N/A Service Type: CONTRACT MAINT Office Location: N
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-2002440_EV-193244_EVP-561029.pdf | fbf11a4d-0feb-4958-b855-d777c8a8c5b0 |  | 2026-04-08 | Call-Out |  |  | TA & Craft Labor | 0 | NO | 0
UNI035718 | FAIRLESS ENERGY CENTER | 298177 | Gas Turbine | 338X738 | Generator | Field_Service_Report_ProjectID_A-1815924_EV-154615_EVP-534947.pdf | 7bf2adc6-90d3-42c5-aa11-7758922df972 |  | 2026-04-04 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 0 | NO | 0
UNI036147 | KENDALL POWER STATION | 297546 | Gas Turbine | 337X760 | Generator | Field_Service_Report_ProjectID_A-1768548_EV-143357_C-10372933_EVP-527944.pdf | 7020949d-54e7-432b-85e1-c43320eecbc1 | 2024-05-15 | 2024-05-02 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 13 | NO | 0 |  | tor is a GE model 741 (7FH2), Hydrogen-cooled, 212MvA unit, identified as GE SN 337X760. Both, this gas turbine, and its associated generator were placed into service
UNI036147 | KENDALL POWER STATION | 297546 | Gas Turbine | 337X760 | Generator | Field_Service_Report_ProjectID_A-1672552_EV-107128_C-10362310.pdf | 6c09d70a-489b-4357-89d7-0a489b8357ec | 2021-12-07 | 2021-11-03 | Large Call-Out |  |  | TA & Craft Labor | 34 | NO | 2 | Seal Rings, MAGIC Inspection | Date 11/7/21 Turbine S/N 297546 Prepared by Therrien FSR # NA Sketches Enclosed? No Photos Enclosed? Yes Chamber # S/N # Inspected Seal Condition Seal Diameter Disposition 1 NA W NA RN-GE 2 NA W NA RN-GE 3 NA W NA RN-GE 4 NA W NA RN-GE 5 NA W NA RN-GE 6 NA W NA RN-GE 7 NA W NA RN-GE 8 NA W NA RN-GE 9 NA W NA RN-GE 10 NA W NA RN-GE 11 NA W NA RN-GE 12 NA W NA RN-GE 13 NA W NA RN-GE 14 NA W NA RN-GE Comments: Typical wear no out of the ordinary conditions Typical wear no out of the ordinary condit
UNI036149 | KENDALL POWER STATION | 297543 | Gas Turbine | 337X757 | Generator | Field_Service_Report_ProjectID_A-1973036_EV-187359_EVP-557070.pdf | a94bbd41-bb8b-467f-b6f2-c819bca9266f | 2025-11-07 | 2025-10-24 | Call-Out |  |  | TA & Craft Labor | 14 | NO | 0 |  | till considered significant. The identified issues included: • Soft feet on the generator • Migration of shims on the turbine foundation • Exhaust gib key clearance well
UNI036149 | KENDALL POWER STATION | 297543 | Gas Turbine | 337X757 | Generator | Field_Service_Report_ProjectID_A-1665346_EV-122463_C-10360633.pdf | e2555139-b2b7-433f-9551-39b2b7f33f6a | 2022-06-02 | 2022-05-06 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 27 | NO | 2 | Wedge Tightness Test, Wedges | . GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property Serial #297543 DYNEGY KENDALL ENERGY, LLC Power Service Now ER case of Interest: 1) ER-20211118-0921: Kendall Unit 1 Borescope Findings_S1N Seal Housing Hardware Observation The seal housing has: • 9 missing and 1 loose bolt - At least 2 seal housing segments are not meeting TIL 2302 criteria of fully en
UNI037113 | Washington Energy Facility | 297623 | Gas Turbine | 337X768 | Generator | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 090dbba1800ee4c5 | 2011-11-14 | [6 empty] | YES | 8 | Blue Check, Generator Pressure Test, Oil Deflector Alignment, Oil Deflectors, Seal Rings, End Shield, Hydrogen Seal Assembly, Wedge Tightness Test | . 337X768 Prepared by Turbine Serial No. 297623 Units recorded in INSPECTIONS & CHECKS CODE Review EM 3404 Measure Resistance X X Work Carried Out Blue Check X Measure Seal Oil Flow N Not Done Seal Joint Check X Inspect Insulation X NA Not Applicable Measure Rings X Inspect Seal Ring Surf. X C See Comments Measure Step X Inspect Springs X V Visual Inspection Center Seal Assembly X Perform Air Test X MP Mag. Particle Replace Stl. Dowels UT Ultrasonic with Glass Dowels PT Penetrant Non-Condutive T
UNI037113 | Washington Energy Facility | 297623 | Gas Turbine | 337X768 | Generator | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 5819dae1-2f19-44ae-99da-e12f19e4aedf |  | 2020-10-10 | Hot Gas Path Inspection (HGPI) |  |  | TA & Craft Labor | 0 | YES | 32 | 10-minute 5000 VDC Megger PI, 10-minute Megger, Collector Rings, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Visual inspection using MAGIC robot and borescope, Wedge Tightness Test, Wedges, Winding Resistance, Centering Ring, Fan Blades, Field Body, Greasing, Core, DC Hipot, Hydrogen Seal Assembly, Step Iron, Wedge Looseness, End Shield, Main Lead, Pole Jumper, Sub-slots, Turn Insulation Migration, Amortisseur, Gooseneck | Inspections of the generator field showed no major abnormalities and was found in satisfactory condition. All Visual inspections and Electrical tests were performed in accordance with GEK 103566k. Generator components tested and inspected during this outage period are discussed, in detail, within the body of this report. Photos and data sheets relevant to this outage inspection are attached to this report as well. GENERATOR STATOR VISUAL INSPECTION (Performed): 1 - Visual Inspection on Stator Ai
UNI026368 | INDEPENDENCE POWER STATION | 296302 | Gas Turbine | 337X007 | Generator | Field_Service_Report_ProjectID_A-1791834_EV-149158_EVP-531208.pdf | b9c3de63-e55c-4266-97d3-bfec482aefbe | 2025-05-06 | 2025-04-05 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 31 | NO | 1 | Wedges | . GE Vernova Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property of GE and TIL Applicability Table: TIL Title Inspected (YES/NO) TIL-1582-R2 F and H Class Lift Oil Hose Inspection and Replacement YES (Inspection Only) *ETC 257 BORESCOPE INSPECTION REVISION FOR 7FA TRANSITION PIECES YES TIL-1724-R1 Inspection and Cleaning of Quaternary Fuel Annulus in Forward Combust
UNI026368 | INDEPENDENCE POWER STATION | 296302 | Gas Turbine | 337X007 | Generator | Field_Service_Report_ProjectID_A-1570274_FSP-281862_C-10341824.pdf | f37502ce-e3d2-4e53-b502-cee3d2fe5310 |  | 2020-10-17 | Call-Out |  |  | TA & Craft Labor | 5 | NO | 0
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1828100_EV-156900_EVP-536584.pdf | 8ce8fdac-770e-4e54-a316-a9defa0a2e49 | 2025-10-14 | 2025-10-06 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 8 | NO | 1 | Water Ingress | . - S1N inner and outer sidewall cracks noted with some areas of TBC spallation. - S1N leading edge chordal cracks noted. One with larger gap and cooling flow noted. - S1N trailing edge TBC spallation noted with some areas of small crack indications. - S1B leading edge TBC spallation noted. S1B damper pins all present. Some misalignment noted. - S1S TBC spallation noted. - S2N leading edge deposits / cracks noted. - Deposits noted on stage 3 components. - Bent exhaust flex seal noted. - S2N bent
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1828044_EV-156895_C-10380820_EVP-536579.pdf | 457d1aa9-6151-4c60-833d-7462ad12c538 | 2024-11-14 | 2024-10-07 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 38 | NO | 2 | Seal Rings, Water Ingress | . GE Vernova Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property of GE and Power Service Now ER case of Interest: 1) MND-20230625-0200: GT Combustion Profile Anomaly - During recent operation a cold spot of ~45F colder than TTXM was observed across TCs #16-17 while operating around 150 MW. This spot does not swirl with load and is only seen on TCs #16 and 17 at load
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1819130_EV-155258_C-10377898.pdf | 37433a05-caaa-4aa1-aa51-94a808e59b59 | 2023-12-06 | 2023-10-07 | Call-Out |  |  | TA & Craft Labor | 60 | NO | 0
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1688336_EV-125133_C-10365404.pdf | bf412777-1db7-4866-83e1-ac26b0a0c3d7 | 2022-06-22 | 2022-05-20 | Call-Out |  |  | TA & Craft Labor | 33 | NO | 0
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1689588_FSP-314067_C-10365656.pdf | c6b73c7c-568e-4133-b73c-7c568e31339c | 2021-11-16 | [6 empty] | NO | 0
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 090dbba1800f260e | 2011-11-29 | [6 empty] | YES | 5 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Greasing | . END POSITION AIR HYD AIR HYD 1 16.0080 16.0055 16.0080 16.0040 2 16.0080 16.0055 16.0080 16.0040 3 16.0080 16.0050 16.0080 16.0055 4 16.0080 16.0055 16.0090 16.0070 5 16.0080 16.0050 16.0090 16.0070 6 16.0080 16.0050 16.0080 16.0055 AVERAGE 16.0080 16.0053 16.0083 16.0055 SHAFT DIA. 15.9990 15.9990 15.9985 15.9985 CLEARANCE 0.0090 0.0062 0.0098 0.0070 H2 SEAL SPRING MEASUREMENTS TURBINE END COLL. END UPPER LOWER UPPER LOWER LENGTH (±1/16 in.) 26.94 26.94 26.94 27.00 WIRE DIA. 0.12 0.12 0.12 0.
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | GAS_TURBINE_INSPECTION_REPORT_CBM_Inspection_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-08-11 | 090dbba1800e7134 | [7 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 337X053,270T4 Accessory Gear S/N: Service Type: Office Location: NE FS-MEDFORD (RW) Ora
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1636480_FSP-300682_C-10354876.pdf | 6d1e27d6-d6fc-4b4f-9e27-d6d6fcfb4fce |  | 2020-10-22 | Call-Out |  |  | TA & Craft Labor | 0 | NO | 0
UNI036334 | Casco Bay Power Station | 297197 | Gas Turbine | 337X053 | Generator | Field_Service_Report_ProjectID_A-1538976_FSP-270516_C-10333889.pdf | 0b48aecb-994c-4e26-88ae-cb994cce2658 |  | 2020-10-19 | Call-Out |  |  | TA & Craft Labor | 0 | NO | 0
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | e7a1aa51-5217-4a95-89ee-41f1973f2d05 | 2025-05-09 | 2025-03-01 | Major Inspection (MI) | Major Inspection (Robotic) | 131453 | TA & Craft Labor | 69 | YES | 29 | AC Impedance, Belly Bands, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Greasing, Hydrogen Seal Assembly, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance, High Voltage Bushings, Loose End-winding Blocking, Sub-slots, End Shield, Fan Blades, Generator Pressure Test, Oil Deflector Alignment, Oil Deflectors, 10-minute 5000 VDC Megger PI, 10-minute Megger, DLRO, Winding resistance DLRO | This report is related with major outage of GT1( 338X731) generator, at Fayette station in PA between March 5-16 2025. The work scope included stator and field visual inspection, electrical testing, wedge tapping of stator wedges, Elcid integrity of stator iron and belly band / knife check of core iron tightness. The other scope is additional block modification of connection ring and three winders mobilized for this modification. Stator end winding has repaired in previous outage and no sign of
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | Field_Service_Report_ProjectID_A-1717002_EV-131398_C-10368873.pdf | de56bfb9-8a7f-447c-bbd6-6eb02e7a7afd | 2023-11-06 | 2023-10-21 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 16 | NO | 0 |  | rly deep enough. We managed to re-insert the T/C to the proper depth. Fixed GT2 Generator Cold Gas Temperature #24. Helped troubleshoot two flame detector problems on GT
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | GAS_TURBINE_INSPECTION_REPORT_Accumulator_replacement_for_DUKE_ENERGY_NORTH_AMERICA_Fayette_Energy_Facility_Unit_GT1_Gas_Turbine_298158_2011-10-03 | 090dbba1800eb11f | 2011-10-19 | [6 empty] | NO | 0 |  | nic Mark VI/TMR Frame Size: MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 270T552;338X7 Accessory Gear S/N: Service Type: CONTRACT MAIN
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 090dbba1800dee9c | 2011-05-11 | [6 empty] | YES | 12 | Belly Bands, Belly band inspection, End Shield, Fan Blades, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Blue Check, Hydrogen Seal Assembly, Wedge Tightness Test, Keybars | . IGV backlash, x gaps, and busing clearances were taken and all were acceptable. The IGV's and inlet bellmouth were cleaned to help ensure efficient operation. Combustion parts were prepped for re-assembly, Fuel nozzles were switched to FWD cans and DLN caps were installed. A Crossfire bellows modification was performed on the AFT cans replacing the need for packing ensuring a longer and more useful lifespan of the outer crossfire tubes. #1 and #2 bearings were opened, clearances taken and a vi
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | GAS_TURBINE_INSPECTION_REPORT_MAINTENANCE_FOR_EX2100s_AND_ISLCI_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_Gas_Turbine_298158_2010-10-04 | 090dbba1800ca1f6 | 2010-12-01 | [6 empty] | NO | 0 |  | nic Mark VI/TMR Frame Size: MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 270T552;338X7 Accessory Gear S/N: Service Type: TECH DIRECTIO
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | GAS_TURBINE_INSPECTION_REPORT_EX2100s_and_LCI_Checkout_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_Gas_Turbine_298158_2010-10-05 | 090dbba1800c6008 | 2010-10-26 | [6 empty] | NO | 0 |  | nic Mark VI/TMR Frame Size: MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 270T552;338X7 Accessory Gear S/N: Service Type: TECH DIRECTIO
UNI035727 | Fayette Energy Facility | 298158 | Gas Turbine | 338X732 | Generator | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 3dce0f9f-7e98-468d-8e0f-9f7e98768de6 | [7 empty] | YES | 30 | 10-minute 5000 VDC Megger PI, 10-minute Megger, Collector Rings, DC Leakage, End-winding, Focused Generator Inspection, Greasing, High Voltage Bushings, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Visual inspection using MAGIC robot and borescope, Wedge Tightness Test, Wedges, Winding Resistance, Core, DC Hipot, Hydrogen Seal Assembly, Centering Ring, Fan Blades, Field Body, End Shield, Wedge Looseness, Main Lead, Sub-slots, Turn Insulation Migration, Step Iron, DLRO | the core. Inspections of the generator field showed no major abnormalities and was found in satisfactory condition. The results of the electrical test were satisfactory and didn't give any indications for alarm. All Visual inspections and Electrical tests were performed in accordance with GEK 103566K. Generator components tested and inspected during this outage period are discussed, in detail, within the body of this report. Photos and data sheets relevant to this outage inspection are attached
UNI000885 | INDEPENDENCE POWER STATION | 270T260 | Steam Turbine | 290T260 | Generator | g_GE_Energy_Services_Spring_2006_Valve_Inspection_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_5_Steam_Turbine_270T260_2006-04-29 | 090dbba18007898a | 2006-05-25 | [6 empty] | NO | 2 | Retaining Rings, Seal Rings | Valve; During the outage the Main Stop and Control valve was disassembled and inspected. The valve was rebuilt using parts called for in TIL-1531. The following routine maintenance procedures were performed: dimensional checks, NDT, disk-to-seat contact checks, and a try bar check of stem bushing alignment. There was scale build up present in the valve. This scale was not substantial enough to warrant grit blasting. The NDT showed cracking of the anti-swirl dam. These cracks were ground out and
UNI035964 | Hanging Rock Energy Facility | 298127 | Gas Turbine | 338X727 | Generator | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 5a385e69-c891-439d-9b9f-3270ae6faa06 | 2024-12-20 | 2024-10-04 | Major Inspection (MI) | Major Inspection (Rotor Out) | 131521 | TA & Craft Labor | 77 | YES | 7 | Collector Rings, End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | . Air Shroud Installed As Found Brush Rigging As Found Collector End Bearing Lower Half Conditon As Found Collector End Bearings As Found Collector End Lower Half Bearing condition As Found Excitor Fan Blade As Found Exciter Fan Blades As Found Exciter Fan Blades And Shroud As found Excited Base Condition As Found Removed Turning Gear As Found Turbine End Field Journal Condition (2) As Found Turbine End Field Journal Condition As Found Turbine End Upper Half Bearing Axial Alignment Of Brush Rigg
UNI035964 | Hanging Rock Energy Facility | 298127 | Gas Turbine | 338X727 | Generator | Field_Service_Report_ProjectID_A-1675148_EV-114985_C-10362914.pdf | f1d5be2d-2f44-4ac8-95be-2d2f445ac85e | 2022-05-16 | 2022-04-06 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 40 | NO | 1 | Wedges | During the EBI it was found that the lower left side ISR housing had 3 bolts loose along with finding 2 stray bolts lying on the S1N cooling cavities. ER-20220409-0248 was submitted in response to the found loose bolts. Closing notes stated “It is recommended to follow TIL-2302 recommendations. Since 5 or less bolts are still fully engaged in the seal housing install new bolts with nordlock or wedge lock washers only in the locations of missing / slightly backed out bolts. Account for and recove
UNI035964 | Hanging Rock Energy Facility | 298127 | Gas Turbine | 338X727 | Generator | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 090dbba1800f68b3 | 2012-01-17 | [6 empty] | YES | 8 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test, Blue Check, Retaining Rings, Seal Rings | . 298127 Prepared by J Dixson NOTE: 1. On most generator bearings, the end leakage groove is on the outboard end. 2. On hood bearings, the outboard end is set low to compensate for vacuum deflection. TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check CE 16.021" 16.023" 21.0 Mils 23.0 Mils 1.6 Mils 0.0 Mils  TE 16.022" 16.022" 22 Mils 22 Mils 1.6 Mils 0.0 Mils  TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual Chec
UNI035964 | Hanging Rock Energy Facility | 298127 | Gas Turbine | 338X727 | Generator | GAS_TURBINE_INSPECTION_REPORT_High_Bearing_Vibration_and_H2_Seal_Inspection_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-06-18 | 090dbba1800e57cc | 2011-08-23 | [6 empty] | NO | 1 | Hydrogen Seal Assembly | GAS TURBINE INSPECTION REPORT High Bearing Vibration and H2 Seal Inspection for HANGING ROCK, Unit 2GT1 Equipment Serial #: 298127 Job Start Date: June 18, 2011 Report Issued: August 23, 2011 Oracle Project Id: 100101295 Report Printed: August 23, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: PETER MONZON Field Engineer Approved By: MARK RUEFER Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 PARTS USED & RECOMME
UNI035964 | Hanging Rock Energy Facility | 298127 | Gas Turbine | 338X727 | Generator | GAS_TURBINE_INSPECTION_REPORT_2GT1_2_Bearing_Inspection_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_HANGING_ROCK_LLC_Unit_2GT1_Gas_Turbine_298127_2010-05-04 | 090dbba1800b5dee | 2010-05-19 | [6 empty] | NO | 1 | Seal Rings | . Diffuser, Exhaust;Assembly;'W' Seal Purchase a new 'W' seal for future outages. 2. Bearing, Journal;Housing;Parts Replace used stock for next outage. RECOMMENDATIONS Item InsRec PU RI QTY UM PartsDescription CustStk Catalog Drawing 1 1 X 1 Each Bearing, Journal,Assembly,Inboard seal ring G1502 159A0601P001 2 1 X 1 Each Bearing, Journal,Assembly,Outboard seal ring G1502 159A0601P002 3 2 X 32 Each Inlet Guide Vane,Spring,Spring washer G0811 158A7887P001 4 3 1 Each Diffuser, Exhaust,Assembly,Flex
UNI035964 | Hanging Rock Energy Facility | 298127 | Gas Turbine | 338X727 | Generator | GAS_TURBINE_INSPECTION_REPORT_R0_Change_Out_with_R1_R5_Inspection_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2009-05-06 | 090dbba1800e9aa2 | [7 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X727;270T4 Accessory Gear S/N: Service Type: CONTRACT MAINT Office Location: CENT FS
UNI036549 | ODESSA ECTOR POWER PLANT | 297493 | Gas Turbine | 337X155 | Generator | Field_Service_Report_ProjectID_A-1916064_EV-175939_EVP-549937.pdf | 1aafca94-d2a6-4d4a-868f-4fa9b2cbc876 | 2025-01-08 | 2024-12-18 | Call-Out |  |  | TA & Craft Labor | 21 | NO | 0 |  | Start Date: 18 Dec 2024 Outage End Date: 27 Dec 2024 ESN/SY: 297493 ¦ SY0070937 Generator Field Serial Number: NA Oracle Project ID: A-1916064 ¦ EV-175939 ¦ EVP-549937 R
UNI036549 | ODESSA ECTOR POWER PLANT | 297493 | Gas Turbine | 337X155 | Generator | Field_Service_Report_ProjectID_A-1828494_EV-156975_C-10378883_EVP-536634.pdf | 01e44da2-b67c-4b5b-a5d7-235a84f42f92 | 2024-11-26 | [6 empty] | NO | 0
UNI036549 | ODESSA ECTOR POWER PLANT | 297493 | Gas Turbine | 337X155 | Generator | Field_Service_Report_ProjectID_A-1686570_FSP-313453_C-10365083.pdf | 716c2b45-590d-48f9-ac2b-45590de8f95e | 2021-11-29 | 2021-10-14 | Call-Out |  |  | TA & Craft Labor | 46 | YES | 3 | Oil Deflector Alignment, Oil Deflectors, Collector Rings | . The lower half was found to be in poor condition with heavy wear, material loss, and signs of over temp. The journal exhibited scratches and some minor grooving. It was determined that none of the grooves exceeded more the 2 mils. The upper and lower half oil deflectors were inspected and found in good condition. The journal was lapped to remove high spots and a refurbished bearing was installed. The oil deflectors cleaned and reused Turbine End Lower Half Turbine End Upper Half Journal As Fou
UNI036549 | ODESSA ECTOR POWER PLANT | 297493 | Gas Turbine | 337X155 | Generator | Field_Service_Report_ProjectID_A-1656076_FSP-305414_C-10358674.pdf | 6cb826de-7e9f-417a-b826-de7e9fe17a36 | 2021-04-28 | 2021-04-04 | Call-Out |  |  | TA & Craft Labor | 24 | YES | 3 | Oil Deflector Alignment, Oil Deflectors, Collector Rings | V : 16.021 H : 16.042 +.002/-.000 4-12-21 Customer GE - FieldCore JD’s Project Number 15149 P.O. 4900153734 Project Type T-4 – CE (Spare) – 16 X 10-3/4 Bearing Work Scope Full Repair Target Bore Diameter V : 16.021 H : 16.042 +.002/-.000 1 Outgoing Report Customer GE - FieldCore JD’s Project Number 15149 P.O. 4900153734 Project Type T-4 – CE (Spare) – 16 X 10-3/4 Bearing Work Scope Full Repair Target Bore Diameter V : 16.021 H : 16.042 +.002/-.000 2 Outgoing Photos Customer GE - FieldCore JD’s P
UNI036549 | ODESSA ECTOR POWER PLANT | 297493 | Gas Turbine | 337X155 | Generator | GAS_TURBINE_INSPECTION_REPORT_Support_of_Major_Inspection_Gas_Turbine_4_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT4_Gas_Turbine_297493_2012-03-17 | 090dbba180112029 | 2012-06-13 | [6 empty] | NO | 2 | MAGIC Inspection, End Shield | . The motors should be bumped tested after being reconnected for the proper rotation and current draw, and instrumentation should be calibrated back to Mark V. Turbine Enclosure Instrumentation;Cont Devices - Turb The instrumentation, wiring and tubing were disconnected on the turbine in preparation for the major inspection. The sparkplugs and flame detectors were tested prior to being reinstalled in the turbine. New wheelspace thermocouples were installed during the outage and have been tested
UNI036549 | ODESSA ECTOR POWER PLANT | 297493 | Gas Turbine | 337X155 | Generator | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 71720880-e6c9-437b-b208-80e6c9437b53 | [7 empty] | YES | 24 | AC Impedance, Collector Rings, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Loose End-winding Blocking, Polarization Index, Retaining Rings, Wedge Tightness Test, Wedges, Fan Blades, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, End Shield, 10-minute 5000 VDC Megger PI, 10-minute Megger, DLRO, Winding Resistance, DC Hipot, Stator Winding, Seal Rings | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 2 1.4 Work Scope __________ 6 2 Technical __________ 7 2.1 Recommendations __________ 7 3 Turbine __________ 9 3.1 FMI F6291G25 - Mechanical Upgrade __________ 9 3.1.1 ML 0509 Fuel Gas Control Valve __________ 9 3.1.2 ML 0705 Turbine Case Arrangement __________ 15 3.1.3 ML 0909 Cooling and Sealing Piping Arrangement - Orifices Replacement Only __________
UNI036336 | Casco Bay Power Station | 270T432 | Steam Turbine | 290T432 | Generator | Field_Service_Report_ProjectID_EV-188520_EVP-557831.pdf | c2c57b72-427d-4e0c-bad2-b3cdb853a071 | 2026-01-09 | 2025-11-17 | Call-Out | Large Call-Out | 188744 | TA & Craft Labor | 53 | YES | 3 | Seal Rings, Wedges, Collector Rings | . Due to the amount of scale build up and material removed to gain proper clearances, it is recommended to replace. 1.1.4 Main Control Valves Below are the recommended parts needed to support this replacement: Balance Chamber: 228C7374P0001 (Qty 1) Bolt Balance Chamber: U810P306L0175 (Qty 8) CV Disc: 203D4524P0001 (Qty 1) Screws, CV Disc: 182A2017P0009 (Qty 4) I would also plan to do this on the Left side valve assembly too. So the above quantities would be doubled. CBM: NA 1.1.4 Main Control Va
UNI036336 | Casco Bay Power Station | 270T432 | Steam Turbine | 290T432 | Generator | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 090dbba1800e0d97 | 2011-06-03 | [6 empty] | YES | 8 | Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, End Shield, Wedge Tightness Test, Wedges, Seal Rings | STEAM TURBINE INSPECTION REPORT D11 L-0 bucket replacement and valve outage Jan. 2011 for CASCO BAY ENERGY COMPANY LLC, Unit ST Equipment Serial #: 270T432 Job Start Date: January 15, 2011 Report Issued: June 03, 2011 Oracle Project Id: 10079907 Report Printed: July 12, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: MICHAEL THERIAULT Field Engineer Approved By: MICHAEL KERKMANN Service Manager PAGE JOB SUMMARY 1 INSPECTI
UNI036336 | Casco Bay Power Station | 270T432 | Steam Turbine | 290T432 | Generator | g_GE_Energy_Services_D11_Major_Inspection_Technical_Direction_for_Dynergy__LS_Power_MAINE_INDEPENDENCE_Unit_1_Steam_Turbine_270T432_2007-04-09 | 090dbba18007202c | 2007-07-12 | [6 empty] | YES | 4 | Stator Winding, Wedges, Blue Check, End Shield | Core Wedge; Collector End Stator Generator Serial #290X432 sustained damage to an "End Wedge" Assembly during the Major Inspection. The Customer requested GE Product Service to evaluate the damage and issue a repair recommendation. (Refer to PAC # 20070427-0097). GE Product Service evaluated the damage and issued instruction to inspect the Generator in accordance with GEK103566c. They instructed to replace the damaged end wedge during this outage. A thorough visual inspection of the stator bar b
UNI035962 | Hanging Rock Energy Facility | 298113 | Gas Turbine | 338X726 | Generator | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 6f6443d0-6046-45df-82cc-5eb4502b185e | 2024-06-13 | 2024-04-06 | Major Inspection (MI) | Major Inspection (Rotor Out) | 131163 | TA & Craft Labor | 68 | YES | 9 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings, End-winding, Greasing, Wedges | . ST00078 GT2130 Sheet: (a) Rev 1.0 - 09/18/2019 GE Energy Proprietary Information Bearings Equip. Code: 7FA.04 Rotor Journal Condition Date Turbine S/N 338X726 Prepared by FSR # Data Type As Found Units of Measure: Inches Journal Number CE NOTE: Mark on sketch to show grooving, discoloration, carbon inclusions, or irregularities in the journal surface. Diameter 19.0045 Inner Oil Deflector 16.0030 16.0030 16.0030 16.0030 Outer Oil Deflector Diameter Inner Oil Deflector 19.0050 16.0050 16.0050 16
UNI035962 | Hanging Rock Energy Facility | 298113 | Gas Turbine | 338X726 | Generator | Field_Service_Report_ProjectID_A-1675010_EV-110242_C-10362910.pdf | 6f1dda92-9bbe-48a2-9dda-929bbe88a28b | 2022-05-13 | 2022-04-02 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 41 | NO | 0
UNI035962 | Hanging Rock Energy Facility | 298113 | Gas Turbine | 338X726 | Generator | GAS_TURBINE_INSPECTION_REPORT_1GT2_Enhanced_Compressor_Package_2_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_HANGING_ROCK_LLC_Unit_1GT2_Gas_Turbine_298113_2010-05-03 | 090dbba1800b5ded | 2010-05-21 | [6 empty] | NO | 0 |  | MS7001FA+e Fuel Type: Natural Gas Driven Equipment: Generator Driven Equip S/N: 338X726;270T5 Accessory Gear S/N: Service Type: CONTRACT MAINT CS Cincinnati: CENT CS-S
UNI036151 | KENDALL POWER STATION | 297544 | Gas Turbine | 337X758 | Generator | Field_Service_Report_ProjectID_A-1768538_EV-143354_C-10372930_EVP-527941.pdf | 3c98af97-1be2-4eff-811d-a57166eecb4d | 2024-05-15 | 2024-05-02 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 13 | NO | 0 |  | tor is a GE model 741 (7FH2), Hydrogen-cooled, 212MvA unit, identified as GE SN 337X758. Both, this gas turbine, and its associated generator were placed into service
UNI036151 | KENDALL POWER STATION | 297544 | Gas Turbine | 337X758 | Generator | Field_Service_Report_ProjectID_A-1809182_EV-153011.pdf | 402840db-2d05-4b17-8e19-a306a424c176 | 2023-06-16 | 2023-05-18 | Call-Out |  |  | TA & Craft Labor | 29 | NO | 0 |  | , is a GE 7FA combined cycle unit coupled to a GE designed 7FH2 hydrogen cooled generator. General Electric (GE) FieldCore (FC), Atlantic Plant Maintenance (APM), and At
UNI036151 | KENDALL POWER STATION | 297544 | Gas Turbine | 337X758 | Generator | Field_Service_Report_ProjectID_A-1676686_FSP-310992_C-10363356.pdf | dc1e23af-6725-4b32-9e23-af67251b32eb | 2022-06-02 | 2022-04-30 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 33 | NO | 2 | Oil Deflector Alignment, Oil Deflectors | . The technical data herein is the property Serial #297544 DYNEGY KENDALL ENERGY, LLC Previous MI- April' 21 Inspection Summary & Focus area Priority Section of the Turbine Previous Inspection Findings 1 Compressor After MI outage, and this will be the first inspection on Compressor section 2 Combustion All CI parts were replaced during MI outage, and this will be the first inspection on Combustion section 3 Hot Gas Path All HGP parts were replaced during MI outage, and this will be the first in
UNI036151 | KENDALL POWER STATION | 297544 | Gas Turbine | 337X758 | Generator | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | ce84e828-0cd3-4782-84e8-280cd35782aa | 2021-06-15 | 2021-04-10 | Major Inspection (MI) |  |  | TA & Craft Labor | 66 | YES | 32 | AC Impedance, Core, DC Hipot, DC Leakage, End Shield, End-winding, Fan Blades, Greasing, MAGIC Inspection, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance, DLRO, Loose End-winding Blocking, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Retaining Rings, Step Iron, Turn Insulation Migration, Wedge Looseness, Collector Rings, Oil Deflector Alignment, Oil Deflectors, Gooseneck, Main Lead, Pole Jumper, Sub-slots, Centering Ring, 10-minute Megger | . It was visually inspected and appeared to be in good condition. Twist and tilt was recorded and is included below. Recommendation Status: Should be planned for next Outage During the outage the CE axial fan blades were removed to allow access for the MAGIC inspection. After removal they were visually inspected with only one indication noted. The one blade with visual indication had NDE performed because the indication was in a high stress area. No findings were noted. The report is included in
UNI026366 | INDEPENDENCE POWER STATION | 296303 | Gas Turbine | 337X008 | Generator | Field_Service_Report_ProjectID_A-1791774_EV-149145_EVP-531197.pdf | 8cb35c38-3d9e-46a6-b027-2cd48d1dd122 | 2025-05-02 | 2025-04-05 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 27 | NO | 0
UNI026366 | INDEPENDENCE POWER STATION | 296303 | Gas Turbine | 337X008 | Generator | Field_Service_Report_ProjectID_A-1807202_EV-152640.pdf | 20dc55d0-3d46-4f7f-9a92-6ce490b24ec4 | 2023-06-01 | 2023-05-06 | Call-Out |  |  | TA & Craft Labor | 26 | NO | 0
UNI026366 | INDEPENDENCE POWER STATION | 296303 | Gas Turbine | 337X008 | Generator | Field_Service_Report_ProjectID_A-1673092_FSP-310131_C-10362652.pdf | 9f85e354-11b5-4a10-85e3-5411b52a1093 | 2021-11-16 | 2021-10-09 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 38 | NO | 0
UNI026366 | INDEPENDENCE POWER STATION | 296303 | Gas Turbine | 337X008 | Generator | Field_Service_Report_ProjectID_A-1570244_FSP-281864_C-10341868.pdf | aa00f754-50d2-4e2f-80f7-5450d28e2fea |  | 2020-10-10 | Call-Out |  |  | TA & Craft Labor | 2 | NO | 0
UNI036484 | Moss Landing | 297605 | Gas Turbine | 337X753 | Generator | Field_Service_Report_ProjectID_A-1841678_EV-156874_EVP-538626.pdf | db8738c9-e758-46a8-a7d3-c0eef3942069 | 2025-06-24 | 2025-05-03 | Borescope Inspection (BI) |  |  | TA & Craft Labor | 52 | NO | 0 |  | n & Life Extension Services Customer: Inspection Date: 9-May-25 Station & Unit: Generator #: 297605 Inspector(s): T. Suggs Procedure # and Rev: A0147 Rev 1.1 A B C 0.025
UNI036484 | Moss Landing | 297605 | Gas Turbine | 337X753 | Generator | Field_Service_Report_ProjectID_A-1868914_EV-165642_C-10379716_EVP-543115.pdf | ca0dcfb0-549e-4918-84cd-2a543b67c909 | 2024-06-28 | [6 empty] | NO | 0
UNI036484 | Moss Landing | 297605 | Gas Turbine | 337X753 | Generator | Field_Service_Report_ProjectID_A-1829800_EV-156863_C-10377609_EVP-536773.pdf | 0060f9b5-e41c-4732-8832-c56429d283ce | 2024-06-28 | [6 empty] | NO | 0
UNI036484 | Moss Landing | 297605 | Gas Turbine | 337X753 | Generator | Field_Service_Report_ProjectID_A-1801336_EV-151469.pdf | 47c33e5c-5c88-487d-a8a3-a66e3d0d6300 | 2023-05-15 | 2023-04-07 | Call-Out |  |  | TA & Craft Labor | 38 | NO | 0
UNI036484 | Moss Landing | 297605 | Gas Turbine | 337X753 | Generator | Field_Service_Report_ProjectID_A-1756706_EV-141386_C-10372203.pdf | e4960aec-5771-4a7f-b25f-5d3366a90784 | 2022-09-29 | 2022-09-10 | Call-Out |  |  | TA & Craft Labor | 19 | NO | 0
UNI036484 | Moss Landing | 297605 | Gas Turbine | 337X753 | Generator | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 7eb1b89a-5e58-4ddf-b1b8-9a5e58cddfdd | 2022-05-22 | 2022-04-01 | Major Inspection (MI) |  |  | TA & Craft Labor | 51 | YES | 48 | 10-minute 5000 VDC Megger PI, AC Impedance, Collector Rings, DC Leakage, DLRO, End Shield, End-winding, Fan Blades, Field Body, Flux Probe Resistance, Flux probe resistance, HVB cleaning, High Voltage Bushings, Hydrogen Seal Assembly, Loose End-winding Blocking, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, RTD Ohmic resistance and 1-minute Megger, Red Eye Repair, Red eye repair on end winding, Retaining Rings, Seal Rings, Visual inspection using MAGIC robot and borescope, Winding Resistance, Winding resistance DLRO, Belly Bands, Belly band inspection, Core, Core Tightness Test, Core tightness test, Focused Generator Inspection, Greasing, Keybars, Water Ingress, Wedges, Centering Ring, Gooseneck, Main Lead, Pole Jumper, Sub-slots, Step Iron, Lamination Damage, Turn Insulation Migration, Turn Jumper, Stator Winding, Wedge Tightness Test, Polarization Index | The following section of the report documents all work performed on unit 337X753 (GT4) at Dynegy Corporation, LLC – Moss Landing Power Plant located in Moss Landing, California. The scheduled outage was started on April 03, 2022 and finished April 13, 2022. The intent of this section is to assess the current generator condition and ensure it can safely return to service. Due to the findings of loose/missing end-winding blocking in the field (generator rotor), engineering has deemed it not suitab

## Generator Scope Candidates
Train ID | Plant Name | PDF Name | Tagged ESNs | Tagged Equipment Types | Chunk ID | Page | Report Date | Scope Category | Components | Specific Scope | Keyword Count | Technical Keywords | Findings / Results | Reference Codes | Semantic Seed Query | Excerpt
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1838482_EV-158764_EVP-538036.pdf | 297258 | Gas Turbine | 81e51e98c4ade06e8d4613a1ec3c322a | 4 | 2026-04-06 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 4 | Collector Rings, Fan Blades, Oil Deflector Alignment, Oil Deflectors | Outer oil deflectors were reassembled and clearances were recorded.; The team then proceeded with restoration and alignment activities, including installation of the outer oil deflectors with clearance recording, reinstallation of borescope plugs and CDM probes, and reestablishment of the oil system. |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Oil Deflectors | On 03/21/2026 GE Vernova (GEV) Craft personnel arrived onsite. Personnel consisted of one GEV Supervisor and 10 GEV Millwrights. The job trailer and site setup commenced and GEV tooling was received and staged near the units. On 03/24/2026 the GEV TFA arrived onsite and set up work trailer area. Scope of work was an annual borescope inspection on gas turbines CT-21 and CT-12 as well a T4 bearing swap on CT-21 and a T3 bearing swap on CT-22. The GEV Borescope Specialist arrived onsite on 03/25/20
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1838482_EV-158764_EVP-538036.pdf | 297258 | Gas Turbine | 6f193e13d63bdf632d7234e71ee7f793 | 289 | 2026-04-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | (a) Rev 0.0 - 08/01/98 Bearings Oil Deflectors, Alignment Date 3/27/26 Turbine S/N GEN 337X711 Prepared by GEV FSR # Sketches Enclosed? Photos Enclosed? Data Type As left CT-21 T4 Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location ; (a) Rev 1.0 - 02/27/2023 Bearings Oil Deflectors, Alignment Date 3/27/26 Turbine S/N 297257 Prepared by GEV FSR # Sketches Enclosed? Photos Enclosed? Data Type As left CT-22 T3 Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 |  | Oil Deflector Alignment ¦ Oil Deflectors | . Type A-Dia B-Dia C-Dia A-Dia B-Dia C-Dia Dia. Mils Mils/In 4 16.039 16.039 16.020 16.039 16.040 16.021 15.999 21.0 1.3 Shim Thickness (mils) Ball Seat Pinch Fits Bearing Pinch* Bearing Pinch* Leadwire Size (mils) Number Mils Number Mils 4 * Pinch equals wire thickness minus shim Comments: INSPECTION REPORT Gas Turbine Maintenance C C B B A A GT2105 Sheet: (a) Rev 0.0 - 08/01/98 Bearings MS 3002, 5001, 5002, 7001, 7001F, 9001, 9001F Journal Bearing Clearances – Elliptical Date 3-27-26 Turbine S
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 1030bbcba510a4a7d2891bb308012c2e | 18 | 2026-03-30 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J Inner Oil Deflector K 0.011 0.011 0.012 0.020 0.010 Mid; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J Inner Oil Deflector K 0.011 0.011 0.011 0.018 0.010 Mid |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J Inner Oil Deflector K 0.011 0.011 0.012 0.020 0.010 Middle Oil Deflector L 0.018 0.013 0.013 0.018 0.018 Hydrogen Seal Casing M 0
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 96b5f427b4e860bdead85cc19193abe1 | 4 | 2026-03-30 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | On Thursday, March 26, disassembly began on the end shield and all components situated in its path;; Various measures were implemented to ensure the proper sealing of the CE UH end shield.; Finally, to ensure a secure seal, the Pump End Shield Sealant Grooves with Sealant (GN-3210) procedure was followed, and detailed records of the processes were documented using End Shield Sealant Pumping Log (IR5GE1700).; For future work, it is recommended that the bolts connecting the horizontal and vertical faces be installed in a specific sequence, installing the horizontal bolts first, followed by the vertical ones—and that washers be installed within th |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | On approximately March 17, 2026, the client at Lamar Power Partners LP (3205 Farm Road 137, Paris, TX 75460) from Vistra Corp detected a hydrogen leak from the steam turbine 20 with serial number 290T435 and equipment code 7FH2. The leak location is within the generator—specifically at the collector end, along the horizontal joint, on the right side—and manifested as bubbles adjacent to three bolts on the horizontal joint. The GE team was contacted, and a crew was dispatched to repair the leak.
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 91afc18bd7b8729e1960d54700908705 | 2 | 2026-03-30 | Mechanical | Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 5 | End Shield, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 STEAM TURBINE (270T435 ¦ SY0073344) __________ 2 1 Summary __________ 2 1.1 Steam Turbine Executive Summary __________ 2 1.2 Work Scope __________ 3 2 Generator __________ 4 2.1 UH CE Assembly _ |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 STEAM TURBINE (270T435 ¦ SY0073344) __________ 2 1 Summary __________ 2 1.1 Steam Turbine Executive Summary __________ 2 1.2 Work Scope __________ 3 2 Generator __________ 4 2.1 UH CE Assembly __________ 4 2.1.1 Collector Housing Cover (CE UH) __________ 4 2.1.2 Hydrogen Seal Casing (CE UH) __________ 5 2.1.3 Inner Oil Deflector (CE UH) __________ 6 2.1.4 Outer Oil Deflector (CE UH) __________ 8 2.1.5 Bearing (UH CE) __________ 9 2.1.6 End Shield (CE
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 9d55a802d232c72f9f9ce14f220caf89 | 13 | 2026-03-30 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 3 | Collector Rings, End Shield, Hydrogen Seal Assembly | Once the End Shield had been inspected and cleaned, reassembly commenced using the appropriate procedures and specified torque values.; Various measures were implemented to ensure the proper sealing of the CE UH end shield.; Finally, to ensure a secure seal, the Pump End Shield Sealant Grooves with Sealant (GN-3210) procedure was followed, and detailed records of the processes were documented using End Shield Sealant Pumping Log (IR5GE1700).; For future work, it is recommended that the bolts connecting the horizontal and vertical faces be installed in a specific sequence, installing the horizontal bolts first, followed by the vertical ones—and that washers be installed within th; CE UH End Shield RS Installed As Found CE IH End Shield Removed 5 CE IH End Shield Removed 1 End Shield Installed 1 Dow Corning Dow Corning Flourosilicone Channel Sealant Pneumatic Pump CE UH End Shield LS Installed As Found CE IH End Shiel |  | Focused Generator Review ¦ Collector Rings ¦ End Shield ¦ Hydrogen Seal Assembly | Part Description: The leak location was along the horizontal joint, on the right side—and manifested as bubbles adjacent to three bolts on the horizontal joint. Once the End Shield had been inspected and cleaned, reassembly commenced using the appropriate procedures and specified torque values. Furthermore, prior to installing each component, the client was notified to perform a "close-out" inspection. Various measures were implemented to ensure the proper sealing of the CE UH end shield. Prior
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 33c8404729f38bae5b5124de97cd344a | 8 | 2026-03-30 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual Part Condition: Good Part Description: The assembly was disassembled, cleaned, inspected, and it was determined to be in condition to return to service. Inner Oil Deflector 3 Inner Oil Deflector Sealant 1 Inner Oil Deflector Sealant 2 Inner Oil Deflector 1 Inner Oil Deflector 4 Inner Oil Deflector 2
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 2ca20fc7f388a3aab1c754c96b4ea3b8 | 24 | 2026-03-30 | Mechanical | Hydrogen Seals | Generator Pressure Test | 2 | End Shield, Generator Pressure Test | With the CE end shields fully assembled Dow corning was pumped into the shields grooves according to GE instructions. |  | Generator Pressure Test ¦ End Shield | Inspection Type: Dimensional Part Description: With the CE end shields fully assembled Dow corning was pumped into the shields grooves according to GE instructions. With the seal oil system reestablished the air test was performed and acceptable values were obtained during the 15hr test period. g Generator Section Generator Air Test Date(m/d/y) Turbine Serial No. Prepared By: Plant: Generator Serial No. Data Prepared By: Unit # Hydrogen System Data: Cubic Feet Cubic Feet Per Day P.S.I. Inches of
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | b1c4a5e9dda0d022b9896fbca8251ed2 | 10 | 2026-03-30 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual Part Condition: Good Part Description: The assembly was disassembled, cleaned, inspected, and it was determined to be in condition to return to service. CE UH Outer Oil Deflector 3 CE UH Outer Oil Deflector 1 CE UH Outer Oil Deflector 5 CE UH Outer Oil Deflector 2 CE UH Outer Oil Deflector 4
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 91a034204c26faac1fe7f1e1a27a0af7 | 7 | 2026-03-30 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | Inspection Type: Visual Part Condition: Good Part Description: The assembly was disassembled, cleaned, inspected, and it was determined to be in condition to return to service. But few parts of the assembly were missing, the plain washer 5/8 PN:N402P17 were not found while working on the unit, the costumer was ok with assembling the unit without that part, but it is recommended to install for the next outage. Hydrogen Seal Casing 5 Hydrogen Seal Casing 2 Hydrogen Seal Casing 4 Hydrogen Seal Casi
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | c118cbebde2d531c5821929cf3c568d0 | 1 | 2026-03-30 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | Lamar ST 20 End Shield Leak H2 Leak CE UH End Shield Repair LAMAR POWER PARTNERS Outage Start Date: |  | Focused Generator Review ¦ End Shield | Lamar ST 20 End Shield Leak H2 Leak CE UH End Shield Repair LAMAR POWER PARTNERS Outage Start Date: 20 Mar 2026 ESN/SY: 270T435 ¦ SY0073344 Generator Field Serial Number: 290T435 Oracle Project ID: A-1989440 ¦ EV-190593 ¦ EVP-559293 Report Issued: 30 Mar 2026 Prepared By Javier Garcia Pinto Field Engineer ( TFA ) (FC) Approved By DANIEL ORTIZ Customer Service Leader (GP) © 2026, GE Vernova. GE Vernova Confidential Information - This document contains GE Vernova proprietary information. It is the
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1989440_EV-190593_EVP-559293.pdf | 270T435 | Steam Turbine | 22be8132d42bec47bdf4619c035be064 | 5 | 2026-03-30 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | Forced Outage Generator End Shield(s) Off |  | Focused Generator Review ¦ End Shield | Outage Type: Forced Outage Generator End Shield(s) Off
UNI036336 | Casco Bay Power Station | Field_Service_Report_ProjectID_EV-188520_EVP-557831.pdf | 270T432 | Steam Turbine | c85eb00e0566870d70a02ae5559c0fc9 | 35 | 2026-01-09 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Crosshead OD NA NA 10.125 10.125 Clearance - - 0.014 0.014 B Bushing ID NA NA 2.752 2.752 TRY BAR Stem OD NA NA 2.749 2.749 Clearance - - 0.003 0.003 Bushing ID NA NA 2.752 2.752 D Stem OD NA NA 2.749 2.749 Clearance - - 0.003 0.003 H Bushi; Allowable from FE Manual 1 1/2 Mils/Ft SV Stem G I K Max Allowable Bowed? Left NA NA NA 0 Right NA NA NA 0 Stem Lgth In. |  | Focused Generator Review ¦ Seal Rings | . Due to the amount of scale build up and material removed to gain proper clearances, it is recommended to replace. 1.1.4 Main Control Valves Below are the recommended parts needed to support this replacement: Balance Chamber: 228C7374P0001 (Qty 1) Bolt Balance Chamber: U810P306L0175 (Qty 8) CV Disc: 203D4524P0001 (Qty 1) Screws, CV Disc: 182A2017P0009 (Qty 4) I would also plan to do this on the Left side valve assembly too. So the above quantities would be doubled. CBM: NA 1.1.4 Main Control Va
UNI036336 | Casco Bay Power Station | Field_Service_Report_ProjectID_EV-188520_EVP-557831.pdf | 270T432 | Steam Turbine | 4847a1766083967b146bcd59f152f1e7 | 29 | 2026-01-09 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . NDT was performed on 12/16/2025. FCSS 600 Galleria Parkway, Suite 1800 Atlanta, GA 30339 Joop Kraijesteijn Digitally signed by Joop Kraijesteijn Date: 2026.01.05 14:02:24 -05'00' _Components Report_Cover Sheet 3A-NDE-0000P_R18_121125 NDT REPORT DATE OF EXAMINATION 12/16/2025 125 Shore Rd, Veazie, ME 04401 3ANGLES JOB NUMBER Member of ASNT * SNT - TC - 1A Certified Technicians PAUT-7313 Job Number: Date: Page: 4 of 5 SCANNING dB: Member of ASNT * SNT - TC - 1A Certified Technicians Performed Ph
UNI036336 | Casco Bay Power Station | Field_Service_Report_ProjectID_EV-188520_EVP-557831.pdf | 270T432 | Steam Turbine | 6c3d95b5ab33d234d919c2ef1acf1adf | 7 | 2026-01-09 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | Inspection Type: Visual, NDT Part Condition: Fair Part Description: During disassembly of the bonnet, it was found six (6) nuts were not able to be fully removed from their respected studs, once loosened up. These six (6) nuts were destructively removed, by the means of cutting/grinding. Once removed, the studs were then cleaned up for NDT inspections. All UT inspections of the studs were found to be in good condition and no issues were noted at this time. During the cleaning phase, the studs th
UNI036336 | Casco Bay Power Station | Field_Service_Report_ProjectID_EV-188520_EVP-557831.pdf | 270T432 | Steam Turbine | b00034d852bfc141fd9dc67438ac8bc5 | 5 | 2026-01-09 | Inspection | Field | Focused Generator Review | 1 | Collector Rings |  |  | Focused Generator Review ¦ Collector Rings | The Steam Turbine Generator (D11/7FH2 LD) at Casco Bay Energy Center was forced out of service due to a Generator field flashover on the collector ring assembly. This took place late Friday (11/28/25) evening. Due to this damage, the site went into a forced outage and this planned valve work was pulled in by a week, as this was planned for a 12/9/25 start. Full outage crews began work on Tuesday (12/2/25), where LOTOs were issued, and a walk down was completed. The outage was executed by GE Vern
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | 344059396d15d83ab743f1a5c8dcb880 | 262 | 2025-10-14 | Inspection | Field, Stator | Focused Generator Review | 4 | Core, Retaining Rings, Step Iron, Sub-slots | Comments Turbine_End_Stator__nd-Step_Iron_General_010-FLAG.J Section Turbine End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Dusting Comments Turbine_End_Stator__nd-Step_Iron_General_011 |  | Focused Generator Review ¦ Core ¦ Retaining Rings ¦ Step Iron ¦ Sub-slots | Comments Turbine_End_Stator__nd-Step_Iron_General_010-FLAG.J Section Turbine End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Dusting Comments Turbine_End_Stator__nd-Step_Iron_General_011-FLAG.J Section Turbine End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Typical Comments Turbine_End_Stator__nd-Step_Iron_General_012.JPG Section Turbine End Sub-Section Stator Core Component Air Gap Locati
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | 5df35f0af1564e7351ce090770f8fe72 | 221 | 2025-10-14 | Inspection | Field, Stator | Focused Generator Review | 4 | Core, Main Lead, Retaining Rings, Step Iron | Sub-Location General Observation Discoloration Comments Collector_End_Stato_ns-Punchings_General_008-FLAG.J Section Collector End Sub-Section Stator Core Component Air Gap Location Stator Vent Sub-Location General Observation Typical Commen |  | Focused Generator Review ¦ Core ¦ Main Lead ¦ Retaining Rings ¦ Step Iron | Sub-Location General Observation Discoloration Comments Collector_End_Stato_ns-Punchings_General_008-FLAG.J Section Collector End Sub-Section Stator Core Component Air Gap Location Stator Vent Sub-Location General Observation Typical Comments Collector_End_Stato__Stator_Vent_General_001.JPG Section Collector End Sub-Section Stator Core Component Air Gap Location Stator Vent Sub-Location General Observation Typical Comments Collector_End_Stato__Stator_Vent_General_002.JPG Section Collector End Su
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | 16381dc18cc603702ce262d13062105b | 252 | 2025-10-14 | Inspection | Stator | Stator Findings Review | 3 | Core, Greasing, Step Iron | Observation Typical Comments Turbine_End_Stator__ns-Punchings_General_001.JPG Section Turbine End Sub-Section Stator Core Component Air Gap Location Laminations- Punchings Sub-Location General Observation Typical Comments Turbine_End_Stator |  | Stator Findings Review ¦ Core ¦ Greasing ¦ Step Iron | Observation Typical Comments Turbine_End_Stator__ns-Punchings_General_001.JPG Section Turbine End Sub-Section Stator Core Component Air Gap Location Laminations- Punchings Sub-Location General Observation Typical Comments Turbine_End_Stator__ns-Punchings_General_002.JPG Section Turbine End Sub-Section Stator Core Component Air Gap Location Laminations- Punchings Sub-Location General Observation Typical Comments Turbine_End_Stator__ns-Punchings_General_003.JPG Section Turbine End Sub-Section Stat
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | 7d2919910531b3cb0896829fea876de0 | 196 | 2025-10-14 | Inspection | Field, Stator | Stator Findings Review | 3 | Greasing, Main Lead, Step Iron | Inspection Results Synopsis -Minor Greasing was noted in the inner basket.; -Migration of a space block was noted near main lead.; - Step iron discoloration noted. |  | Stator Findings Review ¦ Greasing ¦ Main Lead ¦ Step Iron | . Section HGP Stage 3 Component Shroud Block Location Inner Shroud Sub-Location Shroud Body Observation Typical Comments HGP_3_Shroud_Block_Inner_Shroud_Shroud_Body_001.JPG GE Vernova Gas Power Inspection & Life Extension Services Schenectady, NY Abbreviations Abbreviations BI Borescope Inspection RHJ Right Horizontal Joint BS Borescope RS Right Side CDM Combustion Dynamics Monitoring S Compressor Stator Vane Row CI Combustion Inspection S1B Stage 1 Bucket CPM Contractual Performance Manager S2B
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | 659282a5f7cdaf0aa7109444d41a46c7 | 243 | 2025-10-14 | Inspection | Stator | Stator Findings Review | 2 | Core, Greasing | End-Field Sub-Section Field Component Coil Stack Location Coil End Turns Observation Typical Comments Collector_End-Field_Stack_Coil_End_Turns_001.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Locatio |  | Stator Findings Review ¦ Core ¦ Greasing | End-Field Sub-Section Field Component Coil Stack Location Coil End Turns Observation Typical Comments Collector_End-Field_Stack_Coil_End_Turns_001.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Core Compression Nut Sub-Location General Observation Typical Comments Turbine_End_Stator__pression_Nut_General_001.JPG Section Turbine End Sub-Section Stator End Windings Component Stator End Windings Location Core Compression Nut Sub-Location General Obser
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | 1bccb0c8a8645c05573029d87c114f52 | 200 | 2025-10-14 | Inspection | Stator | Focused Generator Review | 1 | High Voltage Bushings |  |  | Focused Generator Review ¦ High Voltage Bushings | . Section Collector End Sub-Section Stator End Windings Component Stator End Location High Voltage Bushing Sub-Location General Comments General_001.JPG Section Collector End Sub-Section Stator End Windings Component Stator End Location High Voltage Bushing Sub-Location General Comments General_002.JPG Section Collector End Sub-Section Stator End Windings Component Stator End Location High Voltage Bushing Sub-Location General Comments General_003.JPG Section Collector End Sub-Section Stator End
UNI036335 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828118_EV-156901_EVP-536585.pdf | 297198 | Gas Turbine | a4fd326e8ce10593b828ca032578ccb1 | 211 | 2025-10-14 | Inspection | Stator | Focused Generator Review | 1 | Core | Collector End Sub-Section Stator End Windings Component Stator End Location Inner Basket Sub-Location General Observation Typical, Dusting Comments Collector_End_Stato_Inner_Basket_General_004.JPG Section Collector End Sub-Section Stator En |  | Focused Generator Review ¦ Core | Collector End Sub-Section Stator End Windings Component Stator End Location Inner Basket Sub-Location General Observation Typical, Dusting Comments Collector_End_Stato_Inner_Basket_General_004.JPG Section Collector End Sub-Section Stator End Windings Component Stator End Location Inner Basket Sub-Location General Observation Typical Comments Collector_End_Stato_Inner_Basket_General_005.JPG Section Collector End Sub-Section Stator End Windings Component Stator End Location Inner Basket Sub-Locati
UNI036334 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828100_EV-156900_EVP-536584.pdf | 297197 | Gas Turbine | b6462157d5fdf651f870f97368f17877 | 26 | 2025-10-14 | Inspection |  | Focused Generator Review | 1 | Water Ingress | - As per ER-20241024-0459 the erosion could be due to online water-wash, water ingress through inlet-duct leaks, inlet fogging, and/ or, water carry-over from poorly conditioned evaporative coolers. | ER-20240709-0330, ER-20241009-1287, ER-20241024-0459 | Focused Generator Review ¦ Water Ingress ¦ ER-20240709-0330 ¦ ER-20241009-1287 | . - S1N inner and outer sidewall cracks noted with some areas of TBC spallation. - S1N leading edge chordal cracks noted. One with larger gap and cooling flow noted. - S1N trailing edge TBC spallation noted with some areas of small crack indications. - S1B leading edge TBC spallation noted. S1B damper pins all present. Some misalignment noted. - S1S TBC spallation noted. - S2N leading edge deposits / cracks noted. - Deposits noted on stage 3 components. - Bent exhaust flex seal noted. - S2N bent
UNI036480 | Moss Landing | Field_Service_Report_ProjectID_A-1777770_EV-145778_EVP-529273.pdf | 297602 | Gas Turbine | a111b921d960ad8b03f9abf18e39f222 | 79 | 2025-06-30 | Inspection | Stator | Focused Generator Review | 1 | Stator Winding | There should be LOTO established since generator heater may be in the “ON” position and stator winding may have ground voltage induced from the generator protection panel (where applicable). |  | Focused Generator Review ¦ Stator Winding | . 8. Personnel should wear the appropriate PPE and clothing. OSHA 29CFR part 1910.146(b) provides additional guidance on compartment entry safety. E. Confined Space Area Pursuant to OSHA 29CFR 1910.146(d)(3), the means, procedures, and practices necessary for safe permit space entry operations for confined spaces must be developed and implemented. If acceptable entry conditions cannot be maintained to protect the entrant from hazards during entry, then entry cannot be authorized. A gas turbine a
UNI036482 | Moss Landing | Field_Service_Report_ProjectID_A-1939570_EV-181176_EVP-552961.pdf | 270T484 | Steam Turbine | 09eeb05086a3881440c1f0c43b08ae61 | 54 | 2025-06-23 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Crosshead OD 10.126 10.126 Clearance 0.009 0.009 B Bushing ID 2.753 2.753 TRY BAR Stem OD 2.741 2.742 Clearance 0.012 0.011 Bushing ID 2.753 2.753 D Stem OD 2.741 2.742 Clearance 0.012 0.011 H Bushing ID TRY BAR Stem OD Clearance Bushing ID |  | Focused Generator Review ¦ Seal Rings | . Particle Main Seat Inspection X Inspection of Equalizer UT Ultrasonic Intercept Valve Disc PT Penetrant Pressure Seal Head X VALVE CLEARANCE LEFT RIGHT Before After Before After Cleaning Cleaning Cleaning Cleaning L Bushing ID 10.135 10.135 TRY BAR. Crosshead OD 10.126 10.126 Clearance 0.009 0.009 B Bushing ID 2.753 2.753 TRY BAR Stem OD 2.741 2.742 Clearance 0.012 0.011 Bushing ID 2.753 2.753 D Stem OD 2.741 2.742 Clearance 0.012 0.011 H Bushing ID TRY BAR Stem OD Clearance Bushing ID J Stem
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 17004b2d01e829e8ead0de96da74e27c | 188 | 2025-05-09 | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 17 | AC Impedance, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Greasing, Hydrogen Seal Assembly, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | The work scope included stator and field visual inspection, electrical testing and MAGIC I inspection including wedge tapping of stator wedges and ElCID integrity of stator iron.; Some of connection ring ties has light/medium greasing and some bar ties has light/medium greasing on CE inner basket no sign of abnormal dusting and greasing of connection ring was found in this outage.; It was found light oil overall around of end windings and on stator wedges which is not desired for generator.; Unit can run with a number of shorted turn as long as those shorted turn equal number of each pole other wise it can cause of vibration because of thermal growth of field body.; Generator work scope are as follows STATOR • MAGIC I inspection • Performed air gap visual inspection of stator • Wedge tightness test for stator wedges • ELCID test for Stator core iron • Stator end winding inspection • Collector ring insp |  | Red Eye Repair ¦ AC Impedance ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding ¦ Field Body | This report is related with major outage of GT2( 338X732) generator, at Fayette station in PA between March 5-16 2025. The work scope included stator and field visual inspection, electrical testing and MAGIC I inspection including wedge tapping of stator wedges and ElCID integrity of stator iron. The other scope is additional block modification of connection ring and three winders mobilized for this modification. Stator end winding has repaired in previous outage. Some of connection ring ties ha
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 973154bccda55189cb7f715e71a77b90 | 188 | 2025-05-09 | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 17 | AC Impedance, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Greasing, Hydrogen Seal Assembly, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | The work scope included stator and field visual inspection, electrical testing and MAGIC I inspection including wedge tapping of stator wedges and ElCID integrity of stator iron.; Some of connection ring ties has light/medium greasing and some bar ties has light/medium greasing on CE inner basket no sign of abnormal dusting and greasing of connection ring was found in this outage.; It was found light oil overall around of end windings and on stator wedges which is not desired for generator.; Unit can run with a number of shorted turn as long as those shorted turn equal number of each pole other wise it can cause of vibration because of thermal growth of field body.; Generator work scope are as follows STATOR • MAGIC I inspection • Performed air gap visual inspection of stator • Wedge tightness test for stator wedges • ELCID test for Stator core iron • Stator end winding inspection • Collector ring insp |  | Red Eye Repair ¦ AC Impedance ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding ¦ Field Body | This report is related with major outage of GT2( 338X732) generator, at Fayette station in PA between March 5-16 2025. The work scope included stator and field visual inspection, electrical testing and MAGIC I inspection including wedge tapping of stator wedges and ElCID integrity of stator iron. The other scope is additional block modification of connection ring and three winders mobilized for this modification. Stator end winding has repaired in previous outage. Some of connection ring ties ha
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 43ad81d0d1ae10292d4a4f012f824933 | 251 | 2025-05-09 | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 17 | AC Impedance, Belly Bands, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Greasing, Hydrogen Seal Assembly, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | The work scope included stator and field visual inspection, electrical testing, wedge tapping of stator wedges, Elcid integrity of stator iron and belly band / knife check of core iron tightness.; Stator end winding has repaired in previous outage and no sign of abnormal dusting and greasing of connection ring was found in this outage.; Unit can run with a number of shorted turn as long as those shorted turn equal number of each pole other wise it can cause of vibration because of thermal growth of field body.; Generator work scope are as follows STATOR • Performed visual inspection of stator end windings and core • Wedge tightness test for stator wedges • Belly band and knife check ID and OD • Visual inspection of gas and air HV bushing check • C |  | Red Eye Repair ¦ AC Impedance ¦ Belly Bands ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding | This report is related with major outage of GT1( 338X731) generator, at Fayette station in PA between March 5-16 2025. The work scope included stator and field visual inspection, electrical testing, wedge tapping of stator wedges, Elcid integrity of stator iron and belly band / knife check of core iron tightness. The other scope is additional block modification of connection ring and three winders mobilized for this modification. Stator end winding has repaired in previous outage and no sign of
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | cf5489c455b23b158b358f3a4a6e31f5 | 251 | 2025-05-09 | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 17 | AC Impedance, Belly Bands, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Greasing, Hydrogen Seal Assembly, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | The work scope included stator and field visual inspection, electrical testing, wedge tapping of stator wedges, Elcid integrity of stator iron and belly band / knife check of core iron tightness.; Stator end winding has repaired in previous outage and no sign of abnormal dusting and greasing of connection ring was found in this outage.; Unit can run with a number of shorted turn as long as those shorted turn equal number of each pole other wise it can cause of vibration because of thermal growth of field body.; Generator work scope are as follows STATOR • Performed visual inspection of stator end windings and core • Wedge tightness test for stator wedges • Belly band and knife check ID and OD • Visual inspection of gas and air HV bushing check • C |  | Red Eye Repair ¦ AC Impedance ¦ Belly Bands ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding | This report is related with major outage of GT1( 338X731) generator, at Fayette station in PA between March 5-16 2025. The work scope included stator and field visual inspection, electrical testing, wedge tapping of stator wedges, Elcid integrity of stator iron and belly band / knife check of core iron tightness. The other scope is additional block modification of connection ring and three winders mobilized for this modification. Stator end winding has repaired in previous outage and no sign of
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 7061fdd474076e37c707fd0ee58272ad | 5 | 2025-05-09 | Electrical | Field, Stator | Polarization Index; DC Leakage | 15 | Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, High Voltage Bushings, Loose End-winding Blocking, MAGIC Inspection, Polarization Index, Retaining Rings, Stator Winding, Sub-slots, Wedge Tightness Test, Wedges | Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility GENERATOR (338X732 ¦ SY0071958) __________ 178 1 Summary __________ 178 1.1 Generator Executive Summary __________ 178 2 Tec; Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.1.8 Stator Space Blocks __________ 194 3.1.9 RTD Wiring/Assembly __________ 195 3.1.10 High Voltage Bushing Box __________; Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.3.2 Field Body __________ 228 3.3.3 Field Wedges __________ 229 3.3.4 Balance Weights __________ 230 3.3.5 Vent Holes ____ |  | Polarization Index; DC Leakage ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding ¦ Field Body ¦ Focused Generator Inspection | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.3 Regulator Calibration __________ 120 3.3.1 SRV Control Valve __________ 120 3.3.2 PM1 Gas Control Valve __________ 122 3.3.3 PM2 Gas Control Valve __________ 124 3.3.4 PM3 Gas Control Valve __________ 126 3.3.5 New Component __________ 128 3.3.6 IGV Calibration __________ 130 3.4 Additional
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | c2f8117c21f8fcd2072cfb9f39ae8025 | 5 | 2025-05-09 | Electrical | Field, Stator | Polarization Index; DC Leakage | 15 | Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, High Voltage Bushings, Loose End-winding Blocking, MAGIC Inspection, Polarization Index, Retaining Rings, Stator Winding, Sub-slots, Wedge Tightness Test, Wedges | Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility GENERATOR (338X732 ¦ SY0071958) __________ 178 1 Summary __________ 178 1.1 Generator Executive Summary __________ 178 2 Tec; Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.1.8 Stator Space Blocks __________ 194 3.1.9 RTD Wiring/Assembly __________ 195 3.1.10 High Voltage Bushing Box __________; Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.3.2 Field Body __________ 228 3.3.3 Field Wedges __________ 229 3.3.4 Balance Weights __________ 230 3.3.5 Vent Holes ____ |  | Polarization Index; DC Leakage ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding ¦ Field Body ¦ Focused Generator Inspection | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 298159, Major Inspection (Robotic) - 338X732 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.3 Regulator Calibration __________ 120 3.3.1 SRV Control Valve __________ 120 3.3.2 PM1 Gas Control Valve __________ 122 3.3.3 PM2 Gas Control Valve __________ 124 3.3.4 PM3 Gas Control Valve __________ 126 3.3.5 New Component __________ 128 3.3.6 IGV Calibration __________ 130 3.4 Additional
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | c71e27df41675c28648f94cd5e338d16 | 6 | 2025-05-09 | Electrical | Field, Stator | Polarization Index; DC Leakage | 15 | AC Impedance, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, High Voltage Bushings, Loose End-winding Blocking, Polarization Index, Retaining Rings, Stator Winding, Sub-slots, Wedge Tightness Test, Wedges | Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 6.1 Generator __________ 183 7 Appendix __________ 222 7.1 Attachments __________ 222 GENERATOR (338X731 ¦ SY0071959) ____; Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.1.5 Stator Connection Ring Blockings and Ties __________ 252 3.1.6 Stator Axial Support Hardware __________ 253 3.1.7 St; Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.3 Field Visual Inspection __________ 293 3.3.1 Field Visual Inspection and Electrical testing __________ 293 3.3.2 Field; Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.4.10 Bore plug test __________ 314 3.5 Field Testing __________ 316 3.5.1 Winding Copper Resistance __________ 316 3.5.2 |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding ¦ Field Body | . Startup and Auto Tune screen replaced. __________ 165 3.4.2 Additional Scope/ Non Standard __________ 166 4 Instrumentation __________ 168 4.1 Control Devices Turbine Vibration Monitoring Equipment GT1 __________ 168 5 Electrical System __________ 173 5.1 Excitation System __________ 173 6 Sub Reports __________ 183 GEGEGE GE Vernova Confidential and Proprietary Information. Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 298158, Ma
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 2edc415f928769dad10b2c9529be3f4e | 6 | 2025-05-09 | Electrical | Field, Stator | Polarization Index; DC Leakage | 15 | AC Impedance, Collector Rings, Core, DC Leakage, End-winding, Field Body, Focused Generator Inspection, High Voltage Bushings, Loose End-winding Blocking, Polarization Index, Retaining Rings, Stator Winding, Sub-slots, Wedge Tightness Test, Wedges | Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 6.1 Generator __________ 183 7 Appendix __________ 222 7.1 Attachments __________ 222 GENERATOR (338X731 ¦ SY0071959) ____; Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.1.5 Stator Connection Ring Blockings and Ties __________ 252 3.1.6 Stator Axial Support Hardware __________ 253 3.1.7 St; Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.3 Field Visual Inspection __________ 293 3.3.1 Field Visual Inspection and Electrical testing __________ 293 3.3.2 Field; Major Inspection (MI) - 298158, Major Inspection (Rotor Out) - 338X731 DYNEGY FAYETTE II, LLC Fayette Energy Facility 3.4.10 Bore plug test __________ 314 3.5 Field Testing __________ 316 3.5.1 Winding Copper Resistance __________ 316 3.5.2 |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ End-winding ¦ Field Body | . Startup and Auto Tune screen replaced. __________ 165 3.4.2 Additional Scope/ Non Standard __________ 166 4 Instrumentation __________ 168 4.1 Control Devices Turbine Vibration Monitoring Equipment GT1 __________ 168 5 Electrical System __________ 173 5.1 Excitation System __________ 173 6 Sub Reports __________ 183 GEGEGE GE Vernova Confidential and Proprietary Information. Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 298158, Ma
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | ba6926fd828d91ed96d62fb759abae32 | 207 | 2025-05-09 | Inspection | Field, Stator | Wedge Tightness Test | 8 | Focused Generator Inspection, Gooseneck, Greasing, MAGIC Inspection, Main Lead, Step Iron, Wedge Tightness Test, Wedges | Schmeltzer Generator Specialist Hakan Citlak Location Comments Photo Identification Slot 22 View of oil on stator packages / wedge ~ 15” from CE RR Image 01 191° / Slot 22 View of scratch on field / oil on stator packages ~ 47” from CE RR I |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Gooseneck ¦ Greasing ¦ MAGIC Inspection ¦ Main Lead ¦ Step Iron | Inspection Type: Visual Part Condition: Good Part Description: Magic I robot has completed visual inspection and performed stator wedge tightness and ELCID test. Inspection & Life Extension Services Magic Photo I.D.Worksheet Job # N/A 1 River Road, Bldg. 55 Rm. 263 Generator # 338X732 Schenectady, New York 12345 Date 3-13-25 Operator S. Schmeltzer Generator Specialist Hakan Citlak Location Comments Photo Identification Slot 22 View of oil on stator packages / wedge ~ 15” from CE RR Image 01 191°
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 63d2b21c811a18d175218b49a984bcfb | 207 | 2025-05-09 | Inspection | Field, Stator | Wedge Tightness Test | 8 | Focused Generator Inspection, Gooseneck, Greasing, MAGIC Inspection, Main Lead, Step Iron, Wedge Tightness Test, Wedges | Schmeltzer Generator Specialist Hakan Citlak Location Comments Photo Identification Slot 22 View of oil on stator packages / wedge ~ 15” from CE RR Image 01 191° / Slot 22 View of scratch on field / oil on stator packages ~ 47” from CE RR I |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Gooseneck ¦ Greasing ¦ MAGIC Inspection ¦ Main Lead ¦ Step Iron | Inspection Type: Visual Part Condition: Good Part Description: Magic I robot has completed visual inspection and performed stator wedge tightness and ELCID test. Inspection & Life Extension Services Magic Photo I.D.Worksheet Job # N/A 1 River Road, Bldg. 55 Rm. 263 Generator # 338X732 Schenectady, New York 12345 Date 3-13-25 Operator S. Schmeltzer Generator Specialist Hakan Citlak Location Comments Photo Identification Slot 22 View of oil on stator packages / wedge ~ 15” from CE RR Image 01 191°
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | a435fb8654addcbb85fe5e29f3f75895 | 209 | 2025-05-09 | Inspection | Field, Stator | MAGIC Inspection | 7 | Gooseneck, Greasing, High Voltage Bushings, MAGIC Inspection, Main Lead, Pole Jumper, Sub-slots | Schmeltzer Generator Specialist Hakan Citlak 90 deg View of turns and insulation Image 43 90 deg View of pole-to-pole jumper Image 44 90 deg 2nd view of pole-to-pole jumper Image 45 90 deg View of inside turns and insulation Image 46 90 deg |  | MAGIC Inspection ¦ Gooseneck ¦ Greasing ¦ High Voltage Bushings ¦ Main Lead ¦ Pole Jumper | . 55 Rm. 263 Generator # 338X732 Schenectady, New York 12345 Date 3-13-25 Operator S. Schmeltzer Generator Specialist Hakan Citlak 90 deg View of turns and insulation Image 43 90 deg View of pole-to-pole jumper Image 44 90 deg 2nd view of pole-to-pole jumper Image 45 90 deg View of inside turns and insulation Image 46 90 deg View of inside turns and insulation (loose tape) Image 47 90 deg Insulation migration (front side) Image 48 90 - 180 deg Typical view of blocking Image 49 180 deg Overview o
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 18fa6c7f2a4cfa53869d9c86ab450672 | 193 | 2025-05-09 | Inspection | Stator | Wedge Tightness Test | 7 | Focused Generator Inspection, Greasing, MAGIC Inspection, Stator Winding, Step Iron, Wedge Tightness Test, Wedges | Stator winding air gap inspection was visual inspected by Magic I robot.; Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration.; Some of TE end wedges have light, medium and high greasing.; Clean slot exit and end wedges greasing on major outage.; Stator air gap TE slot 24-26 step iron greasing TE step iron greasing TE slot 17-18 oil & greasing |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Stator Winding ¦ Step Iron | Inspection Type: Visual Part Condition: Good Part Description: Stator winding air gap inspection was visual inspected by Magic I robot. Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration. Some of TE end wedges have light, medium and high greasing. Recommendation Status: Should be planned for next Outage Recommendation Description: Clean slot exit and end wedges greasing on major outage. Stator air gap TE slot 24-26 step iron greasing TE step iron greasing TE s
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | bc33f3c0bf2f6541a52174d9c78b04eb | 209 | 2025-05-09 | Inspection | Field, Stator | MAGIC Inspection | 7 | Gooseneck, Greasing, High Voltage Bushings, MAGIC Inspection, Main Lead, Pole Jumper, Sub-slots | Schmeltzer Generator Specialist Hakan Citlak 90 deg View of turns and insulation Image 43 90 deg View of pole-to-pole jumper Image 44 90 deg 2nd view of pole-to-pole jumper Image 45 90 deg View of inside turns and insulation Image 46 90 deg |  | MAGIC Inspection ¦ Gooseneck ¦ Greasing ¦ High Voltage Bushings ¦ Main Lead ¦ Pole Jumper | . 55 Rm. 263 Generator # 338X732 Schenectady, New York 12345 Date 3-13-25 Operator S. Schmeltzer Generator Specialist Hakan Citlak 90 deg View of turns and insulation Image 43 90 deg View of pole-to-pole jumper Image 44 90 deg 2nd view of pole-to-pole jumper Image 45 90 deg View of inside turns and insulation Image 46 90 deg View of inside turns and insulation (loose tape) Image 47 90 deg Insulation migration (front side) Image 48 90 - 180 deg Typical view of blocking Image 49 180 deg Overview o
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 249e86b10cccbdf738cd318eb9966086 | 193 | 2025-05-09 | Inspection | Stator | Wedge Tightness Test | 7 | Focused Generator Inspection, Greasing, MAGIC Inspection, Stator Winding, Step Iron, Wedge Tightness Test, Wedges | Stator winding air gap inspection was visual inspected by Magic I robot.; Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration.; Some of TE end wedges have light, medium and high greasing.; Clean slot exit and end wedges greasing on major outage.; Stator air gap TE slot 24-26 step iron greasing TE step iron greasing TE slot 17-18 oil & greasing |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Stator Winding ¦ Step Iron | Inspection Type: Visual Part Condition: Good Part Description: Stator winding air gap inspection was visual inspected by Magic I robot. Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration. Some of TE end wedges have light, medium and high greasing. Recommendation Status: Should be planned for next Outage Recommendation Description: Clean slot exit and end wedges greasing on major outage. Stator air gap TE slot 24-26 step iron greasing TE step iron greasing TE s
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | b8b044a8733f0039fbb26da5b0a8070d | 256 | 2025-05-09 | Inspection | Stator | Wedge Tightness Test | 6 | End-winding, Focused Generator Inspection, Greasing, Stator Winding, Wedge Tightness Test, Wedges | Stator winding air gap inspection was found satisfactory.; Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration.; Some of CE/TE end wedges have light, medium and high greasing.; S=Satisfactory, LD/G=Light Dusting/Greasing, MD/G=Moderate Dusting/Greasing, HD/G=Heavy Dusting/Greasin Stator end winding dusting 3/9/2025 338X731 Prepared by Hakan Citlak I01-103908 Slot exit dusting Date(m/d/y) 3/9/2025 Generator Serial |  | Wedge Tightness Test ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ Stator Winding ¦ Wedges | Inspection Type: Visual Part Condition: Good Part Description: Stator winding air gap inspection was found satisfactory. Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration. Some of CE/TE end wedges have light, medium and high greasing. Winder cleaned up those areas with denatured alcohol with clean rags and bottle brushes. IMG 0439 IMG 0475 IMG 0476 TE slot exit ~ 3 clcok TE slot exit ~ 10 clock TE bar slot exit ~ 12 clock GE Date(m/d/y) Gen S/N FSR No. 7FH2 M
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 2ed73a8bdd639bb3f39f0bf40047bef4 | 193 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 6 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | CE Closeout (1) CE Closeout (2) CE Disassembly (1) CE Closeout (3) CE Closeout (5) CE Closeout (4) CE Disassembly (5) Skid pan (1) CE Closeout (6) CE Disassembly (4) Skid pan (3) CE Disassembly (3) CE Disassembly (2) Skid pan (2) Skid pan p |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual, NDT, Dimensional Part Condition: Fair Recommendation Description: The collector end of the generator was completely disassembled for the removal of the field. The T4 bearing was replaced with a newly refurbished bearing. New hydrogen seals, inner oil deflector, mid oil deflector, and outer oil deflector installed. Data sheets are attached below. See photos below for installation and applications of sealants. The turbine end of the generator was completely disassembled fo
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 1d4dd45c420cbd080915724d40d1466a | 256 | 2025-05-09 | Inspection | Stator | Wedge Tightness Test | 6 | End-winding, Focused Generator Inspection, Greasing, Stator Winding, Wedge Tightness Test, Wedges | Stator winding air gap inspection was found satisfactory.; Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration.; Some of CE/TE end wedges have light, medium and high greasing.; S=Satisfactory, LD/G=Light Dusting/Greasing, MD/G=Moderate Dusting/Greasing, HD/G=Heavy Dusting/Greasin Stator end winding dusting 3/9/2025 338X731 Prepared by Hakan Citlak I01-103908 Slot exit dusting Date(m/d/y) 3/9/2025 Generator Serial |  | Wedge Tightness Test ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ Stator Winding ¦ Wedges | Inspection Type: Visual Part Condition: Good Part Description: Stator winding air gap inspection was found satisfactory. Stator wedge tightness has no loose and hallow wedges which can cause to bar vibration. Some of CE/TE end wedges have light, medium and high greasing. Winder cleaned up those areas with denatured alcohol with clean rags and bottle brushes. IMG 0439 IMG 0475 IMG 0476 TE slot exit ~ 3 clcok TE slot exit ~ 10 clock TE bar slot exit ~ 12 clock GE Date(m/d/y) Gen S/N FSR No. 7FH2 M
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 5ccf03665c0ea2c68a91fd4ec60d3b93 | 193 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 6 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | CE Closeout (1) CE Closeout (2) CE Disassembly (1) CE Closeout (3) CE Closeout (5) CE Closeout (4) CE Disassembly (5) Skid pan (1) CE Closeout (6) CE Disassembly (4) Skid pan (3) CE Disassembly (3) CE Disassembly (2) Skid pan (2) Skid pan p |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual, NDT, Dimensional Part Condition: Fair Recommendation Description: The collector end of the generator was completely disassembled for the removal of the field. The T4 bearing was replaced with a newly refurbished bearing. New hydrogen seals, inner oil deflector, mid oil deflector, and outer oil deflector installed. Data sheets are attached below. See photos below for installation and applications of sealants. The turbine end of the generator was completely disassembled fo
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | ef382223137640cfa8eb52cedc6b9143 | 146 | 2025-05-09 | Inspection | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Fan Blades, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | The collector end of the generator was completely disassembled for a magic inspection.; The magic inspection was conducted on the field.; Closeout (3) Closeout (5) Closeout (2) Closeout (6) Closeout (7) Closeout (1) Closeout (9) Closeout (8) Closeout (10) Closeout (11) Closeout (15) Closeout (13) Closeout (4) Closeout (12) Closeout (18) Closeout (17) Closeout (14) GAS CE (1) |  | Oil Deflector Alignment ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | Inspection Type: Visual, Dimensional, NDT Part Condition: Fair Part Description: The collector end of the generator was completely disassembled for a magic inspection. The T4 bearing was replaced with a newly refurbished bearing. New hydrogen seals, inner oil deflector, mid oil deflector, and outer oil deflector installed. Data sheets are attached below. See photos below for installation and applications of sealants. The turbine end of the generator was completely disassembled for the removal of
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 6d3439fa7397ad12ebd404dd15aefb37 | 182 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.061 NA 0.052 0.061 0.056 0.048 Inner Oil Deflector K 0.013 NA 0.011 0.010 0.0; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Shaft Grounding Brushes A NA NA NA NA Outer Oil Deflector B 0.008 0.020 0.010 0.010 0.015 0 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 298159 Prepared by Generator Serial No. 338X731 ERP Project ID Units recorded in Data set Notes: 1) Coupling should be the the cold setting when reading is taken. The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fa
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 0a2984cab8b085cc89f7327c99ed144f | 182 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.061 NA 0.052 0.061 0.056 0.048 Inner Oil Deflector K 0.013 NA 0.011 0.010 0.0; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Shaft Grounding Brushes A NA NA NA NA Outer Oil Deflector B 0.008 0.020 0.010 0.010 0.015 0 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 298159 Prepared by Generator Serial No. 338X731 ERP Project ID Units recorded in Data set Notes: 1) Coupling should be the the cold setting when reading is taken. The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fa
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | f1e7308d5be4b92a57390094f453c4fc | 236 | 2025-05-09 | Inspection | Stator | Wedge Tightness Test | 5 | Focused Generator Inspection, MAGIC Inspection, Wedge Looseness, Wedge Tightness Test, Wedges | Wedge tightness test was performed by Magic I robot and map is attached.; No loose and hallow wedges found ? ? ? Customer:; Fayette / GT-2 Number of Wedges: |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Wedge Looseness ¦ Wedges | Part Condition: Good Part Description: Wedge tightness test was performed by Magic I robot and map is attached. No loose and hallow wedges found ? ? ? Customer: Vistra Number of Slots: 60 Hollow Wedge Lowest Value 34 Site/Unit: Fayette / GT-2 Number of Wedges: 19 Tight Wedge Lowest Value: 67 Generator #: 338X732 Test Specialist: S
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633218_EV-106619_EVP-502992.pdf | 298159, 338X732 | Gas Turbine, Generator | 62ce1072ae1b41c4d9e3a80b5f716406 | 178 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.057 0.0540 0.050 0.058 0.058 0.051 Inner Oil Deflector K 0.005 0.007 0.005 0.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.006 0.006 0.006 0.006 0.010 0.008 Hydrogen Seal Casing C 0.181 NA 0 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . GE Proprietary – Non-Public Not to be distributed or reproduced to third parties without prior GE approval. D3165012 Sheet: (a) Rev 3.6 - 02-JUN-2022 Seal Oil System Hydrogen Seals and Springs Date(m/d/y) 3/9/2025 Turbine Serial No. 298159 Prepared by Generator Serial No. 338X731 Project ID Equip Code: Units recorded in Data set SEAL THICKNESS 'A' MEASUREMENTS (in.) TURBINE END COLL. END POSITION AIR HYD AIR HYD 1 1.247 1.249 1.247 1.249 2 1.246 1.248 1.247 1.250 3 1.246 1.248 1.247 1.250 4 1.
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 9313678e7c3afb777541cd9c71fdfd71 | 319 | 2025-05-09 | Electrical |  | DLRO; Winding Resistance | 5 | 10-minute 5000 VDC Megger PI, 10-minute Megger, DLRO, Polarization Index, Winding Resistance | After terminal stud installation, performed field winding resistance test and 10 minute megger and PI test.; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) INSULATION RESISTANC AT 500V (TM4030) 22.0 Time (min) R (megohms) 73.0% 0.50 159 1 178 FIELD WINDING RESISTANCE (TM4010) All Units 2 188 0.1372 3 210 21.0 0.1393 4 212 Near CE 5 244 Centerl; CAL Date 102229482 01/15/2025 203530 07/25/2024 2254313 10/08/2024 2989143 2/6/2025 Reading Checks per TM4010 Previous Test Correct to 25 ºC Prior Test @25 ºC Historical Resistance Readings Instrument Description 7FH2 Number of Starts Facto | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ 10-minute 5000 VDC Megger PI ¦ 10-minute Megger ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | Inspection Type: Visual Part Condition: Good Part Description: in this outage, Terminal stud were replaced with O ring design. 0 and 180 pole terminal studs were removed without any issue. Old terminal stud went to vendor to fabricate the new one. When received new terminal studs and field on turning gear, new terminal stud installed and performed leak test. The new terminal stud number is 132T5693G0016. After terminal stud installation, performed field winding resistance test and 10 minute megg
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | cf604295a280b45b1a13b4c5529bcf62 | 227 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.062 0.0510 0.065 0.055 0.062 0.046 Inner Oil Deflector K 0.004 0.005 0.005 0.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.043 0.042 0.057 0.050 0.055 0.041 Inner Oil Deflector K 0.011 NA 0.010 0.013 ; 0.036 - Exciter House Blades 0.038 - Gen Fan Blades D316319 Sheet: |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.062 0.0510 0.065 0.055 0.062 0.046 Inner Oil Deflector K 0.004 0.005 0.005 0.006 0.011 0.005 Middle Oil Deflector L 0.011 NA 0.012 0.012 0.011 0.0120 H
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | cc781c17b86ee8662d42eef45e1c2a61 | 230 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.008 0.005 0.007 0.008 0.012 0.009 Hydrogen Seal Casing C 0.186 NA 0; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Shaft Grounding Brushes A NA NA NA NA Outer Oil Deflector B 0.008 0.011 0.014 0.010 0.021 0 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 338X731 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.008 0.005 0.007 0.008 0.012 0.009 Hydrogen Seal Casing C 0.186 NA 0.181 0.186 0.186 0.186 Middle Oil Deflector D 0.015 NA 0.021 0.024 0
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 990228517156868bc4b244afefdbc6f5 | 319 | 2025-05-09 | Electrical |  | DLRO; Winding Resistance | 5 | 10-minute 5000 VDC Megger PI, 10-minute Megger, DLRO, Polarization Index, Winding Resistance | After terminal stud installation, performed field winding resistance test and 10 minute megger and PI test.; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) INSULATION RESISTANC AT 500V (TM4030) 22.0 Time (min) R (megohms) 73.0% 0.50 159 1 178 FIELD WINDING RESISTANCE (TM4010) All Units 2 188 0.1372 3 210 21.0 0.1393 4 212 Near CE 5 244 Centerl; CAL Date 102229482 01/15/2025 203530 07/25/2024 2254313 10/08/2024 2989143 2/6/2025 Reading Checks per TM4010 Previous Test Correct to 25 ºC Prior Test @25 ºC Historical Resistance Readings Instrument Description 7FH2 Number of Starts Facto | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ 10-minute 5000 VDC Megger PI ¦ 10-minute Megger ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | Inspection Type: Visual Part Condition: Good Part Description: in this outage, Terminal stud were replaced with O ring design. 0 and 180 pole terminal studs were removed without any issue. Old terminal stud went to vendor to fabricate the new one. When received new terminal studs and field on turning gear, new terminal stud installed and performed leak test. The new terminal stud number is 132T5693G0016. After terminal stud installation, performed field winding resistance test and 10 minute megg
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | bc0f172c2f7dd332577190858551439b | 227 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.062 0.0510 0.065 0.055 0.062 0.046 Inner Oil Deflector K 0.004 0.005 0.005 0.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.043 0.042 0.057 0.050 0.055 0.041 Inner Oil Deflector K 0.011 NA 0.010 0.013 ; 0.036 - Exciter House Blades 0.038 - Gen Fan Blades D316319 Sheet: |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.062 0.0510 0.065 0.055 0.062 0.046 Inner Oil Deflector K 0.004 0.005 0.005 0.006 0.011 0.005 Middle Oil Deflector L 0.011 NA 0.012 0.012 0.011 0.0120 H
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | 3928c00d7138e1c2212b264446a1b041 | 230 | 2025-05-09 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.008 0.005 0.007 0.008 0.012 0.009 Hydrogen Seal Casing C 0.186 NA 0; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Shaft Grounding Brushes A NA NA NA NA Outer Oil Deflector B 0.008 0.011 0.014 0.010 0.021 0 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 338X731 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.008 0.005 0.007 0.008 0.012 0.009 Hydrogen Seal Casing C 0.186 NA 0.181 0.186 0.186 0.186 Middle Oil Deflector D 0.015 NA 0.021 0.024 0
UNI035727, UNI035728 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1633216_EV-106618_EVP-502991.pdf | 298158, 338X731 | Gas Turbine, Generator | ffc2e88b08f2fd425ef963658bff26b1 | 326 | 2025-05-09 | Electrical |  | DLRO; Winding Resistance | 4 | DLRO, Polarization Index, Winding Resistance, Winding resistance DLRO | The field winding resistance was measured using a DLRO and corrected to 25 degrees Celsius for comparison .; The winding resistance was found to be within tolerance when compared to a factory resistance value.; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.11 1.74 5.81 20.31 3.54 5.74 30.30 5.24 5.78 40.39 6.95 5.81 50.22 8.61 5.83 60.25 10.25 5.88 70.10 11.77 5.96 80.70 13.32 6.06 90.10 14.64 6.15 100.60 16.06 6.26 110.60 17.32 6.39 120.2; CAL Date 102229482 01/15/2025 203530 07/25/2024 2254313 10/08/2024 2989143 2/6/2025 Reading Checks per TM4010 Previous Test Correct to 25 ºC Prior Test @25 ºC Historical Resistance Readings Instrument Description 7FH2 Number of Starts Facto | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ Winding resistance DLRO ¦ TM4010 ¦ TM4020 | Part Condition: Good Part Description: The field winding resistance was measured using a DLRO and corrected to 25 degrees Celsius for comparison . The winding resistance was found to be within tolerance when compared to a factory resistance value. GT1 Field Measurements Date Turbine No.: 298158 Prepared by: Equipment Generator No.: 338X731 Project ID: OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.11 1.74 5.81 20.31 3.54 5.74 30.30 5.24 5.78 40.39 6.95 5.81 50.22 8.61 5.83 60.25 10.25 5.8
UNI026368 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1791834_EV-149158_EVP-531208.pdf | 296302 | Gas Turbine | a0799717b1194a7b400c48f9304354c1 | 20 | 2025-05-06 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . GE Vernova Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property of GE and TIL Applicability Table: TIL Title Inspected (YES/NO) TIL-1582-R2 F and H Class Lift Oil Hose Inspection and Replacement YES (Inspection Only) *ETC 257 BORESCOPE INSPECTION REVISION FOR 7FA TRANSITION PIECES YES TIL-1724-R1 Inspection and Cleaning of Quaternary Fuel Annulus in Forward Combust
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1881852_EV-168186_EVP-545083.pdf | 270T435 | Steam Turbine | 4ccceedf1985c834c167b35c1fad4aa6 | 10 | 2025-04-08 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test |  |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . Removal of the L-1 TE, L-2 GE and TE buckets was performed at which time MPI Mag Particle Inspections was performed in the areas of the indications on the bucket wheels. LES team submitted data as needed be the engineering team and excavation of the indications was initiated. The OSS team utilized small burr bits to perform the removal of material at a minimal rate with constant MPI’s performed during the process to monitor excavation of indications. This evolution was performed on L-1 TE buck
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1881852_EV-168186_EVP-545083.pdf | 270T435 | Steam Turbine | 755d4bdaf40dd0754be0e3d3043da074 | 12 | 2025-04-08 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test |  |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . The bearing cover was installed with sealant and all bolting torqued. An FME closeout was performed of the mid standard verifying no foreign material in the cavity and no FME devices remaining. The mid standard cover was installed with sealant, bolting installed and torqued. T-4 bearing standard was inspected for FME closeout and prepared to close. UH oil deflector was installed with sealant, alignment set and recorded. UH bearing was installed with bolting torqued, bearing ring was installed
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1881852_EV-168186_EVP-545083.pdf | 270T435 | Steam Turbine | a77b3fa428bad924518ae458f4d02b3c | 67 | 2025-04-08 | Inspection | Field | Focused Generator Review | 1 | Collector Rings | During this outage the customer requested the team to realign the generator collector brushes due to the aft brushes not having 100% contact with the collector rings.; Doing this moved the brushes forward to have full contact with the collector rings. |  | Focused Generator Review ¦ Collector Rings | . Face readings in inches. Data: Position Top Left Bottom Right Rim 0.0 -1.0 -4.0 -3.0 0.0 Face 0º .9350" .9350" .9350" .9360" 0.0 Face 90º .9350" .9350" .9340" .9350" 0.0 Face 180º .9370" .9360" .9380" .9370" Face 270º .9390" .9380" .9380" .9390" -1.0 -0.5 0.3 -3.0 Average .9365" .9360" .9363" .9368" Relative 0.0 -0.5 -0.2 0.3 -0.2 Check Face Rim Top + Bottom= 0 -4 -4.0 Right + Left = 0 -4 Difference= 0 0 Face with Indicator or Parrallels (I or P): P 1nd Set 2rd Set 270T435 FieldCore 36 TE Dial
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1881852_EV-168186_EVP-545083.pdf | 270T435 | Steam Turbine | 72ac099e50c3a6f5694e5da1416aa2f3 | 13 | 2025-04-08 | Inspection | Field | Focused Generator Review | 1 | Collector Rings | Visual inspection found that the axial location of the brushes was approximately .375 out of location to the collector rings. |  | Focused Generator Review ¦ Collector Rings | . Contact checks of the CVs was performed with the LS valve having acceptable result but the RS unsatisfactory. The LS valve was prepared for assembly with closeouts of the steam lines and leak-off lines done with Vistra representative present. LS SV was installed after which CV upper head assembly installed with gaskets verified on both. The SV pressure seal head threaded ring pull down bolts were torqued per the drawing specifications and lock nuts set. The steam strainer was installed after w
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 60cef93e2b60e3f8e3c710fef1dd86bd | 97 | 2024-12-20 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 6 | Collector Rings, End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Air Shroud Installed As Found Brush Rigging As Found Collector End Bearing Lower Half Conditon As Found Collector End Bearings As Found Collector End Lower Half Bearing condition As Found Excitor Fan Blade As Found Exciter Fan Blades As Fou |  | Oil Deflector Alignment ¦ Collector Rings ¦ End Shield ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . Air Shroud Installed As Found Brush Rigging As Found Collector End Bearing Lower Half Conditon As Found Collector End Bearings As Found Collector End Lower Half Bearing condition As Found Excitor Fan Blade As Found Exciter Fan Blades As Found Exciter Fan Blades And Shroud As found Excited Base Condition As Found Removed Turning Gear As Found Turbine End Field Journal Condition (2) As Found Turbine End Field Journal Condition As Found Turbine End Upper Half Bearing Axial Alignment Of Brush Rigg
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | bf1b25c8d8c395612821c8434239b617 | 194 | 2024-12-20 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | The collector brushes should ride fully on the collector rings when the unit is at running tempeature |  | Oil Deflector Alignment ¦ Collector Rings ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | . By design it should be 0.010 inches [0.25 mm]. If it is less than 0.005 inches[0.13 mm] contact Product Service for disposition. GE Proprietary – Non-Public Not to be distributed or reproduced to third parties without prior GE approval. D3165012 Sheet: (b) Rev 3.6 - 02-JUN-2022 Seal Oil System Hydrogen Seals and Springs Date(m/d/y) Turbine Serial No. Prepared by Generator Serial No. Project ID Units recorded in Equip Code: Data set Seal Type / System Type / No. of Poles Nominal Shaft Dia. (in.
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 7eca220789c33b81f1130d802e943c5f | 197 | 2024-12-20 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J 0.056 0.014 0.054 0.049 0.072 0.063 Inner Oil Deflector; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Location 1 2 3 4 5 6 Cold Coupling Postion Z N/A N/A N/A N/A N/A N/A Shaft Grounding Brushes A N/A N/A N/A N/A N/A N/A Outer; Fan blades:; Slight foreign object damage was noted on select fan blades. |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J 0.056 0.014 0.054 0.049 0.072 0.063 Inner Oil Deflector K 0.008 0.007 0.012 0.015 0.019 0.011 Middle Oil Deflector L Hydrogen Sea
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | c46f067a38acccb892d678d744cef86c | 190 | 2024-12-20 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 4 | Collector Rings, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  | EM2101 | Oil Deflector Alignment ¦ Collector Rings ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM2101 | . 2. G1= generator coupling end bearing, G2 = generator collector end bearing. S1 = Steady rest bearing. A1 = Alterrex coupling bearing, A2 = Alterrex collector bearing. Brg LSL USL Acutal Tolerance #3 IV OV IT OT (inches) (inches) (inches) Check TE 16.000 16.000 0.016 0.017 0.000 0.0016 0.001 Acceptable CE 16.000 16.000 0.022 0.022 0.000 0.0016 0.000 Acceptable Brg LSL USL Actual Tolerance #3 IL OL IR OR (inches) (inches) (inches) Check TE 0.019 0.018 0.016 0.017 -0.005 0.005 0.001 Acceptable C
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 60bc5d4142b23f8953b054f9c73b57c8 | 212 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | Initial Date Initial Date Initial Date 1 Mobilization 2 Receiving, Prep & Setup 3 7F002.1.2 Receive, Inspect, and Set Up Crane and Other Heavy Lift Equipment - Certifications Crane and Heavy Equipment Certifications Verified WD 10/4/24, 9:1 |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | . Reproduction, use or disclosure to third parties without express authority is strictly forbidden. © GE 2019 QCP - Quality Control Plan 10366888 No. Checklist ID Checklist Name - Checklist Page Quality Check Remarks . Initial Date Initial Date Initial Date Outage ID: Craft Supervisor GE Field Engineer Customer (if applicable) Initial WD KH MB WD1 Full names and SSO of GE signatories Walter Darnell Kiah Hollenbeck Maverick Birch Walter Darnelll We reserve all rights in this document and the info
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 385648c6e0a04d53af3740413ce88840 | 97 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Inspection Type: Visual Part Condition: Good Part Description: The collector end of the generator was completely disassembled for the removal of the field. The T4 bearing was sent out for NDE but the babbet was not re-poured or machined. See below for measured dimensions, the NDE report, and photos. Documented scoring was found in T4 bearing babbet, customer elected to reinstall bearing. New hydrogen seals, inner oil deflector, mid oil deflector, and outer oil deflector installed. Data sheets ar
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 936384d4eac20974e6fcd38adc48a418 | 122 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Inspection Type: Visual, Dimensional Part Condition: Good Part Description: The turbine end of the generator was completely disassembled for the removal of the field. The T3 bearing was sent out for NDE but the babbet was not re-poured or machined. See below for measured dimensions, the NDE report, and photos. Documented scoring was found in T3 bearing babbet, customer elected to reinstall bearing. New hydrogen seals, inner oil deflector, mid oil deflector, and outer oil deflector installed. Dat
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 754b3fa31686f42fb3aa84aee9b0b9ad | 22 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | As Found Oil Seals As Found T1 Bearing As Found T1 Oil Seal Cleaned T1 Bearing Cap Incoming Tilt Pad Bearing (3) Incoming Tilt Pad Bearing Installed T1 Oil Seals (2) Installed T1 Oil Seals (3) Installed T1 Oil Seals Loctite 510 Applied As S | GEK103551 | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ GEK103551 | Inspection Type: Visual, Dimensional Part Condition: Good Part Description: The upper and lower half T1 bearing liners were removed and inspected visually. The as found condition reported shallow surface scratches, minor dents and nicks, and minor de- babbiting on the upper and lower half tilting pads. The unit received new lift oil lines along with a newly cut bearing with reference to the new rotor's T1 journal conditions. Machine Shop Data was reviewed and a lead wire clearance inspection was
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 3a8740403cde22dc9e848b93b3cb7bc9 | 6 | 2024-12-20 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | Fan Blades, Seal Rings | 7-13 Generator Fan Blades TE GE and Exciter VT PT........................................................................................................................... |  | Focused Generator Review ¦ Fan Blades ¦ Seal Rings | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 298128 Hanging Rock Power Company LLC Hanging Rock Energy Facility 1 2 3 4 5 6 7 8 9 10 Member of ASNT * SNT - TC - 1A Certified Technicians 3A-NDE-0000P_R16_020624 _Components Report_Table of Contents 2GT2 Rotor Blade Blends FPI.......................................................................................................................................................... 27-2
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 128fa4a4f964222a5c0d63efde25cf68 | 211 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | WD 11/17/24, 8:55 AM GMT-5 KH 11/17/24, 8:55 AM GMT-5 16 Oil Deflectors 17 7FH2GOD 300.4.5 Install CE Inner Oil Deflector - Quality Checks CE Inner Oil Deflector Installation Satisfactory WD 11/13/24, 9:22 AM GMT-5 KH 11/12/24, 6:25 AM GMT- |  | Oil Deflector Alignment ¦ Oil Deflectors | . WD 11/17/24, 8:55 AM GMT-5 KH 11/17/24, 8:55 AM GMT-5 16 Oil Deflectors 17 7FH2GOD 300.4.5 Install CE Inner Oil Deflector - Quality Checks CE Inner Oil Deflector Installation Satisfactory WD 11/13/24, 9:22 AM GMT-5 KH 11/12/24, 6:25 AM GMT-5 18 7FH2GOD 301.4.5 Install TE Inner Oil Deflector - Quality Checks TE Inner Oil Deflector Installation Satisfactory WD 11/13/24, 9:20 AM GMT-5 KH 11/12/24, 6:25 AM GMT-5 19 7FH2GOD 302B.3.4 Install CE Outer Oil Deflector - Install CE Outer Oil Deflector CE
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | af53bdd84a72a843fbe74140e863eca1 | 26 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Clearance checks were performed on T1 bearing liner, seals rings, and oil deflectors upon closure, and results were verified against the unit clearance diagram. |  | Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual, Dimensional Part Condition: Poor Part Description: Upon removal of the inlet bellmouth, the T1 bearing instrument ports, the bearing casing horizontal joint, and the bellmouth horizontal joint were checked for signs of oil leakage. No signs of oil leakage into the unit or outside the bearing cap was noted. The initial inspection of the tilt-pads showed a moderate amount of babbitt wiping. The root cause was not determined during this outage but several possible contribut
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 701d7a5717d9bbbcf8e4ff34ae4dc20a | 210 | 2024-12-20 | Mechanical | Field | Blue Check | 2 | Blue Check, Fan Blades | Initial Date Initial Date Initial Date 1 Clean & Inspect 2 Hydrogen Casings & Seals 3 7FH2GHY 204B.3.10 Lap CE H2 Bolted Seals - Lap CE H2 Gas Seals Bolted CE H2 Gas Seals Blue Check Satisfactory WD 11/2/24, 7:37 AM GMT-4 KH 11/1/24, 12:25 |  | Blue Check ¦ Fan Blades | See content below. GEGEGE GE Vernova Confidential and Proprietary Information. Not to be copied, reproduced or distributed without GE Vernova prior written consent. QCP - Quality Control Plan 28 Hanging Rock Energy Facility (Day Shift) MI Fall 2024 - 7F - 7FH2 Generator - QCP Hanging Rock Created: 605037920 2GT2 Approved: Name/Date: Maverick Birch Vistra Export Date: 12/1/24, 5:49 PM GMT-5 10366888 No. Checklist ID Checklist Name - Checklist Page Quality Check Remarks . Initial Date Initial Date
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 614469b3ad4114299bdf8d69d857933d | 528 | 2024-12-20 | Inspection | Hydrogen Seals | Focused Generator Review | 2 | Hydrogen Seal Assembly, Seal Rings | The hydrogen seal rings seal against the casing and tend to chatter during startup and shutdown. |  | Focused Generator Review ¦ Hydrogen Seal Assembly ¦ Seal Rings | . 001 Page ¦ 1 2GT2 Generator Hydrogen Leak Discovery Executive Summary: While inspecting the generator stator frame with Viking, oil leakage was noticed to be coming from the upper generator lead access covers. It is evident that the vaporized oil began leaking through the cover with the hydrogen. The indicated dark spots in the pictures below are showing the oil leakage where hydrogen is escaping. It is recommended to replace the two gaskets with 252C1022P0001. Part Number Description Order QT
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | fb7740fd615465f0b7339db3129be7d5 | 212 | 2024-12-20 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | End Shield, Fan Blades | Craft Supervisor GE Field Engineer Customer (if applicable) 31 7FH2GB30 6.3.10 Install CE Bearing Cap - Perform Pinch Check CE Bearing Cap Pinch Check Satisfactory WD 11/16/24, 3:08 PM GMT-5 KH 11/13/24, 5:32 PM GMT-5 32 7FH2GB30 6.4.2 Inst |  | Focused Generator Review ¦ End Shield ¦ Fan Blades | . Initial Date Initial Date Initial Date Outage ID: Craft Supervisor GE Field Engineer Customer (if applicable) 31 7FH2GB30 6.3.10 Install CE Bearing Cap - Perform Pinch Check CE Bearing Cap Pinch Check Satisfactory WD 11/16/24, 3:08 PM GMT-5 KH 11/13/24, 5:32 PM GMT-5 32 7FH2GB30 6.4.2 Install CE Bearing Cap - Install CE Bearing Cap CE Bearing Cap Close Out Complete WD 11/16/24, 3:08 PM GMT-5 KH 11/13/24, 5:32 PM GMT-5 33 7FH2GB30 7H.3.10 Install TE Bearing Cap - Perform Pinch Check TE Bearing
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | c5f7ba29afc96f3461b4dc7e9ce16d38 | 214 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | . WD 10/9/24, 5:00 PM GMT-4 MB 10/9/24, 5:01 PM GMT-4 27 Roof, Walls, Enclosures & Ducting 28 7F038.4.5 Remove FWD Roof - FWD Roof Removal Critical Lift Meeting Complete WD 10/8/24, 2:23 PM GMT-4 MB1 10/8/24, 4:55 PM GMT-4 29 7F037.4.5 Remove AFT Roof - Aft Roof Removal Critical Lift Meeting Complete WD 10/8/24, 2:21 PM GMT-4 MB1 10/8/24, 4:56 PM GMT-4 30 Opening Clearances 31 7F435.4.3 Record Opening Turbine Clearances (AGP) - Quality Checks Opening Turbine Clearances QC Complete KH 10/15/24, 5
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 15bba9f23c7e839ced814ec75a65d785 | 522 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | ER-20180605-0899, ER-20190312-1286 | Oil Deflector Alignment ¦ Oil Deflectors ¦ ER-20180605-0899 ¦ ER-20190312-1286 | . 001 Page ¦ 1 Hanging Rock Facility 2GT2 Discovery Log Mini Report Executive Summary: Throughout the disassembly of 2GT2, the following parts and components were found to be damaged and will require replacements or repairs. Findings: T2 bearing oil seal PN: 188D7278G001 (x1) The T2 bearing oil seal was found to be damaged. A replacement is required. Findings: T1 bearing oil seal PN: 199C4741G001 (x1) The T1 bearing oil seal was found to be damaged. A replacement is required. Hanging Rock 2GT2 D
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 5b64b0bc2c09c79e291329b1a8d0356c | 219 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | 7 Install UH HGP - Quality Checks Install UH HGP QC Complete WD 10/27/24, 6:23 PM GMT-4 MB1 10/22/24, 2:09 PM GMT-4 154 7F145.4.3 S1N Concentricity Checks - Quality Checks S1N Concentricity Checks QC Complete WD 10/22/24, 2:11 PM GMT-4 KH 1 |  | Oil Deflector Alignment ¦ Oil Deflectors | . 7 Install UH HGP - Quality Checks Install UH HGP QC Complete WD 10/27/24, 6:23 PM GMT-4 MB1 10/22/24, 2:09 PM GMT-4 154 7F145.4.3 S1N Concentricity Checks - Quality Checks S1N Concentricity Checks QC Complete WD 10/22/24, 2:11 PM GMT-4 KH 10/21/24, 4:28 PM GMT-4 155 Bearings 156 7F148.3.3 Install T1 LH Bearing and Labyrinth Seals - FME Close Out LH T1 FME Close Out Complete WD 11/2/24, 6:00 PM GMT-4 KH 11/1/24, 3:11 PM GMT-4 157 7F148.6.4 Install T1 LH Bearing and Labyrinth Seals - Quality Che
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | abeadb51738cf36c7b065e8d52696ee8 | 250 | 2024-12-20 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | Collector Rings, End Shield | ER-20241024-0338 – submitted on 10/24/24 This Engineering Record was entered due to the current condition of 2GT1’s field collector rings.; Disposition recommended grinding collector rings to meet criteria listed in GEK116363-revM.; Upper half end shield removal – Destructive disassembly hardware PN:; • 114T5127P0002 (2x) Select upper half end shield mechanical fasteners required copious amounts of heat to disassemble. | ER-20241020-0083, ER-20241024-0338, ER-20241027-0372, ER-20241101-0090, GEK116363 | Focused Generator Review ¦ Collector Rings ¦ End Shield ¦ ER-20241020-0083 ¦ ER-20241024-0338 | . There is notable wear to S15 area of the case. Disposition states no action is required to correct the twisting found in S14-S16. Monitoring of S14-S16 is recommended during annual borescope inspection ER-20241020-0083 – submitted on 10/19/24 This Engineering Record was entered to obtain disposition to blend FOD found on the stator and blades of the compressor section. Disposition was given and post blend photos were entered for documentation. ER-20241024-0338 – submitted on 10/24/24 This Engi
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | bd2efb7528a69aac8c2c35bfee57ac54 | 90 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | Inspection Type: Visual Part Condition: Good Part Description: New bearings were used from customer stock and within specification to be installed in the unit. T2 bearing clearances were recorded and are provided below. A new forward oil deflector was installed this outage. New thermocouples were installed and nichrome welded in place, along with new lift oil lines.
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | f362bb2c0815849c1433cd2a2d79f33d | 30 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Clearance checks were performed on T1 bearing liner, seals rings, and oil deflectors upon closure, and results were verified against the unit clearance diagram.; All other T1 oil deflectors were removed, cleaned, measured and reinstalled. |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Description: Magnetic speed pickups, key phasor, seismic sensors, axial probes, and radial probes were also inspected, found in good condition, and returned to service. All instrumentation devices were tested, verified, and set (gap adjusted) post installation and connection. Clearance checks were performed on T1 bearing liner, seals rings, and oil deflectors upon closure, and results were verified against the unit clearance diagram. All clearance measurements were within acceptable limits
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 4d875bad2ace3dafe290f8f21d16831a | 192 | 2024-12-20 | Inspection | Hydrogen Seals | Focused Generator Review | 2 | Hydrogen Seal Assembly, Seal Rings |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly ¦ Seal Rings | . Enter "NA" if bearing is not insulated. Ball Pinch Check 7FH2 11/5/2024 298127 GE/APM 338X727 10366903 As Left English - Inches Inspections and Checks Description CODE 396,300 Ball Torque Check Twist & Tilt Check Journal Inspection Babbit Inspection Screens & Orifices Insulation Resistance Test Inboard Outboard Vertical Clearance Insul. Resistance (Ohms)* N/A Comments Instrument Description ID No. Calibration Date User Name D316602 Sheet: (a) Rev 2.1 - 01/12/17 Seal Oil System Hydrogen Seals a
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 315daf1ba22262d5c81bf2319e35277d | 262 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | EM5342 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5342 | . Pipe Location Damage type Repair or Replace Part Number Can 5 Quaternary Welds have fractured on one end exposing wire mesh. It is recommended to weld the armor back to the flange. Repair 366A2336P032 Can 7 Quaternary Armor shows signs of abrasion. Crude repairs can be made in emergency situations, but it is recommended to replace Replace 366A2336P034 Can 11 Quaternary Armor has completely sheared in a middle section. It is recommended to replace. Replace 366A2336P038 Can 10 Quaternary Armor h
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 7e42a3d2e85853abe7529a04108649b3 | 163 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | are the final measurements for the new generator oil deflectors. |  | Oil Deflector Alignment ¦ Oil Deflectors | . INSPECTION REPORT Gas Turbine Maintenance X1 X2 Date Turbine No. 298127 Prepared by GE/APM FSR # Sketches Enclosed? Photos Enclosed? Position X1 X2 Backlash Inner 26 0.038 0.055 0.010 27 0.038 0.049 0.011 28 0.042 0.050 0.014 29 0.035 0.049 0.015 30 0.041 0.047 0.019 31 0.042 0.049 0.020 32 0.047 0.047 0.013 33 0.038 0.050 0.018 34 0.033 0.049 0.016 35 0.029 0.049 0.011 36 0.018 0.048 0.019 37 0.026 0.049 0.010 38 0.023 0.045 0.013 39 0.021 0.045 0.018 40 0.017 0.050 0.019 41 0.019 0.045 0.020
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | 564f63732de3d196b942c081e8c4fcd3 | 187 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | A B B A C C 110E2905G002 A B Turbine Oil Deflectors - 298127 - GT2 - D309301 GE Energy Services Company Proprietary Information Oil Seal Clearances Date(m/d/y) 10/26/2024 Turbine Serial No. |  | Oil Deflector Alignment ¦ Oil Deflectors | . GT2060 Sheet: (a) Rev 3.0 - 02/22/2023 g Oil Deflector Clearances Date (m/d/y) Turbine Serial No. 298113 Prepared by Teeth Inspected x BT Bent Teeth X Work Carried Out Journals Inspected x MT Missing Teeth N Not Done Drain Holes Inspected x RT Rubbed Teeth NA Not Applicable Inspect for Rubs x DHT Hor. Joint Damage C See Comments RN Repair Needed V Visual Inspection EC Excessive Clearance T-1 T-1 Inlet T-2 T-2 T-1 A-Dia B-Dia C-Dia A-Dia B-Dia C-Dia Average Minimum Maximum #1 Forward - A 18.558
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633208_EV-118802_C-10366901_EVP-515932.pdf | 298127 | Gas Turbine | d6340c334c53e1842b51ad109f352f2f | 183 | 2024-12-20 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | . Dim. • All axial clearances are measured with rotor against the loaded thrust face. Refer to EM5260 to confirm rotor position. 10/12/2024 CONDITION CODE M - Missing Metal W - Worn CR - Cracked DISPOSITION CODE N - No Repair or Replacement Necessary R - Repaired RN - Replaced with New Component GT71F103 T1S 1S1 1 WF1 T1 TAS #1 BRG. 1S2 1S7* LOADED THRUST FACE 1S8* 1S9* 1S3 1S4 1S5 1S6 1S10* CL INSPECTION REPORT Gas Turbine Maintenance GT2025 Sheet: (a) Rev 3.0 - 06/28/2020 GE Proprietary - Non
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | d5b5757c34d808d012a0b8862b00e211 | 176 | 2024-12-20 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . Bibek Thapa MT, PT, VT II PO #: 4900414059 SURFACE CONDITION: In Service Job Number: CF-6996 Date: 10/18/2024 Page: 33 CONTINUATION SHEET CUSTOMER: FCSS JOB SITE: Hanging Rock Energy Facility LOB on the edge. FOD on Blade 7 pad face. 9 of NDT Technician: Member of ASNT * SNT - TC - 1A Certified Technicians 3A-NDE-0000P_R16_020624 _Components Report_Continuation Sheet MATERIAL DESCRIPTION: Thrust pads : Inactive(8). Bibek Thapa MT, PT, VT II PO #: 4900414059 SURFACE CONDITION: In Service Job Nu
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 91fe381c220bfee1d32de87c046147ec | 228 | 2024-12-20 | Inspection |  | Focused Generator Review | 1 | Greasing | Likely due to excessive greasing during maintenance intervals. | ER-20241020-0098, ER-20241021-0869, ER-20241023-1147, ER-20241027-0148 | Focused Generator Review ¦ Greasing ¦ ER-20241020-0098 ¦ ER-20241021-0869 | . If this action taken, flex seals MUST be replaced at next planned outage. Site could also locally weld build up tabs in the pipe gap to close some of the gap. Would not need to do entire pipe circumference, instead just a handful of locations to help reduce risk of shingling by bringing pipe gap closer to spec. If this option is taken, there is risk to the pipe itself. Weld addition could impact pipe strength or cause localized cracking in the welded region. If this action taken, pipe MUST be
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | d2afdece581cc0267e80076ae4e3d9cd | 212 | 2024-12-20 | Inspection | Field | Focused Generator Review | 1 | Fan Blades | TE Fan Blades - Quality Checks TE Fan Blades Torqued and Lock Tabs Bent WD 11/13/24, 9:18 AM GMT-5 KH 11/12/24, 6:23 AM GMT-5 59 Non-Standard 60 Bearings 61 7FH2GB40 0.4.10 Replace CE Lift Oil Line - Install CE Lift Oil Line CE Lift Oil Lin |  | Focused Generator Review ¦ Fan Blades | TE Fan Blades - Quality Checks TE Fan Blades Torqued and Lock Tabs Bent WD 11/13/24, 9:18 AM GMT-5 KH 11/12/24, 6:23 AM GMT-5 59 Non-Standard 60 Bearings 61 7FH2GB40 0.4.10 Replace CE Lift Oil Line - Install CE Lift Oil Line CE Lift Oil Line Installation Satisfactory WD 11/10/24, 8:54 AM GMT-5 KH 11/17/24, 8:50 AM GMT-5 62 7FH2GB40 1.4.10 Replace TE Lift Oil Line - Install TE Lift Oil Line TE Lift Oil Line Installation Satisfactory WD 11/10/24, 9:04 AM GMT-5 KH 11/17/24, 8:50 AM GMT-5 We reserve
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | cb69f1a54f120730e9f16af1f3ef9e84 | 416 | 2024-12-20 | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | . Job #: S1N7FAE171703 3. Comments GE Power supplies components for hot gas management in power generating equipment. These components gain their thermal and abrasion resistant properties from the application of a surface coating of yttria-stabilized zirconia ceramic powder. The powder used in this process contains low levels of naturally occurring radioactive material (NORM). The enclosed parts list specifies the parts that include these coatings. Customers should consider this activity level,
UNI035965 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633210_EV-123983_C-10366888_EVP-515935.pdf | 298128 | Gas Turbine | 39b140ddd0220cc4578ac0daf7325275 | 106 | 2024-12-20 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | Part Description: The T2 bearing cap was removed, inspected, and cleaned. The T2 bearing strongback was removed, inspected, and cleaned. The new bearing liner reports are in the appendix. The new bearing liner lift lines and check valves were blown with air to verify the check valve orientation. The new bearing was installed without issues to note. New lift lines were also installed and verified to be torqued to 15 ft*lbs. New thermocouples were installed and routed per GE drawing suggestions. D
UNI036334 | Casco Bay Power Station | Field_Service_Report_ProjectID_A-1828044_EV-156895_C-10380820_EVP-536579.pdf | 297197 | Gas Turbine | 6dd14ef93a891b859b5887f19004b447 | 52 | 2024-11-14 | Inspection | Hydrogen Seals | Hydrogen Seal Findings Review | 2 | Seal Rings, Water Ingress | - Contributors to the noted erosion could be online water-wash, water ingress through inlet-duct leaks, inlet fogging, and/ or, water carry-over from poorly conditioned evaporative coolers. | ER-20231123-0536, ER-20240709-0330 | Hydrogen Seal Findings Review ¦ Seal Rings ¦ Water Ingress ¦ ER-20231123-0536 ¦ ER-20240709-0330 | . GE Vernova Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property of GE and Power Service Now ER case of Interest: 1) MND-20230625-0200: GT Combustion Profile Anomaly - During recent operation a cold spot of ~45F colder than TTXM was observed across TCs #16-17 while operating around 150 MW. This spot does not swirl with load and is only seen on TCs #16 and 17 at load
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 8eb2e7ddc129869692e7236745d0653b | 5 | 2024-06-26 | Electrical | Field, Hydrogen Seals, Stator | Polarization Index; DC Leakage | 9 | AC Impedance, DC Leakage, Fan Blades, Focused Generator Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Wedge Tightness Test, Wedges | Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 4.1 Attachments __________ 288 5 Unit __________ 297 5.1 Parts Used __________ 297 6 PIPO __________ 326 6.1 Combustion __; Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.1.3 Outer End-Shield __________ 434 2.1.4 Inner Air-Shields __________ 438 2.1.5 H2 Seals and Cases __________ 438 2.1.6; Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.3.7 Megger Test on RTDs __________ 465 2.3.8 Wedge Tightness Test __________ 467 2.4 Field Visual Inspection __________ |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ DC Leakage ¦ Fan Blades ¦ Focused Generator Inspection ¦ Oil Deflector Alignment ¦ Oil Deflectors | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.7.2 Exhaust Diffuser __________ 219 2.7.3 T2 Journal Bearing __________ 220 2.8 Unit Rotor and Casing Alignment __________ 224 2.8.1 Turbine to Generator Alignment __________ 224 2.8.2 Unit Rotor __________ 226 2.8.3 Internal Casing Alignment __________ 230 2.8.4 Load Coupling and Coupling B
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 8910207aa55c415ee1d3943edbab6fb1 | 5 | 2024-06-26 | Electrical | Field, Hydrogen Seals, Stator | Polarization Index; DC Leakage | 9 | AC Impedance, DC Leakage, Fan Blades, Focused Generator Inspection, Oil Deflector Alignment, Oil Deflectors, Polarization Index, Wedge Tightness Test, Wedges | Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 4.1 Attachments __________ 288 5 Unit __________ 297 5.1 Parts Used __________ 297 6 PIPO __________ 326 6.1 Combustion __; Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.1.3 Outer End-Shield __________ 434 2.1.4 Inner Air-Shields __________ 438 2.1.5 H2 Seals and Cases __________ 438 2.1.6; Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.3.7 Megger Test on RTDs __________ 465 2.3.8 Wedge Tightness Test __________ 467 2.4 Field Visual Inspection __________ |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ DC Leakage ¦ Fan Blades ¦ Focused Generator Inspection ¦ Oil Deflector Alignment ¦ Oil Deflectors | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 297257, Major Inspection (Rotor Out) - 337X710 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.7.2 Exhaust Diffuser __________ 219 2.7.3 T2 Journal Bearing __________ 220 2.8 Unit Rotor and Casing Alignment __________ 224 2.8.1 Turbine to Generator Alignment __________ 224 2.8.2 Unit Rotor __________ 226 2.8.3 Internal Casing Alignment __________ 230 2.8.4 Load Coupling and Coupling B
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | db345006eb270f8e43c8d85a745175e2 | 483 | 2024-06-26 | Electrical | Hydrogen Seals, Stator | DC Leakage; AC Impedance | 7 | AC Impedance, DC Leakage, End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Stator Winding | DZ 4/28/24, 12:18 PM GMT-7 4 GS 202A.4.1 Stator Winding Copper Resistance - As Found - Clean Up Test is complete and results have been reviewed with Customer.; DZ 4/30/24, 5:41 AM GMT-7 6 GS 204A.4.1 Stator DC Leakage-DC Hi-pot Test - As Found - Clean Up Test is complete and results have been reviewed with Customer.; DZ 4/28/24, 8:51 AM GMT-7 11 GS 303A.4.1 Field AC Impedance Test - As Found - Clean Up Test is complete and results have been reviewed with Customer.; BH 5/10/24, 12:45 PM GMT-7 CT 5/10/24, 12:45 PM GMT-7 4 7FH2- 009.8.2 Prepare and Inspect Oil Deflectors - Review Measurements Generator Oil Deflectors - Cleaned and dimensionally checked BH 5/10/24, 12:45 PM GMT-7 CT 5/10/24, 12:45 PM GMT-; BH 4/23/24, 7:23 AM GMT-7 CT 4/23/24, 7:24 AM GMT-7 11 End Shield 12 7FH2- 106.4.2 CE Disassemble Upper Half End Shield - 7FH2 - Disassemble UH End Shield Sniff for H2 and ensure confined space is hung |  | DC Leakage; AC Impedance ¦ AC Impedance ¦ DC Leakage ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | See content below. QCP - Quality Control Plan Lamar Power Partners MI Spring 2024 - Generator Test and Inspect - QCP Created: 605011422 337X710 Approved: Name/Date: Luminant Export Date: 6/12/24, 9:05 AM GMT-7 10333910 No. Checklist ID Checklist Name - Checklist Page Quality Check Remarks . Initial Date Initial Date Initial Date 1 As Found 2 GENERATOR STATOR AS FOUND TESTING 3 GS 201A.4.1 RTD Measurements - As Found - Clean Up Test is complete and results have been reviewed with Customer. DZ 4/2
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 971f137767149defeb8c48d63578f210 | 483 | 2024-06-26 | Electrical | Hydrogen Seals, Stator | DC Leakage; AC Impedance | 7 | AC Impedance, DC Leakage, End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Stator Winding | DZ 4/28/24, 12:18 PM GMT-7 4 GS 202A.4.1 Stator Winding Copper Resistance - As Found - Clean Up Test is complete and results have been reviewed with Customer.; DZ 4/30/24, 5:41 AM GMT-7 6 GS 204A.4.1 Stator DC Leakage-DC Hi-pot Test - As Found - Clean Up Test is complete and results have been reviewed with Customer.; DZ 4/28/24, 8:51 AM GMT-7 11 GS 303A.4.1 Field AC Impedance Test - As Found - Clean Up Test is complete and results have been reviewed with Customer.; BH 5/10/24, 12:45 PM GMT-7 CT 5/10/24, 12:45 PM GMT-7 4 7FH2- 009.8.2 Prepare and Inspect Oil Deflectors - Review Measurements Generator Oil Deflectors - Cleaned and dimensionally checked BH 5/10/24, 12:45 PM GMT-7 CT 5/10/24, 12:45 PM GMT-; BH 4/23/24, 7:23 AM GMT-7 CT 4/23/24, 7:24 AM GMT-7 11 End Shield 12 7FH2- 106.4.2 CE Disassemble Upper Half End Shield - 7FH2 - Disassemble UH End Shield Sniff for H2 and ensure confined space is hung |  | DC Leakage; AC Impedance ¦ AC Impedance ¦ DC Leakage ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | See content below. QCP - Quality Control Plan Lamar Power Partners MI Spring 2024 - Generator Test and Inspect - QCP Created: 605011422 337X710 Approved: Name/Date: Luminant Export Date: 6/12/24, 9:05 AM GMT-7 10333910 No. Checklist ID Checklist Name - Checklist Page Quality Check Remarks . Initial Date Initial Date Initial Date 1 As Found 2 GENERATOR STATOR AS FOUND TESTING 3 GS 201A.4.1 RTD Measurements - As Found - Clean Up Test is complete and results have been reviewed with Customer. DZ 4/2
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 39c559097bf806dcb53b424a9089179b | 485 | 2024-06-26 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | BH 4/23/24, 7:23 AM GMT-7 CT 4/23/24, 7:24 AM GMT-7 13 7FH2- 106.4.4 CE Disassemble Upper Half End Shield - 7FH2 - Disassemble UH End Shield Verify non-permitted confined space has been approved.; BH 5/8/24, 10:01 AM GMT-7 CT 5/8/24, 10:02 AM GMT-7 28 Oil Deflectors 29 7FH2- 215.4.5 Clean and Inspect Oil Deflector - 7FH2 - Quality Checks Oil Deflector quality checks complete.; BH 5/8/24, 10:04 AM GMT-7 CT 5/8/24, 10:05 AM GMT-7 30 Fan Blades 31 7FH2- 211.4.6 Clean and Inspect Fan Blades and Bolts - Quality Checks Inspection results have been reviewed and are satisfactory. |  | Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . If Hydrogen is present, use of ventilation/air movers may be necessary to remove remaining H2. BH 4/23/24, 7:23 AM GMT-7 CT 4/23/24, 7:24 AM GMT-7 13 7FH2- 106.4.4 CE Disassemble Upper Half End Shield - 7FH2 - Disassemble UH End Shield Verify non-permitted confined space has been approved. 14 H2 Seals & Casings 15 7FH2- 104.7.4 CE Disassemble Hydrogen Seal Casing - Quality Checks CE Hydrogen Seal Casing disassembly Qualify Checks complete. BH 4/23/24, 7:27 AM GMT-7 CT 4/23/24, 7:28 AM GMT-7 16
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 8e14e92bf95fa175840400bffb81f58e | 461 | 2024-06-26 | Inspection | Field, Stator | Stator Findings Review | 5 | Core, Field Body, Greasing, Retaining Rings, Wedges | The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition.; Axial support hardware is performing as intended, aside from four location that greasing was present.; Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was visible.; Even though greasing was present at the tie to connection ring locations globally as well as the bar-bar ties, no signs of blocking or tie looseness was found.; Stator core was thoroughly inspected. |  | Stator Findings Review ¦ Core ¦ Field Body ¦ Greasing ¦ Retaining Rings ¦ Wedges | Part Description: The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition. Axial support hardware is performing as intended, aside from four location that greasing was present. Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was visible. These locations were retorqued to OEM specified values and locked
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | bf906ab5d75119dfb84d12a0157a7472 | 465 | 2024-06-26 | Electrical | Stator | DLRO; Polarization Index | 5 | DC Hipot, DC Leakage, DLRO, Polarization Index, Stator Winding | Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded.; Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.:; Left (CE) Center (CE)Right (CE) 4 4 5 26 7FH2 DC Conditions During HV Proof Test Winding Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044.; DC HIPOT RESULTS Daniel Zarate Steve Brown I01-094246 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Humidity (%) Conditions During Insulation Resistance 337X710 Insulati; Megger DLRO 513135 09/04/2024 Generator Test & Inspection 18.0 COMMENTS Thermal Setting (i.e. | TM2030, TM2050 | DLRO; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Description: Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded. These tests evaluate insulation integrity and GE has recommended values for proceeding to High Voltage testing or Return to Service. All results were satisfactory. Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.: Prepared by: Equipment Year Select OEM GE Stator Voltage (kV): Project ID: DC INSULATION RESISTANCE
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | e6a9f9b46af637fe201386944e4d4702 | 465 | 2024-06-26 | Electrical | Stator | DLRO; Polarization Index | 5 | DC Hipot, DC Leakage, DLRO, Polarization Index, Stator Winding | Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded.; Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.:; Left (CE) Center (CE)Right (CE) 4 4 5 26 7FH2 DC Conditions During HV Proof Test Winding Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044.; DC HIPOT RESULTS Daniel Zarate Steve Brown I01-094246 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Humidity (%) Conditions During Insulation Resistance 337X710 Insulati; Megger DLRO 513135 09/04/2024 Generator Test & Inspection 18.0 COMMENTS Thermal Setting (i.e. | TM2030, TM2050 | DLRO; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Description: Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded. These tests evaluate insulation integrity and GE has recommended values for proceeding to High Voltage testing or Return to Service. All results were satisfactory. Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.: Prepared by: Equipment Year Select OEM GE Stator Voltage (kV): Project ID: DC INSULATION RESISTANCE
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | cf3674e160bd255f5dacdec9c7e60b8b | 430 | 2024-06-26 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, Hydrogen Seal Assembly, Wedge Tightness Test, Wedges | · Stator Wedge Tightness Test.; · Core Tightness check (Knife test). |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ Hydrogen Seal Assembly ¦ Wedges | On April 20, 2024, GE Vernova mobilized to Lamar Power Partners to perform a Major T&I on CT22 Generator S/N 337X710. This scope included: Generator: · Maintenance Electrical Testing. · Stator Wedge Tightness Test. · Core Tightness check (Knife test). · EL CID Field: · Maintenance Electrical Testing. · Hydrogen Seal Test of Collector Studs.
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | d790455b5ef946abca83f940a8e51719 | 474 | 2024-06-26 | Electrical | Stator | DLRO; Polarization Index | 5 | DC Hipot, DC Leakage, DLRO, Polarization Index, Stator Winding | Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded.; Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.:; Left (CE) Center (CE)Right (CE) 4 4 5 26 7FH2 DC Conditions During HV Proof Test Winding Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044.; DC HIPOT RESULTS Daniel Zarate Steve Brown I01-094246 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Humidity (%) Conditions During Insulation Resistance 337X710 Insulati; Megger DLRO 513135 09/04/2024 Generator Test & Inspection 18.0 COMMENTS Thermal Setting (i.e. | TM2030, TM2050 | DLRO; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Description: Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded. These tests evaluate insulation integrity and GE has recommended values for proceeding to High Voltage testing or Return to Service. All results were satisfactory. Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.: Prepared by: Equipment Year Select OEM GE Stator Voltage (kV): Project ID: DC INSULATION RESISTANCE
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 8b12484288fbdb1571d716e06c2485bd | 430 | 2024-06-26 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, Hydrogen Seal Assembly, Wedge Tightness Test, Wedges | · Stator Wedge Tightness Test.; · Core Tightness check (Knife test). |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ Hydrogen Seal Assembly ¦ Wedges | On April 20, 2024, GE Vernova mobilized to Lamar Power Partners to perform a Major T&I on CT22 Generator S/N 337X710. This scope included: Generator: · Maintenance Electrical Testing. · Stator Wedge Tightness Test. · Core Tightness check (Knife test). · EL CID Field: · Maintenance Electrical Testing. · Hydrogen Seal Test of Collector Studs.
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 3ec0f21105f73413261a47c80f601f37 | 474 | 2024-06-26 | Electrical | Stator | DLRO; Polarization Index | 5 | DC Hipot, DC Leakage, DLRO, Polarization Index, Stator Winding | Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded.; Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.:; Left (CE) Center (CE)Right (CE) 4 4 5 26 7FH2 DC Conditions During HV Proof Test Winding Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044.; DC HIPOT RESULTS Daniel Zarate Steve Brown I01-094246 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Humidity (%) Conditions During Insulation Resistance 337X710 Insulati; Megger DLRO 513135 09/04/2024 Generator Test & Inspection 18.0 COMMENTS Thermal Setting (i.e. | TM2030, TM2050 | DLRO; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Description: Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded. These tests evaluate insulation integrity and GE has recommended values for proceeding to High Voltage testing or Return to Service. All results were satisfactory. Stator Winding Insulation Resistance / HV Proof Tests Date 04/29/2024 Generator No.: Prepared by: Equipment Year Select OEM GE Stator Voltage (kV): Project ID: DC INSULATION RESISTANCE
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | d13c29f1bca8da8ba9fc1558c340f852 | 461 | 2024-06-26 | Inspection | Field, Stator | Stator Findings Review | 5 | Core, Field Body, Greasing, Retaining Rings, Wedges | The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition.; Axial support hardware is performing as intended, aside from four location that greasing was present.; Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was visible.; Even though greasing was present at the tie to connection ring locations globally as well as the bar-bar ties, no signs of blocking or tie looseness was found.; Stator core was thoroughly inspected. |  | Stator Findings Review ¦ Core ¦ Field Body ¦ Greasing ¦ Retaining Rings ¦ Wedges | Part Description: The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition. Axial support hardware is performing as intended, aside from four location that greasing was present. Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was visible. These locations were retorqued to OEM specified values and locked
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | 43f9ee2897f66b95a916d06b4b280ae9 | 485 | 2024-06-26 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | BH 4/23/24, 7:23 AM GMT-7 CT 4/23/24, 7:24 AM GMT-7 13 7FH2- 106.4.4 CE Disassemble Upper Half End Shield - 7FH2 - Disassemble UH End Shield Verify non-permitted confined space has been approved.; BH 5/8/24, 10:01 AM GMT-7 CT 5/8/24, 10:02 AM GMT-7 28 Oil Deflectors 29 7FH2- 215.4.5 Clean and Inspect Oil Deflector - 7FH2 - Quality Checks Oil Deflector quality checks complete.; BH 5/8/24, 10:04 AM GMT-7 CT 5/8/24, 10:05 AM GMT-7 30 Fan Blades 31 7FH2- 211.4.6 Clean and Inspect Fan Blades and Bolts - Quality Checks Inspection results have been reviewed and are satisfactory. |  | Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . If Hydrogen is present, use of ventilation/air movers may be necessary to remove remaining H2. BH 4/23/24, 7:23 AM GMT-7 CT 4/23/24, 7:24 AM GMT-7 13 7FH2- 106.4.4 CE Disassemble Upper Half End Shield - 7FH2 - Disassemble UH End Shield Verify non-permitted confined space has been approved. 14 H2 Seals & Casings 15 7FH2- 104.7.4 CE Disassemble Hydrogen Seal Casing - Quality Checks CE Hydrogen Seal Casing disassembly Qualify Checks complete. BH 4/23/24, 7:27 AM GMT-7 CT 4/23/24, 7:28 AM GMT-7 16
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1426924_EV-107829_C-10333940_EVP-504930.pdf | 297257, 337X710 | Gas Turbine, Generator | c6c5d73036be7ea8c129b0fa4734ad2c | 16 | 2024-06-26 | Mechanical | Field, Hydrogen Seals, Stator | Oil Deflector Alignment | 4 | Core, Fan Blades, Oil Deflector Alignment, Oil Deflectors | · Removed, visually inspected, cleaned, and reinstalled CE and TE end-shields · Removed and replaced TE and CE H2 seals and reinstalled H2 seal cases · Removed, cleaned, visually inspected, and replaced CE and TE outer oil deflectors · Remo | ER-20240502-1615, ER-20240519-0171, ER-20240520-1081, ER-20240528-0784 | Oil Deflector Alignment ¦ Core ¦ Fan Blades ¦ Oil Deflectors ¦ ER-20240502-1615 ¦ ER-20240519-0171 | . Flexible metal hoses portion of each can were replaced · T2 bearing area cooling flexible metal hose was removed and replaced · Cooling and seal air piping were removed, inspected, and reinstalled. Flexible metal hoses were replaced Fuel Gas System: · PM1, PM2, PM4 (now Pilot) and SRV were removed and replaced with Moog refurbished valves · PM3 removed and replaced with a Woodward larger size valve · All gas fuel vales were successful calibrated by control TA Hydraulic Accumulator: Replaced 8-
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 614db543c6c294f87e24ead334356a04 | 5 | 2024-06-25 | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 8 | AC Impedance, DC Leakage, Focused Generator Inspection, Generator Pressure Test, Hydrogen Seal Assembly, Polarization Index, Wedge Tightness Test, Wedges | Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 5.1 Combustion __________ 160 5.2 Hot Gas Path __________ 164 5.3 Rotor __________ 190 6 Appendix __________ 191 6.1 Attac; Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.2.3 Armature Winding Copper Resistance Test __________ 431 2.2.4 DC Leakage Test and Hipot Test __________ 433 2.2.5 EL |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ DC Leakage ¦ Focused Generator Inspection ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Polarization Index | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 3.1.3 Work Scope Completed __________ 124 3.1.4 Task identified for next Outage __________ 141 3.2 Mark Controller Status __________ 141 3.2.1 General Hardware __________ 141 3.3 Regulator Calibration __________ 141 3.3.1 GCV Calibration __________ 141 3.3.2 IGV Calibration __________ 147 3.3.
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 0d92f56a3bc2e449907058ef8d2785ae | 5 | 2024-06-25 | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 8 | AC Impedance, DC Leakage, Focused Generator Inspection, Generator Pressure Test, Hydrogen Seal Assembly, Polarization Index, Wedge Tightness Test, Wedges | Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 5.1 Combustion __________ 160 5.2 Hot Gas Path __________ 164 5.3 Rotor __________ 190 6 Appendix __________ 191 6.1 Attac; Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 2.2.3 Armature Winding Copper Resistance Test __________ 431 2.2.4 DC Leakage Test and Hipot Test __________ 433 2.2.5 EL |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ DC Leakage ¦ Focused Generator Inspection ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Polarization Index | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (MI) - 297258, Major Inspection (Rotor Out) - 337X711 LA FRONTERA HOLDINGS, LLC LAMAR POWER PARTNERS 3.1.3 Work Scope Completed __________ 124 3.1.4 Task identified for next Outage __________ 141 3.2 Mark Controller Status __________ 141 3.2.1 General Hardware __________ 141 3.3 Regulator Calibration __________ 141 3.3.1 GCV Calibration __________ 141 3.3.2 IGV Calibration __________ 147 3.3.
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 4e54219386f1ee1888d5184f100797dd | 23 | 2024-06-25 | Mechanical | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 6 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Unit Rotor • Rotor Assembly • Load Coupling Hardware GENERATOR • T3 Bearing • T4 Bearing • Oil Deflectors • Hydrogen Seals • Hydrogen Casings • Radial Fan Blades • Collector Fan Blades Additional maintenance included:; GAS TURBINE • Load Coupling – in good condition, cleaned, and reinstalled • Inner Barrel – in good condition, cleaned, and reinstalled • Compressor Discharge Casing – in good condition, cleaned, and reinstalled • Turbine Casing – in good co |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | . Exhaust • Exhaust Frame • T2 Bearing 6. Unit Rotor • Rotor Assembly • Load Coupling Hardware GENERATOR • T3 Bearing • T4 Bearing • Oil Deflectors • Hydrogen Seals • Hydrogen Casings • Radial Fan Blades • Collector Fan Blades Additional maintenance included: • Clean and Inspect Extraction, Cooling, and Sealing Air Piping • Remove and replace Extraction Air Block Valves • Lube Oil Flush Block install and removal • Exhaust Diffuser Skin repairs • Replaced Generator Lift Oil Lines and Check Valves
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | c8bc65c487952c3e8d29fb85e8362f79 | 475 | 2024-06-25 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 6 | Collector Rings, End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Collector (CE) and Turbine Ends (TE) disassembled in support of Field removal and concurrent MI requirements, this consisted of removing Hydrogen (H2) Casing and Seal Assemblies, Bearings, End Shields, Inner Gas Shields, and Fan Blades.; CE End Shield reinstalled after H2 Casing Feed Bore Plug weld was weld repaired and NDE performed;; Both End Shields and associated components reinstalled with fresh Channel Sealant.; Three of four Oil Deflectors inspected and found wore beyond limits then replaced with new from on-hand store surplus.; Both CE and TE Radial Fan Blades replaced with new to include all associated hardware. |  | Oil Deflector Alignment ¦ Collector Rings ¦ End Shield ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Part Description: Collector (CE) and Turbine Ends (TE) disassembled in support of Field removal and concurrent MI requirements, this consisted of removing Hydrogen (H2) Casing and Seal Assemblies, Bearings, End Shields, Inner Gas Shields, and Fan Blades. Field was supported by hydraulic and mechanical Jacking devices, after associated component removal, Field was transferred to installed Body Shoes for removal. Lamar supplied Field removal support structure installed and Field pulled for require
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 1703ab1a86f23b6c8634892ac2e7c68e | 475 | 2024-06-25 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 6 | Collector Rings, End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Collector (CE) and Turbine Ends (TE) disassembled in support of Field removal and concurrent MI requirements, this consisted of removing Hydrogen (H2) Casing and Seal Assemblies, Bearings, End Shields, Inner Gas Shields, and Fan Blades.; CE End Shield reinstalled after H2 Casing Feed Bore Plug weld was weld repaired and NDE performed;; Both End Shields and associated components reinstalled with fresh Channel Sealant.; Three of four Oil Deflectors inspected and found wore beyond limits then replaced with new from on-hand store surplus.; Both CE and TE Radial Fan Blades replaced with new to include all associated hardware. |  | Oil Deflector Alignment ¦ Collector Rings ¦ End Shield ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Part Description: Collector (CE) and Turbine Ends (TE) disassembled in support of Field removal and concurrent MI requirements, this consisted of removing Hydrogen (H2) Casing and Seal Assemblies, Bearings, End Shields, Inner Gas Shields, and Fan Blades. Field was supported by hydraulic and mechanical Jacking devices, after associated component removal, Field was transferred to installed Body Shoes for removal. Lamar supplied Field removal support structure installed and Field pulled for require
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 964a06436fd1a43b1a20759858c9ba9f | 23 | 2024-06-25 | Mechanical | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 6 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Unit Rotor • Rotor Assembly • Load Coupling Hardware GENERATOR • T3 Bearing • T4 Bearing • Oil Deflectors • Hydrogen Seals • Hydrogen Casings • Radial Fan Blades • Collector Fan Blades Additional maintenance included:; GAS TURBINE • Load Coupling – in good condition, cleaned, and reinstalled • Inner Barrel – in good condition, cleaned, and reinstalled • Compressor Discharge Casing – in good condition, cleaned, and reinstalled • Turbine Casing – in good co |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | . Exhaust • Exhaust Frame • T2 Bearing 6. Unit Rotor • Rotor Assembly • Load Coupling Hardware GENERATOR • T3 Bearing • T4 Bearing • Oil Deflectors • Hydrogen Seals • Hydrogen Casings • Radial Fan Blades • Collector Fan Blades Additional maintenance included: • Clean and Inspect Extraction, Cooling, and Sealing Air Piping • Remove and replace Extraction Air Block Valves • Lube Oil Flush Block install and removal • Exhaust Diffuser Skin repairs • Replaced Generator Lift Oil Lines and Check Valves
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 794ce04152093cc61a7f2836cdcdff78 | 478 | 2024-06-25 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z Shaft Grounding Brushes A Outer Oil Deflector B 0.008 0.006 0.008 0; Inner & Outer Oil Deflectors ERP Proj. |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 337X711 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z Shaft Grounding Brushes A Outer Oil Deflector B 0.008 0.006 0.008 0.008 0.013 0.008 Hydrogen Seal Casing C 0.185 0.186 0.187 0.185 0.18
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 29c398c7cfdd4f1004e8a3f1cd3997c3 | 478 | 2024-06-25 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z Shaft Grounding Brushes A Outer Oil Deflector B 0.008 0.006 0.008 0; Inner & Outer Oil Deflectors ERP Proj. |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 337X711 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z Shaft Grounding Brushes A Outer Oil Deflector B 0.008 0.006 0.008 0.008 0.013 0.008 Hydrogen Seal Casing C 0.185 0.186 0.187 0.185 0.18
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 6ea78c1eefe449ae5bf5e1e3930bc2c3 | 435 | 2024-06-25 | Inspection | Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, Greasing, Wedge Tightness Test, Wedges | The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition.; Axial support hardware is performing as intended, aside from a single location that greasing was visible.; Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was present.; Even though greasing was present at the tie to connection ring locations globally as well as the bar-bar ties, no signs of blocking or tie looseness was found.; Single location at the 1 o’clock position was identified as having heavy greasing. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ Greasing ¦ Wedges | Part Condition: Fair Part Description: The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition. Axial support hardware is performing as intended, aside from a single location that greasing was visible. Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was present. These locations were retorqued to OEM spe
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | ec2ec155351eb5517099c9c54f023b39 | 434 | 2024-06-25 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, Hydrogen Seal Assembly, Wedge Tightness Test, Wedges | · Stator Wedge Tightness Test.; · Core Tightness check (Knife test). |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ Hydrogen Seal Assembly ¦ Wedges | On April 20, 2024, GE Vernova mobilized to Lamar Power Partners to perform a Major T&I on CT21 Generator S/N 337X711. This scope included: Generator: · Maintenance Electrical Testing. · Stator Wedge Tightness Test. · Core Tightness check (Knife test). · EL CID Field: · Maintenance Electrical Testing. · Hydrogen Seal Test of Collector Studs.
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | f35017dbd1ff3b05447e2440da629482 | 438 | 2024-06-25 | Electrical | Stator | DLRO; Polarization Index | 5 | DC Hipot, DC Leakage, DLRO, Polarization Index, Stator Winding | Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded.; Stator Winding Insulation Resistance / HV Proof Tests Date 04/23/2024 Generator No.:; Left (CE) Center (CE)Right (CE) Passed Passed Passed 21 21 62% 7FH2 Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is perfor; DC HIPOT RESULTS Current (Amps) Daniel Zarate Steve Brown I01-077685 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Humidity (%) Conditions During Insulation Resistance 3; Megger DLRO 513135 09/25/2024 Generator Test & Inspection 18.0 COMMENTS Thermal Setting (i.e. | TM2030, TM2050 | DLRO; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Condition: Good Part Description: Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded. These tests evaluate insulation integrity and GE has recommended values for proceeding to High Voltage testing or Return to Service. All results were satisfactory. Recommendation Description: Stator Winding Insulation Resistance / HV Proof Tests Date 04/23/2024 Generator No.: Prepared by: Equipment Year Select OEM GE Stator V
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 77f1b90329342596e7385f0efc7f2811 | 434 | 2024-06-25 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, Hydrogen Seal Assembly, Wedge Tightness Test, Wedges | · Stator Wedge Tightness Test.; · Core Tightness check (Knife test). |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ Hydrogen Seal Assembly ¦ Wedges | On April 20, 2024, GE Vernova mobilized to Lamar Power Partners to perform a Major T&I on CT21 Generator S/N 337X711. This scope included: Generator: · Maintenance Electrical Testing. · Stator Wedge Tightness Test. · Core Tightness check (Knife test). · EL CID Field: · Maintenance Electrical Testing. · Hydrogen Seal Test of Collector Studs.
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | 7a0fb07d7891014be1a7c2b6445bd74c | 438 | 2024-06-25 | Electrical | Stator | DLRO; Polarization Index | 5 | DC Hipot, DC Leakage, DLRO, Polarization Index, Stator Winding | Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded.; Stator Winding Insulation Resistance / HV Proof Tests Date 04/23/2024 Generator No.:; Left (CE) Center (CE)Right (CE) Passed Passed Passed 21 21 62% 7FH2 Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is perfor; DC HIPOT RESULTS Current (Amps) Daniel Zarate Steve Brown I01-077685 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Humidity (%) Conditions During Insulation Resistance 3; Megger DLRO 513135 09/25/2024 Generator Test & Inspection 18.0 COMMENTS Thermal Setting (i.e. | TM2030, TM2050 | DLRO; Polarization Index ¦ DC Hipot ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Condition: Good Part Description: Insulation Resistance (IR or Megger) and Polarization Index (PI) tests were completed per phase, with phases not under test grounded. These tests evaluate insulation integrity and GE has recommended values for proceeding to High Voltage testing or Return to Service. All results were satisfactory. Recommendation Description: Stator Winding Insulation Resistance / HV Proof Tests Date 04/23/2024 Generator No.: Prepared by: Equipment Year Select OEM GE Stator V
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | b6df5637d7d0c08452fc1eba56b64d42 | 435 | 2024-06-25 | Inspection | Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, Greasing, Wedge Tightness Test, Wedges | The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition.; Axial support hardware is performing as intended, aside from a single location that greasing was visible.; Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was present.; Even though greasing was present at the tie to connection ring locations globally as well as the bar-bar ties, no signs of blocking or tie looseness was found.; Single location at the 1 o’clock position was identified as having heavy greasing. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ Greasing ¦ Wedges | Part Condition: Fair Part Description: The Stator Core, End windings, including support system and hardware, Connection Rings, were visually inspected both for foreign object and overall condition. Axial support hardware is performing as intended, aside from a single location that greasing was visible. Recommendations were made to re-torque the axial support hardware system, however customer opted to address only the locations where greasing was present. These locations were retorqued to OEM spe
UNI036594, UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1718410_EV-131641_C-10378975_EVP-521582.pdf | 297258, 337X711 | Gas Turbine, Generator | e5110cb44ee1731e671489de001b3f54 | 471 | 2024-06-25 | Electrical |  | DLRO; Winding Resistance | 4 | AC Impedance, DLRO, Polarization Index, Winding Resistance | AC Impedance is a static test used to evaluate for shorted turns:; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.10 1.80 5.61 20.50 3.90 5.26 30.30 5.90 5.14 40.00 7.70 5.19 INSULATION RESISTANCE AT 500V (TM4030) 14.0 Time (min) R (megohms) 53.0% 0.50 6270 1 11420 FIELD WINDING RESISTANCE (TM4010) ; CAL Date 2253927 09/12/2024 513135 09/12/2024 2253611 09/12/2024 Reading Checks per TM4010 Previous Test Correct to 25 ºC Prior Test @25 ºC Historical Resistance Readings Instrument Description 7FH2 Number of Starts Factory (or Calculated) | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ AC Impedance ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | Part Condition: Good Part Description: AC Impedance is a static test used to evaluate for shorted turns: a step change between test intervals indicates a potential short, however, lack of step change is not definitive that there are no shorts. In service, flux probe testing at a variety of loads is the best evaluation for shorted turns. Results were satisfactory. Field Measurements Date Turbine No.: 297258 Prepared by: Equipment Generator No.: 337X711 Project ID: OEM FIELD IMPEDANCE (TM4020) Vol
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 24e79cec39513b943714274db648f237 | 263 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Shaft Grounding Brushes A NA NA NA NA Outer Oil Deflector B 0.005 0.008 0.006 0.006 0.016 0; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.054 0.048 0.058 0.054 0.063 0.060 Inner Oil Deflector K 0.009 NA 0.009 0.009 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . ST00078 GT2130 Sheet: (a) Rev 1.0 - 09/18/2019 GE Energy Proprietary Information Bearings Equip. Code: 7FA.04 Rotor Journal Condition Date Turbine S/N 338X726 Prepared by FSR # Data Type As Found Units of Measure: Inches Journal Number CE NOTE: Mark on sketch to show grooving, discoloration, carbon inclusions, or irregularities in the journal surface. Diameter 19.0045 Inner Oil Deflector 16.0030 16.0030 16.0030 16.0030 Outer Oil Deflector Diameter Inner Oil Deflector 19.0050 16.0050 16.0050 16
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | ebaa0936455113ab159cd2fe7ba140ec | 267 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.007 0.006 0.007 0.007 0.012 0.007 Hydrogen Seal Casing C 0.184 NA 0; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.056 NA 0.053 0.061 0.050 0.055 Inner Oil Deflector K 0.007 0.006 0.007 0.007 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 338X726 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.007 0.006 0.007 0.007 0.012 0.007 Hydrogen Seal Casing C 0.184 NA 0.182 0.184 0.185 0.185 Middle Oil Deflector D 0.012 NA 0.012 0.012 0
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 91a5798a6a77871eabb55b576d4a6a42 | 219 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA NA Shaft Grounding Brushes A NA NA NA NA NA NA Outer Oi; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J 0.061 NA 0.053 0.049 0.046 0.070 Inner Oil Deflector K 0.008 0.008 0.008 0.010 ; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA NA Shaft Grounding Brushes A NA NA NA NA Outer Oil Defl |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . The H2 seal casing is in overall good condition Cleaned Joints Dowels Insp per GN-2151 Top T. Left B. Left T. Right B. Right "A" Gap "A" Gap dimensions Bottom C A B B C D E AIR SIDE HYDROGEN SIDE OIL DEFLECTOR A ST00065 D316512 Sheet: (a) Rev 2.2 - 08/28/2018 Generator Field Clearance Equip Code: Turbine End As Found Date(m/d/y) 4.10.2024 Turbine Serial No. 298112 Prepared by Generator Serial No. 338X725 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbe
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 9415e45049523a334997af3d75f89a9c | 198 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J NA Inner Oil Deflector K 0.006 0.006 0.006 0.006 0.011 0.006 Middle Oil Deflect |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 'C' MEASUREMENTS (in.) TURBINE END COLL. END POSITION AIR HYD AIR HYD 2 TO 8 17.125 17.320 17.126 17.326 5 TO 11 17.125 17.320 17.124 17.326 AVERAGE 17.125 17.320 17.125 17.326 POSITION AIR HYD AIR HYD 3 0.010 0.009 0.009 0.009 4 0.010 0.009 0.009 0.009 9 0.010 0.009 0.009 0.009 10 0.010 0.009 0.009 0.009 COMMENTS 7FH2/H33 GE / APM English - inches As Found TURBINE END COLL. END OFFSET 'D' MEASUREMENTS (in.) Offset "D" Measurement: Measure the offset distance in two locations on each piece of
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | cac32ef7f78852a4d121b44ab1ba65f2 | 223 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fan Blade J NA Inner Oil Deflector K 0.006 0.006 0.006 0.006 0.011 0.006 Middle Oil Deflect |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 298112 Prepared by Generator Serial No. 337X725 ERP Project ID Units recorded in Data set Notes: 1) Coupling should be the the cold setting when reading is taken. The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Fa
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 049eacaee17835c47ceb65d351e643f5 | 177 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | BRUSH RIGGING AS FOUND BRUSH RIGGING INSTALL 2 BRUSH RIGGING INSTALL CE DISASSEMBLY CE END SHIELD INSTALL BUS BAR INSTALL 2 CE DISASSEMBLY 2 CE BEARING PINCH CHECK CE BEARING PINCH CHECK 2 BUS BAR INSTALL CE EYEBROW ASSEMBLY CE EYEBROW INST; GE/APM Above are the final measurements for the new generator oil deflectors. |  | Oil Deflector Alignment ¦ Collector Rings ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Inspection Type: Visual, Dimensional Part Condition: Good Part Description: The collector end was completely disassembled for the removal of the field. The T4 bearing was sent out for NDE but the babbet was not re-poured or machined. See below for measured dimensions, NDE report, and photos. The T4 bearing was meggered to test the insulation and initially failed. The bearing was disassembled, wiped, reassembled, and tested with positive results. New hydrogen seals, inner oil deflector, mid oil d
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 33f534c60c6830f9923ebdeb8f758786 | 230 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | . END Enter design ID from seal ring drawing in appropriate fields below for measurement evaluation (Rules 1-3) to work. Babbitted Steel–Bolted/Scavenging/2 Pole (<20 in. shaft dia.) Ex. 7FH2 324 GE / APM 7FH2/H33 English - inches As Found 4/21/2024 298113 338X726 LENGTH (±1/16 in.) WIRE DIA. GRADIENT (#/in.) 120E9005G0009 RULE 2 RULE 1 120E8988G0009 Seal ID per Dwg - CE AIR HYD COIL DIA. 5 6 AVERAGE ACTUAL SHAFT DIA. CLEARANCE POSITION 1 2 3 4 TE Seal Ring Part Number CE Seal Ring Part Number H
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 85959045c8ffcecd9372b0687188d0db | 200 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. “UNCONTROLLED” As-Found Journal Bearing Inspection Report ISO 9001 Registered Licensee of: Siemens Energy, Inc. Description: Numbers stamped on face: GT2 CE 16” Turbine 111E5592 O.D. Measurements: Job End: Opposite Job End: Deviation From Nominal: H: 32.000” H: 31.998” H: 32.000” H: 31.999” V: 32.000” V: 32.000” • .003”-.004” Deviation the customer needs contacted. • If .005 or more deviation the customer sho
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 49fa80d20bed0409ec936c8995af1b38 | 196 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 4 | Collector Rings, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  | EM2101 | Oil Deflector Alignment ¦ Collector Rings ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM2101 | . 298112 Prepared by Equipment Generator Serial No. 338X725 Units INSPECTIONS & CHECKS CODE X X Work Carried Out X N Not Done X NA Not Applicable C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Air Hydrogen Average 'A' GAP DIMENSIONS (inches) LOCATION PINS IN PINS OUT Top Left 1.641 Top 1.640 Top Right 1.640 Bottom Left 1.641 Bottom 1.640 Bottom Right 1.640 Average 1.640 Stack Check Validation JOINT STEP CHECK (inches) LOCATION LEFT RIGHT "B" .0000 .0000 "C" .0000
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | ac05a6b91dede78a8b3f579cb2a5d2dc | 201 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | AS FOUND T3 BEARING 3 END SHIELD REINSTALL AS FOUND T3 BEARING 2 END SHIELD RTV (2) AS FOUND T3 BEARING BEARING CAP SEALANT DOW CORNING PUMPING END SHIELD RTV GROUNDING STRAP GAS TE H2 SEAL CONTACT CHECK H2 SEAL CASE LIFT OIL LINE CONNECTED | EM3406 | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3406 | Part Description: The collector end was completely disassembled for the removal of the field. The T3 bearing was sent out for NDE but the babbet was not re-poured or machined. See below for measured dimensions, NDE report, and photos. Documented scoring was found in T3 bearing babbet, customer elected to reinstall bearing. New hydrogen seals, inner oil deflector, mid oil deflector, and outer oil deflector installed. Data sheets are attached below. See photos below for installation and applicatio
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 908bc4841eea1532cd4158bf1b391994 | 27 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | Clearance checks were performed on T1 bearing liner, seals rings, and oil deflectors upon closure, and results were verified against the unit clearance diagram.; Opening feeler-check measurements were not recorded for the floating end seal rings of the journal/thrust bearing (1S7-1S10).; These seal rings were removed and sent out with the bearings for refurbishment. | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ EM5260 | Inspection Type: Visual, Dimensional Part Condition: Good Part Description: Upon removal of the inlet bellmouth, the T1 bearing instrument ports, the bearing casing horizontal joint, and the bellmouth horizontal joint were checked for signs of oil leakage. Oil was discovered in the bearing cavity before the air seal, resulting in a dimensional clearance check of the adjacent oil and air seals. In reference to their design dimensions, these seals were found to be on the higher end of their tolera
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | b93112d9407881113223b81327a2b57e | 195 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 001 Page ¦ 1 Hanging Rock Facility GT2 Balance Weight Groove Entry Slot Inspection Executive Summary: A visual inspection was conducted on the Balance Weight Groove (BWG) entry slots. These slots allow for balance weights to be installed into the balance planes at the compressor aft shaft (CAS) and the distance piece (DP). TIL-2284 describes the importance of machine blending the entry slot to reduce localized stress and the risks associated with disregarding these recommendations. A common ri
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 318c100281c4c8734fd4e90cf6eb086d | 234 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . • If .005 or more deviation the customer should consider OD restoration. (needs approved by customer) I.D. Measurements: Job End: Opposite Job End: Rings: H: 16.039” H: 16.037” 16.038” 16.037” H: 16.041” H: 16.042” 16.040” 16.040” V: 16.021” V: 16.022” 16.021” 16.022” Gap between horizontal joints: Minimum: Maximum: .000” .001” Alignment Pins: (less than .002” loose is acceptable) Pin OD: Hole ID: Deviation: U/H: .747” U/H: .750” U/H: .748” U/H: .752” L/H: .749” L/H: .752” L/H: .750” L/H: .752
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 8e7332f0e70f869217be754c215f28e9 | 28 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings |  |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | Inspection Type: Visual Part Condition: Good Part Description: Bearing pads are newly machined and within specification. A new bearing was received from another Vistra site to use in 298112. After satisfactory measurements were taken, sealant was applied to the T1 bearing cap and the cap was installed. New TC's were installed and Nichrome welded in place while being routed accordingly. The original tilt pad bearing was out for repair at the customers discretion. A new aft air/oil seal was instal
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | ae0ccdf607624e21c712a1ba276d44b9 | 224 | 2024-06-13 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 3 | Collector Rings, Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Collector Rings ¦ Oil Deflectors | Inspection Type: Visual Part Condition: Good Part Description: Field was pulled from generator and inspected by generator specialist. Detailed report included in appendix. See below for report on terminal stud replacement and photos of field during removal process. Field journals were measured and data is recorded below. FIELD INSTALL 3 FIELD INSTALL 4 FIELD INSTALL 2 FIELD INSTALL 5 FIELD INSTALL FIELD INSTALLED TO EYEBROW FIELD INSTALL 6 FIELD PULL 5 FIELD PULL 6 FIELD PULL 8 FIELD PULL 4 FIEL
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 3ef91aa1a61bc7b205de2ab88355a49f | 139 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | EM2015 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM2015 | Inspection Type: Visual Part Condition: Good Part Description: New bearings were used from customer stock and within specification to be installed in the unit. T2 bearing clearances were recorded and are provided below. New thermocouples were installed and nichrome welded in place, along with new lift oil lines. GEGEGE GE Vernova Confidential and Proprietary Information. Not to be copied, reproduced or distributed without GE Vernova prior written consent. T2 Bearing As Found GEGEGE GE Vernova Co
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | d23e3b18616897bfeae9da4a307eab3a | 10 | 2024-06-13 | Inspection | Stator | Stator Findings Review | 2 | End-winding, Greasing | 1460-2 - 7FA, 9FA, 7FB, AND 9H GAS TURBINE ENCLOSURE CRANES (MLI-1648) RE- GREASING / STORAGE Enclosure cranes were removed, the customer rebuilt, then GE reinstalled | GEK 110806 | Stator Findings Review ¦ End-winding ¦ Greasing ¦ GEK 110806 | General Electric (GE) mobilized to Hanging Rock Energy Facility in Ironton, Ohio on April 1st. LOTO was granted and work on the unit commenced April 6th. The work scope comprised of a turbine rotor out major inspection and generator rotor out major inspection. Numerous extra work additions (EWA's) were submitted, completed and are listed below. Shift personnel entailed a GE Vernova Field Engineer (FE), an APM crew of 15 Millwrights (MW), and 1 superintendent to complete the scope. Work on 298113
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | d3e555fa538b801f1d805183ccc604b0 | 361 | 2024-06-13 | Inspection | Field, Stator | Focused Generator Review | 2 | Fan Blades, Wedges | GT2 Rotor & Casing Blends, Fan Blades, Thrust Pads, Coupling Bolts, IBH Welds, Weldolets At your request, 3angles, Inc.; FCSS 4200 Wildwood Parkway, Atlanta, GA 30339 PRELIMINARY _Components Report_Cover Sheet 3A-NDE-0000P_R16_020624 NDT REPORT OF GT2 Rotor & Casing Blends, Fan Blades, Thrust Pads, Coupling Bolts, IBH Welds, Weldolets DATES OF EXAMINATIONS 04 |  | Focused Generator Review ¦ Fan Blades ¦ Wedges | . S/N: 19-10706 DELAY: 1.025 µs MATERIALS / EQUIPMENT UT SCOPE: COUPLANT Model: Olympus Epoch 650 S/N: 190999812 CAL DUE: 12/14/2024 Ultragel CAL BLOCK: DSC: S/N: 3134 21 MATERIAL VELOCITY: 0.2312 inch/µs TRANSDUCER: SHEAR WEDGE: MFG: DELAY: µs LINEARITY PERFORMED: YES INSPECTION RESULTS COMPONENT/ LOCATION REFERENCE dB SCANNING dB NUMBER LENGTH (in) DIAMETER (in) DATE TESTED FINDINGS GE Bolting (16) 38.6 44.9 16 10 2.5 4/25/2024 No indications TE Bolting (18) 43.4 49.4 18 10.25 2.125 4/25/2024
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 7314c826215f3c694a9b011b3c026f3f | 29 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The nominal design clearance is 51 to 56 mils.; The minimum, average, and maximum as-found clearances were 45 mils, 32 mils, and 54 mils, respectively.; The nominal design clearance is 46 to 51 mils.; The minimum, average, and maximum as-found clearances were 56 mils, 54 mils, and 57 mils, respectively. | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | . 1S2 1S7* LOADED THRUST FACE 1S8* 1S9* 1S3 1S4 1S5 1S6 1S10* CL INSPECTION REPORT Gas Turbine Maintenance GT2025 Sheet: (a) Rev 3.0 - 06/28/2020 GE Proprietary - Non Public Bearings Bearing & Seal Clearances, No. 1 Date Turbine S/N 298113 Prepared by FSR # Photos Enclosed? Yes Sketches Enclosed? Yes Units of Measure Inch • All views with turbine flow. Left Right Top Sum (L / R) Left Right Top Sum (L / R) 1S1 0.024 0.026 0.000 0.000 1S2 0.025 0.025 0.000 0.000 1S3 0.027 0.026 0.000 0.000 1S4 0.0
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 5ce8a4a68772873f69ed652c8fd3c5ba | 31 | 2024-06-13 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The minimum, average, and maximum as-found clearances were 56 mils, 54 mils, and 57 mils, respectively.; The nominal design clearance is 51 to 56 mils.; The minimum, average, and maximum as-found clearances were 54 mils, 52 mils, and 58 mils, respectively.; The nominal design clearance is 50 to 57 mils.; The minimum, average, and maximum as-found clearances were 56 mils, 53 mils, and 59 mils, respectively. |  | Oil Deflector Alignment ¦ Oil Deflectors | . The minimum, average, and maximum as-found clearances were 56 mils, 54 mils, and 57 mils, respectively. This oil seal was deemed suitable for continued service. #1 Aft-2: The design diameter of the #1 bearing housing aft-2 oil seal is 18.5535" ± 0.0025". The nominal design clearance is 51 to 56 mils. The minimum, average, and maximum as-found clearances were 54 mils, 52 mils, and 58 mils, respectively. This oil seal was deemed suitable for continued service. Inlet Air Deflector: The design dia
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 4bfd57e51f70d5d60d205aa59c2a3d1d | 9 | 2024-06-13 | Inspection | Stator | Stator Findings Review | 2 | End-winding, Greasing | 1460-2 - 7FA, 9FA, 7FB, AND 9H GAS TURBINE ENCLOSURE CRANES (MLI-1648) RE- GREASING / STORAGE Enclosure cranes were removed, the customer rebuilt, then GE reinstalled. | GEK 110806 | Stator Findings Review ¦ End-winding ¦ Greasing ¦ GEK 110806 | General Electric (GE) mobilized to Hanging Rock Energy Facility in Ironton, Ohio on April 4th. LOTO was granted and work on the unit commenced April 5th. The work scope comprised of a turbine rotor out major inspection and generator rotor out major inspection. Numerous extra work additions (EWAs) were submitted, completed and are listed below. Shift personnel entailed a GE Vernova Field Engineer (FE),an APM crew of 15 Millwrights (MW), and 1 superintendent to complete the scope. Work on 298112 w
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 3011cf64455ecdeb65babd8e2bc634e4 | 15 | 2024-06-13 | Inspection | Field | Field Findings Review | 2 | Collector Rings, Greasing | with that said there are some connection ring block with moderate to heavy greasing and the same with some bar ties.; Cut the tie on the blocks with heavy greasing and see if the blocks are loose.; ER-20240418-1788 When performing measurements on the collector rings it was found that in some locations of where readings were taken per the data sheet we have a difference of .025 which is well above the recommended allowable per the GEK. | ER-20240418-1788, ER-20240420-0153, ER-20240420-0157, ER-20240420-0251, ER-20240421-0273, ER-20240421-0289 | Field Findings Review ¦ Collector Rings ¦ Greasing ¦ ER-20240418-1788 ¦ ER-20240420-0153 | . Speaking with CPM & customer, it is being agreed that GE and customer would split costs as the onus of the discrepancy shall be borne by both parties. ER Cases submitted: ER-20240420-0251 I&LES has performed Visual inspections and FPI of the lockwire tabs and balance weight grooves. During the visual inspection rubs were noted on the 1-2 spacer. The report documenting the inspection is attached. It is recommended to use scotch-brite or fine grit sand paper to remove any and all high spot metal
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 779faf75b2b68e92dd7a1eb5f938265c | 366 | 2024-06-13 | Inspection | Field | Focused Generator Review | 1 | Fan Blades | GT2 CE Fan Blades (24) LIQUID PENETRANT INSPECTION CUSTOMER:; COLOR CONTRAST FLUORESCENT SOLVENT REMOVABLE WATER WASHABLE 3A-NDE-0000P_R16_020624 _Components Report_Liquid Penetrant Testing INSPECTION RESULTS A visible solvent removable penetrant test was performed on the GT2 CE Fan blades and yielded |  | Focused Generator Review ¦ Fan Blades | . fc. X X Member of ASNT * SNT - TC - 1A Certified Technicians CF-6925 4/18/2024 PO #: 4900377715 SURFACE CONDITION: In Service / Cleaned PROCEDURE/S: 3A-NDE-3000 REV 9 ACCEPTANCE STD: Report Findings MATERIAL DESCRIPTION: GT2 CE Fan Blades (24) LIQUID PENETRANT INSPECTION CUSTOMER: FCSS JOB SITE: Hanging Rock Energy Facility Magnaflux SKL-SP2 / 22J07C MATERIALS / EQUIPMENT CLEANER/REMOVER MFG / BATCH: Magnaflux SKC-S / 22L01C / 23C03C / 20A01C PENETRANT MFG / BATCH: OTHER MATERIALS: n/a BLACKLI
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 0b8804b685d403d077eb1749c489bc1f | 376 | 2024-06-13 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . NDT Technician: Joseph Glogan MT, PT, VT II Overview photo of parts of NDT Technician: Job Number: CF-6925 Date: 4/20/2024 Page: 15 25 PO #: 4900377715 SURFACE CONDITION: In Service / Cleaned MATERIAL DESCRIPTION: GT2 Active Thrust Pads (14) CONTINUATION SHEET CUSTOMER: FCSS JOB SITE: Hanging Rock Energy Facility Pad 11 scratching Mechanical damage pad 11 Pad 7 mechanical damage Uneven wear example pad 11 overview Mechanical damage pad 11 Mechanical damage pad 10 Scratching pad 3 Scratching pa
UNI035962 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633204_EV-124343_C-10366903_EVP-515929.pdf | 298113 | Gas Turbine | 2fd0e764578d8c05fe005abfcc45f657 | 367 | 2024-06-13 | Inspection | Field | Focused Generator Review | 1 | Fan Blades | GT2 CE Fan Blades (24) CONTINUATION SHEET CUSTOMER:; GT2 TE Fan Blades (24) LIQUID PENETRANT INSPECTION CUSTOMER:; COLOR CONTRAST FLUORESCENT SOLVENT REMOVABLE WATER WASHABLE 3A-NDE-0000P_R16_020624 _Components Report_Liquid Penetrant Testing INSPECTION RESULTS A visible solvent removable penetrant test was performed on the GT2 TE Fan blades and yielded; GT2 TE Fan Blades (24) CONTINUATION SHEET CUSTOMER:; GT2 Collector Fan Blades (26) LIQUID PENETRANT INSPECTION CUSTOMER: |  | Focused Generator Review ¦ Fan Blades | of NDT Technician: Job Number: CF-6925 Date: 4/18/2024 Page: 5 25 PO #: 4900377715 SURFACE CONDITION: Hand Cleaned MATERIAL DESCRIPTION: GT2 CE Fan Blades (24) CONTINUATION SHEET CUSTOMER: FCSS JOB SITE: Hanging Rock Energy Facility Example of mechanical damage found on mounting base Example of mechanical damage found on mounting base Example of mechanical damage found on mounting base Example of mechanical damage found on mounting base Joseph Glogan MT, PT, VT II Member of ASNT * SNT - TC - 1A
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 38603b73e6a3c73a5aff1124fc879b6f | 320 | 2024-06-13 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . / BATCH: MATERIALS / EQUIPMENT PARTICLES: DRY - COLOR: RED WET FLUORESCENT COLOR: BLACK BLACKLIGHT: READING: µW/cm2 WHITELIGHT METER: Spectroline AccuMAX XRP-3000 S/N: 2181101/2 CAL DUE: 07/23/24 MAGNETIC PARTICLE BATH CONCENTRATION: n/a BLACKLIGHT METER: Spectroline AccuMAX XRP-3000 S/N: 2181101/2 CAL DUE: 07/23/24 BLACKLIGHT: TATTU U3S S/N: 881 READING: 5936 µW/cm2 WHITELIGHT: AT SURFACE PART FLASHLIGHT: Zebralight SC64c LE READING: 228.2 WHITELIGHT: AT SURFACE PART FLASHLIGHT: READING: 0.76
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 8ef139fecb40e575c8a5d283a62576f6 | 313 | 2024-06-13 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | . NDT Technician: Joseph Glogan MT, PT, VT II Overview photo of (8) Inactive Thrust Pads of NDT Technician: Job Number: CF-6924 Date: 4/22/2024 Page: 17 25 PO #: 4900378003 SURFACE CONDITION: In Service / Cleaned MATERIAL DESCRIPTION: GT1 Inactive Thrust Pads (8) CONTINUATION SHEET CUSTOMER: FCSS JOB SITE: Uneven wear found on all pads Longitudinal scratching found on all pads Deeper scratching on pad D Pad H overview Deeper scratching on pad H Deeper scratching pad H Pad D overview Pads develop
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | f4ccfd1d03792afd9a2b566f7f3673f6 | 305 | 2024-06-13 | Inspection | Field | Focused Generator Review | 1 | Fan Blades | X X Member of ASNT * SNT - TC - 1A Certified Technicians 3A-NDE-0000P_R16_020624 _Components Report_Liquid Penetrant Testing INSPECTION RESULTS A visible solvent removable penetrant test was performed on the collector fan blades (26) and yi; GT1 Collector Fan Blades (26) CF-6924 4/21/2024 Overview photo of parts of NDT Technician:; GT1 Collector Fan Blades CONTINUATION SHEET CUSTOMER: |  | Focused Generator Review ¦ Fan Blades | . fc. X X Member of ASNT * SNT - TC - 1A Certified Technicians 3A-NDE-0000P_R16_020624 _Components Report_Liquid Penetrant Testing INSPECTION RESULTS A visible solvent removable penetrant test was performed on the collector fan blades (26) and yielded the following results: -FOD on trailing edge of blade # 2, 6, 7, 8, 9, 18, 20, 23, 22, 15, 21, 24 -FOD exhaust side face blade # 10, 14, 20, 11, 16, 17 -Mechanical damage to admission side top edge # 1 -Mechanical damage to all mounting bases Pictu
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 0072801f0d7960e096e9f0841621411d | 34 | 2024-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Opening feeler-check measurements were recorded for the floating end seal rings of the journal/thrust bearing (1S7-1S10).; These seal rings were removed and sent out with the bearings for refurbishment. |  | Focused Generator Review ¦ Seal Rings | . Max. Min. Max. Min. Max. Min. Max. 1S1 0.022 0.034 0.022 0.034 0.032 0.038 1S2 0.022 0.034 0.022 0.034 1S3 0.016 0.032 0.016 0.032 1S4 0.018 0.036 0.018 0.036 1S5 0.018 0.036 0.018 0.036 0.020 0.040 1S6 0.018 0.036 0.018 0.036 1S7* 0.006 0.016 1S8* 0.006 0.016 1S9* 0.005 0.013 1S10* 0.005 0.013 1WF1 0.022 0.034 0.022 0.034 T1 0.013 0.017 These opening oil seal/deflector radial clearances were measured after removing the #1 journal/thrust bearing cover. All as-found oil seal/deflector radial cl
UNI035961 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1633202_EV-116831_C-10366904_EVP-515928.pdf | 298112 | Gas Turbine | 8c68adcd834e0ebd06c9b4b759e99087 | 297 | 2024-06-13 | Inspection | Field | Focused Generator Review | 1 | Fan Blades | GT1 Rotor Blends, Casing Blends, Thrust Pads, Coupling Bolts, Fan Blades, IBH Welds, Weldolets At your request, 3angles, Inc.; 2024.05.16 09:41:38 -04'00' _Components Report_Cover Sheet 1395 County Road 1A Ironton, OH 45638-8699 3ANGLES JOB NUMBER Member of ASNT * SNT - TC - 1A Certified Technicians CF-6924 3A-NDE-0000P_R16_020624 NDT REPORT OF GT1 Rotor Blends, Ca; X X Member of ASNT * SNT - TC - 1A Certified Technicians 3A-NDE-0000P_R16_020624 _Components Report_Liquid Penetrant Testing INSPECTION RESULTS A visible solvent removable penetrant test was performed on the CE Generator fan blades and yiel |  | Focused Generator Review ¦ Fan Blades | . Visual inspection showed damage on the face. Investigation Visual Aids Job Site: Site Address: Dear Mr. Jason Callahan Sincerely, Joseph Glogan MT, PT, VT II 2 Access Rd. Albany, NY 12205 (518) 640-3000 (Office) (518) 218-0490 (Fax) info@3anglesndt.com www.3anglesndt.com FCSS 4200 Wildwood Parkway, Atlanta, GA 30339 Findings reported in the enclosed document are provided for informational purposes only. Any determinations, actions, recommendations or dispositions should be made by engineering
UNI000886 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1874366_EV-166829_EVP-543930.pdf | 270T259 | Steam Turbine | 06a9a269015a156e9e5afb9c442864a9 | 5 | 2024-06-05 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | T4 and TG oil deflectors were replaced with new. |  | Oil Deflector Alignment ¦ Oil Deflectors | Dynegy Independence Station, Unit ST-6, 270T259, was forced offline for high T4 bearing metal temperatures. On 4/16/2024, GE signed on LOTO to investigate and repair the unit. As found condition: T4 bearing cover was removed, rotor positions were measured, the rotor was found to be sitting 0.058” lower than the as-built data from 2023 major inspection. T4 bearing was rolled out and found to be wiped. T4 oil deflector and turning gear oil deflector were also found to be heavily damaged on the bot
UNI000886 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1874366_EV-166829_EVP-543930.pdf | 270T259 | Steam Turbine | e44f4d66e6707ced276f799079b2aa02 | 9 | 2024-06-05 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | 270T259 Prepared by Dejewski BEARING Lead Average Shim Used Mandrel DIA Journal DIA Wire A B C TE 0.006 0.006 0.004 Center 0.005 0.005 0.005 0.006 0.010 16.026 15.998 T5 UH Left GE 0.005 0.008 0.009 0.024 mils 1.49 mils/inch BEARING Lead Av |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Description: • T4 Bearing was found wiped, and was sent for spin cast repair at APS. Once received back from repair, the bearing was visually inspected and found to be free of debris. Bearing dimensions were checked after repair and found to be satisfactory. • All bearings were rolled out for inspection, looking for foreign material or bearing damage. The pads of all the tilt pad journal bearings were removed cleaned and inspected. • Rubber gasket material was found in T4 oil feed orifice a
UNI000886 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1874366_EV-166829_EVP-543930.pdf | 270T259 | Steam Turbine | 4f85a32ecab76834c75f5b7bb16bc7c2 | 30 | 2024-06-05 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | T2 and T3 oil deflectors were not disturbed during the outage, alignment was measured, but the rotor was not centered at the time.; T4 and TG oil deflectors were found heavily damaged from rubbing on bottom.; T5 and T6 outer oil deflectors were removed as part of the bearing removal process.; The T5 and T6 outer oil deflectors were later re-installed and aligned during final assembly.; New Oil Deflectors A B B A C C D309301 Sheet: |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Description: T1 oil deflector was removed as part of the T1 bearing removal process. It was later re- installed and re-aligned with the rotor centered in the float of the tilt pad bearing. T2 and T3 oil deflectors were not disturbed during the outage, alignment was measured, but the rotor was not centered at the time. T4 and TG oil deflectors were found heavily damaged from rubbing on bottom. They were replaced with new, and aligned during final assembly. T5 and T6 outer oil deflectors were
UNI000886 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1874366_EV-166829_EVP-543930.pdf | 270T259 | Steam Turbine | d113263a50ff4424bddbb2ad03d1cbd2 | 2 | 2024-06-05 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | INDEPENDENCE POWER STATION 3.1.3 Oil Deflectors __________ 27 3.2 Lubrication System __________ 32 3.2.1 Lube Oil System __________ 32 4 Appendix __________ 36 4.1 Attachments __________ 36 GEGEGE GE Vernova Confidential and Proprietary Inf |  | Oil Deflector Alignment ¦ Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 2 1.3 EHS __________ 3 1.4 Quality __________ 3 STEAM TURBINE (270T259 ¦ SY0052322) __________ 4 1 Summary __________ 4 1.1 Work Scope __________ 4 2 Technical __________ 5 2.1 Recommendations __________ 5 3 Turbine __________ 6 3.1 Bearings __________ 6 3.1.1 Journal Bearings __________ 6 3.1.2 Thrust Bearing __________ 25 GEGEGE GE Vernova Confidential and Propr
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 048edcb46acb6e26891ae158d1fe6252 | 214 | 2024-05-31 | Electrical | Field, Stator | Polarization Index; DC Leakage | 10 | AC Impedance, Belly Bands, Belly band inspection, Core, DC Leakage, End-winding, Field Body, MAGIC Inspection, Polarization Index, Wedges | • Minor end-winding support system repairs were performed.; • No loose stator wedges were detected.; • Visual / MAGIC inspection was satisfactory.; 2 Technical 2.1 Recommendations Stator Core / Laminations Next Outage Services Track & Trend.; Stator Core - Belly Band Inspection Next Outage Services Track & Trend. |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ Belly Bands ¦ Belly band inspection ¦ Core ¦ DC Leakage ¦ End-winding | . • Minor end-winding support system repairs were performed. • No loose stator wedges were detected. (Via MAGIC Insp.). • Electrical testing was satisfactory. • This Generator was found to have good amounts of oil in its belly area (in the cooler area). Major Inspection (Robotic) - 337X009 DYNEGY INC. 1.1 Generator Executive Summary FIELD: • Visual / MAGIC inspection was satisfactory. • Baseline electrical test results were satisfactory. INSTRUMENTATION: • RTD’s electrical tests were satisfactor
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | d8fd09041a7225e9bba2e24732d98c9b | 426 | 2024-05-31 | Inspection | Field, Stator | Wedge Tightness Test | 9 | Core, Focused Generator Inspection, High Voltage Bushings, Lamination Damage, MAGIC Inspection, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges | Stator/Core Core Laminations Foreign object damage, hot spots, evidence of movement X X Space Blocks Migration, cooling passage blockage X X Gas Gap Baffle Studs Cracked welds, looseness X X Stator Wedges Looseness, loss, sparking damage X ; Generator in-situ inspection capabilities provide the specialist with a clear view of the sta- tor core laminations, stator wedges, field wedges and surface on the inboard ends of the retaining rings.; Figure 4 is a picture of some repaired core damage using both the wide angle and close up cameras on the MAGIC robot.; Stator Wedge Tightness Assessment The Stator Wedge Tightness Test is offered as an option to the MAGIC visual generator inspection.; Loose wedges and the resulting stator bar movement are major contributors to premature stator winding damage and failure. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ High Voltage Bushings ¦ Lamination Damage ¦ MAGIC Inspection ¦ Retaining Rings | . Inspection capabilities Component Common Problems MAGIC Visual RAC Visual Wedge Tapping EL-CID RR NDE Capac- itance Clearance Meas. Stator/Core Core Laminations Foreign object damage, hot spots, evidence of movement X X Space Blocks Migration, cooling passage blockage X X Gas Gap Baffle Studs Cracked welds, looseness X X Stator Wedges Looseness, loss, sparking damage X X Stator Bars Foreign object damage, sparking, girth cracks, movement X X X Wet groundwall insulation X End Windings Bar movem
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | c99e89f5b4de922d4994b7b6e9d7865a | 428 | 2024-05-31 | Inspection | Field, Stator | Wedge Tightness Test | 8 | Core, Field Body, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges | A highly sensitive, miniaturized sensing coil, or chattock, is used along the core surface to detect fault currents which will result from core insulation damage.; EL-CID has been proven to be espe- cially valuable on machines where core loosen- ing has been more prevalent.; Stator Clearance Measurement Radial clearance between the stator winding and core permit unwanted motion of the stator bars during operation.; As a result, GE recommends measuring the actual clearance between the stator bars and the bot- tom of the core slot through a stator clearance test.; Clearance testing involves applying a force on each stator bar where it exits the core slot, and accurately measuring its radial movement. |  | Wedge Tightness Test ¦ Core ¦ Field Body ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Stator Winding | . A highly sensitive, miniaturized sensing coil, or chattock, is used along the core surface to detect fault currents which will result from core insulation damage. A signal processor located in the control system computer is used to measure, record and report these faults. EL-CID has been proven to be espe- cially valuable on machines where core loosen- ing has been more prevalent. Stator Clearance Measurement Radial clearance between the stator winding and core permit unwanted motion of the st
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 1ccd9f64e8bd46e67d8af3dde58e9390 | 434 | 2024-05-31 | Inspection | Field, Hydrogen Seals, Stator | Wedge Tightness Test; Oil Deflector Alignment | 8 | Focused Generator Inspection, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Retaining Rings, Wedge Tightness Test, Wedges | removal of the bearings, hydrogen seals, oil deflectors and exciter assemblies;; Closeup, detailed views of the core and rotor surfaces, stator and rotor wedges, retaining ring tips and vent ducts allow a generator specialist to detect and assess potential problems not generally dis- cernible by electrical testing or ot |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Focused Generator Inspection ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Retaining Rings | . Not removing the field from the genera- tor also frees up overhead crane availability for use on other parts of the outage. The total cost of field removal and reassembly is reported at $100,000 to $250,000 for fossil plants and $250,000 to $500,000 for nuclear plants. The cost associated with partial disassembly to allow in-situ inspection varies with the scope of the inspection but, generally, runs about 1/3 the cost of complete disassembly. Table 3 compares the cost of a traditional vs. in-
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | d782f5a9a176d89495580932ed6e8707 | 209 | 2024-05-31 | Electrical | Field, Stator | Polarization Index; DC Leakage | 8 | AC Impedance, DC Leakage, End-winding, Field Body, MAGIC Inspection, Polarization Index, Stator Winding, Wedges | INDEPENDENCE POWER STATION Page 204 of 433 3.1.6 Stator Wedge Map via MAGIC Inspection __________ 20 3.1.7 MAGIC Inspection __________ 23 3.2 Stator Electrical Tests __________ 80 3.2.1 Armature Winding Copper Resistance Test __________ 80 ; INDEPENDENCE POWER STATION Page 205 of 433 3.4 Field Visual Inspection __________ 96 3.4.1 Field Body __________ 96 3.4.2 Field Wedges __________ 97 3.4.3 Vent Holes __________ 97 3.5 Field Electrical Testing __________ 98 3.5.1 Winding Cop |  | Polarization Index; DC Leakage ¦ AC Impedance ¦ DC Leakage ¦ End-winding ¦ Field Body ¦ MAGIC Inspection ¦ Polarization Index | . Not to be copied, reproduced or distributed without GE Vernova prior written consent. Major Inspection (Robotic) - 337X009 DYNEGY INC. INDEPENDENCE POWER STATION Page 204 of 433 3.1.6 Stator Wedge Map via MAGIC Inspection __________ 20 3.1.7 MAGIC Inspection __________ 23 3.2 Stator Electrical Tests __________ 80 3.2.1 Armature Winding Copper Resistance Test __________ 80 3.2.2 Armature Insulation Resistance with Polarization Index (PI) Test __________ 82 3.2.3 DC Leakage Test __________ 84 3.
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | fe0daa9e33e7981912b2839ad1dc612a | 336 | 2024-05-31 | Electrical | Stator | Polarization Index; DC Leakage | 8 | Core, DC Hipot, DC Leakage, End-winding, High Voltage Bushings, Polarization Index, Stator Winding, Wedges | Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) ; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In 1 DC Leakage and Partial Discharge testing are optional but high; 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 5 This test does not apply to units with asphalt stator windings, GVPI windings (Global Vacuum Pressure Impregnated) or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds. |  | Polarization Index; DC Leakage ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ High Voltage Bushings ¦ Polarization Index | . Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) Stator Winding Contamination and/or deterioration of insulation X X X 6 X X X DC Leakage Current Stator Winding Contamination and/or deterioration of insulation X X X 6 O 1 X X Endwinding Tightness Check 8 Endwinding support rods Torque measurement X X X X W
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | a9a3ee4f53ceaf1c2828b460fc31b0d9 | 116 | 2024-05-31 | Inspection | Field, Stator | Wedge Tightness Test; Generator Pressure Test | 7 | End-winding, Fan Blades, Generator Pressure Test, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | MM 4/24/24, 3:22 AM GMT-4 AP 4/24/24, 3:22 AM GMT-4 N 4/24/24, 3:22 AM GMT-4 73 7FH2- 313.4.5 CE Install Upper Half Fan Blades - 7FH2 - Quality Checks Collector End Fan Blade QC Complete. |  | Wedge Tightness Test; Generator Pressure Test ¦ End-winding ¦ Fan Blades ¦ Generator Pressure Test ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedge Tightness Test | . MM 4/24/24, 3:22 AM GMT-4 AP 4/24/24, 3:22 AM GMT-4 N 4/24/24, 3:22 AM GMT-4 73 7FH2- 313.4.5 CE Install Upper Half Fan Blades - 7FH2 - Quality Checks Collector End Fan Blade QC Complete. MM 4/24/24, 3:23 AM GMT-4 AP 4/24/24, 3:23 AM GMT-4 74 QC 75 7FH2- 400.9.1 Perform Generator Air Test - Clean Up Pressure decay test is complete and unit is ready for service - record final leak rate values for both Air and Hydrogen. Initial MM AP PC AT AT1 AT2 W N Adam T Adam Therrien Weak NA Full names and
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 3c287eee77ee0228a5b17e549b0bf510 | 334 | 2024-05-31 | Inspection | Hydrogen Seals, Stator | Wedge Tightness Test | 7 | End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Stator Winding, Wedge Tightness Test, Wedges | Partial Discharge 1 Stator Winding Insulation Localized deterioration X X X O 1 O-R 2 O-R 2 Visual Inspection All Visible Components within the End Winding Compartment Cleanliness, foreign material, loose or displaced parts, damage, wear, d |  | Wedge Tightness Test ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings ¦ Hydrogen Seal Assembly ¦ Stator Winding | . Rotor Out Inspection is recommended every 2nd inspection interval. Consult the appropriate maintenance and inspection manual of the turbine for interval guidance. This example is meant to demonstrate how generator inspection and maintenance intervals would be synchronized for a turbine with the referenced intervals. Generator Turbine Generator Turbine GE Proprietary Information - Class II (Internal) US EAR - NLR GEK 103566M Creating a More Effective Generator Maintenance 9 without prior permis
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 4723ca6f0eb3912b20340cdb0e745a0f | 423 | 2024-05-31 | Inspection | Stator | Wedge Tightness Test | 7 | Blocked Vent Ducts, Focused Generator Inspection, Greasing, MAGIC Inspection, Stator Winding, Wedge Tightness Test, Wedges | Cost impact of condition assessment techniques Continuous Periodic Minor Major On-Line On-Line Outage Outage STATOR Stator Wedge Tightness X Bar Movement X Stator Winding Leaks X X Core Insulation X Stator Winding Insulation Integrity X X X |  | Wedge Tightness Test ¦ Blocked Vent Ducts ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Stator Winding | . New bottom line reali- ties, however, are motivating many plant opera- tors to reevaluate established maintenance practices and deviate from them where they perceive net cost-to-risk advantages. Plant operators are increasingly looking to extend equipment running time between planned maintenance outages, eliminate unnecessary outages and reduce the duration of the necessary ones. GE, as the leading manu- facturer of turbine-generators and a major sup- plier of power generation services, is ass
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | e23d4d94e4519493849f1118b9fd5cb4 | 436 | 2024-05-31 | Inspection | Stator | Wedge Tightness Test | 7 | End-winding, Focused Generator Inspection, Lamination Damage, MAGIC Inspection, Stator Winding, Wedge Tightness Test, Wedges | Stator winding clearance measurement Figure 8. |  | Wedge Tightness Test ¦ End-winding ¦ Focused Generator Inspection ¦ Lamination Damage ¦ MAGIC Inspection ¦ Stator Winding | . Periodic MAGIC in-situ inspections, together with elec- trical testing and hydraulic checks, provide an acceptable alternative to many traditional OEM maintenance protocols. Skillful interpretation of in-situ inspection observations and related data can provide plant operators with cost effec- tive opportunities to reduce outages and outage duration while maintaining the outstanding reliability and availability of their generators. Recommended maintenance schedules for tra- ditional and in-sit
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | a73a75c61e6ead5430eb26d871be43cf | 424 | 2024-05-31 | Inspection | Field, Stator | Wedge Tightness Test | 7 | Core, End-winding, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | MAGIC Visual Inspection Visual inspection of the generator stator and field within the bore region is performed by a trained specialist using GE’s exclusive MAGIC inspection robot.; The robot is a precision crawler carrying two high resolution video cam- eras that moves through the gap between the stator core and field.; Full inspection coverage of the core ID and field surface is made possible by the robot’s axial and transverse motion capa- bility.; The high resolution video scopes Generator In-Situ Inspections GE Power Systems I GER-3954B I (04/03) 3 Generator In-Situ Inspections GE Power Systems I GER-3954B I (04/03) 4 MAGIC Visual – Core Laminations – Space Blocks – Stator Bars, Wed; Ultrasonic Stator Wedge Tightness Assessment Electromagnetic Core Imperfection Detection (ELCID) Stator Insulation Capacitance Measurement Stator Clearance Measurement GT25678 Table 1 | GEK-103566 | Wedge Tightness Test ¦ Core ¦ End-winding ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ GEK-103566 | . Generator inspection items outages. This information can be used to deter- mine if the field will need to be pulled and what components will require maintenance at this or future outages. If the generator condition is found to be acceptable, a future in-situ inspec- tion may be planned with no maintenance nec- essary at this time. As long as the generator con- dition is found acceptable, there would be no additional need to pull the field. GE’s in-situ inspection techniques can also be used wi
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | e10a9c5835fb671b1a324aa5b7655767 | 309 | 2024-05-31 | Electrical | Field | DLRO; Winding Resistance | 6 | AC Impedance, DLRO, Field Body, Polarization Index, Winding Resistance, Winding resistance DLRO | The winding resistance was measured with a DLRO and the value was converted to 25degC for trending.; NA 3.5.2 Megger Test with Polarization Index (PI) Inspection Type:; 3.5.2 Megger Test with Polarization Index (PI) Recommendation Type:; 3.5.3 AC Impedance Test Inspection Type:; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.76 2.00 5.38 20.42 3.80 5.37 30.06 5.60 5.37 40.25 7.40 5.44 50.15 8.90 5.63 59.80 10.50 5.70 70.39 12.20 5.77 80.36 13.50 5.95 91.62 15.00 6.11 100.09 16.10 6.22 110.46 17.30 6.38 113.2 | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ AC Impedance ¦ DLRO ¦ Field Body ¦ Polarization Index ¦ Winding Resistance ¦ Winding resistance DLRO ¦ TM4010 ¦ TM4020 | . 3.5 Field Electrical Testing 3.5.1 Winding Copper Resistance Inspection Type: Electrical Part Condition: Good Part Description: The winding resistance was measured with a DLRO and the value was converted to 25degC for trending. The measured value compares favorably to the value stamped on the coupling. Data Recommendation Status: Should be planned for next Outage Recommendation Type: Services Recommendation Description: Track & Trend CBM: NA 3.5.2 Megger Test with Polarization Index (PI) Inspe
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 997fffd8a247ef1af9ba5d151a350e36 | 341 | 2024-05-31 | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically constructed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . A typical visual inspection should include those items listed in Tables 4,5,6 and 7. As a critical component of the overall maintenance program, visual inspection is limited to areas that can be accessed for view either directly or with mirrors, borescopes, cameras, etc., and therefore must be combined with other tests to give a complete picture of generator condition. Medium and High Voltage Auxiliary Equipment As part of a robust maintenance program it is advised to routinely inspect all the
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 073eb312a5ad4bafc53a6d5ef4e7b24f | 329 | 2024-05-31 | Inspection | Stator | Stator Findings Review | 5 | Blocked Vent Ducts, Core, End-winding, Stator Winding, Wedges | During the first several months of operation, the stator winding support system and some of the other generator components experience a break-in period.; Some examples that may point to the abnormal aging of the generator includes repeated heavy dusting on the stator end windings, early or frequent stator re-wedges (units with concave-convex wedges require re-tightening), blocked vent ducts |  | Stator Findings Review ¦ Blocked Vent Ducts ¦ Core ¦ End-winding ¦ Stator Winding ¦ Wedges | . 1 . Background A thorough maintenance program is recommended to improve generator reliability and avoid major maintenance expenses. The three important elements of a thorough program are maintenance frequency, visual inspection and testing. It is the intent of this document to provide information on each of these elements, which will assist the owner/operator to establish a thorough and cost-effective maintenance program synchronized with the prime mover. Plant operating experience, plant hist
UNI026365 | INDEPENDENCE POWER STATION | Field_Service_Report_ProjectID_A-1586168_FSP-286344_C-10344989.pdf | 296300 | Gas Turbine | 0fc1d044daa91a232ec5726de460026f | 332 | 2024-05-31 | Electrical | Field, Stator | DC Leakage | 5 | DC Leakage, Retaining Rings, Stator Winding, Wedge Looseness, Wedges | Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened materia |  | DC Leakage ¦ Retaining Rings ¦ Stator Winding ¦ Wedge Looseness ¦ Wedges | . Some turbines relate to the Equivalent Operation Hours. Please refer to GER 3620 and Turbine and/ or Generator O&M documents. 3 Inspection and maintenance intervals are determined by whichever occurs first, whether it is actual turbine hours, factored turbine hours, actual turbine starts, factored turbine starts, turning gear hours. First inspection should not exceed the first 18 months of operation. Subsequent inspection and maintenance intervals for typical operating regimes are expected to
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 297255 | Gas Turbine | a485a33952590a2735f1ba3882bee6e0 | 180 | 2024-04-13 | Inspection | Stator | Wedge Tightness Test | 6 | Focused Generator Inspection, Greasing, Keybars, Step Iron, Wedge Tightness Test, Wedges | The inspection consisted of a borescope on the CE and TE step iron looking for loose laminations.; Greasing was found on the step iron and end wedge locations.; A wedge tap was performed on the unit with the wedge map showing no loose or hollow wedges.; The step iron and end windings had greasing that was cleaned, red eye and flooding resin applied.; Due to the greasing on the step iron and end wedges it is recommended at the next outage to check the tightness of the bellybands and keybar nuts. |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ Keybars ¦ Step Iron ¦ Wedges | . The plant decided to do an inspection of the generator due to a humming noise that has been present in the generator for a couple of weeks. The inspection consisted of a borescope on the CE and TE step iron looking for loose laminations. The borescope inspection was performed by the borescope technician Dillan Smith and Generator Specialist Franklin Wright. No laminations were found to be loose or damaged. Greasing was found on the step iron and end wedge locations. The unit had a field out in
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 297255 | Gas Turbine | 79c592c879c12f2d91d2e6d883ca70f2 | 188 | 2024-04-13 | Inspection | Stator | Stator Findings Review | 3 | Core, Greasing, Step Iron | GE Gas Power Inspection & Life Extension Services Inspection Details Menu Directed Gen_V1_2 Serial Number 337X709 Customer LA Frontera Holding, LLC Site Lamar Power Partners Location Paris, TX Unit Number 12 Equipment Model 7FH2 CPM/Site Co |  | Stator Findings Review ¦ Core ¦ Greasing ¦ Step Iron | . GE Gas Power Inspection & Life Extension Services Inspection Details Menu Directed Gen_V1_2 Serial Number 337X709 Customer LA Frontera Holding, LLC Site Lamar Power Partners Location Paris, TX Unit Number 12 Equipment Model 7FH2 CPM/Site Contact Scott Garner Inspector Dilan Smith Generator Specialist Frank Wright Outage Type Planned Date 3/26/2024 Time 08:58:04 Study Instance ID e4070e04-e1ac-49e6-8975-47927279ace8- 2123a9356 Inspection Summary No Images/Approved Nodes No Flagged Images Flagge
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 297255 | Gas Turbine | ff2460aee5ea30aa46c55fa72b7dee98 | 197 | 2024-04-13 | Inspection | Stator | Stator Findings Review | 3 | Core, Greasing, Step Iron | End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Greasing Comments Collector_End_Stato_nd-Step_Iron_General_015-FLAG.J Section Collector End Sub-Section Stator Core Component Air Gap Loca |  | Stator Findings Review ¦ Core ¦ Greasing ¦ Step Iron | End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Greasing Comments Collector_End_Stato_nd-Step_Iron_General_015-FLAG.J Section Collector End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Greasing Comments Collector_End_Stato_nd-Step_Iron_General_016-FLAG.J GE Gas Power Inspection & Life Extension Services Section Collector End Sub-Section Stator Core Component Air Gap Location End-Step Iron S
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 297255 | Gas Turbine | 0422b9c199cc1e657f84a625eff544f4 | 205 | 2024-04-13 | Inspection | Stator | Stator Findings Review | 3 | Core, Greasing, Step Iron | Comments Collector_End_Stato_nd-Step_Iron_General_032-FLAG.J GE Gas Power Inspection & Life Extension Services Section Collector End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Greasing |  | Stator Findings Review ¦ Core ¦ Greasing ¦ Step Iron | Comments Collector_End_Stato_nd-Step_Iron_General_032-FLAG.J GE Gas Power Inspection & Life Extension Services Section Collector End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Greasing Comments Collector_End_Stato_nd-Step_Iron_General_033-FLAG.J Section Collector End Sub-Section Stator Core Component Air Gap Location End-Step Iron Sub-Location General Observation Greasing Comments Collector_End_Stato_nd-Step_Iron_General_034-FLAG.J GE Gas Po
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 297255 | Gas Turbine | 996c7cac8c427b47b3bb6967077fdea0 | 214 | 2024-04-13 | Inspection | Stator | Stator Findings Review | 3 | Core, Greasing, Step Iron | Core Component Stator Core Location End-Step Iron Sub-Location General Observation Greasing Comments Turbine_End_Stator__nd-Step_Iron_General_014-FLAG.J GE Gas Power Inspection & Life Extension Services Section Turbine End Sub-Section Stato |  | Stator Findings Review ¦ Core ¦ Greasing ¦ Step Iron | Core Component Stator Core Location End-Step Iron Sub-Location General Observation Greasing Comments Turbine_End_Stator__nd-Step_Iron_General_014-FLAG.J GE Gas Power Inspection & Life Extension Services Section Turbine End Sub-Section Stator Core Component Stator Core Location End-Step Iron Sub-Location General Observation Greasing Comments Turbine_End_Stator__nd-Step_Iron_General_015-FLAG.J Section Turbine End Sub-Section Stator Core Component Stator Core Location End-Step Iron Sub-Location Gen
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1828574_EV-156982_C-10378887_EVP-536642.pdf | 297255 | Gas Turbine | dcafe02d32c8b2c1e2cdd3a2b7a23f5b | 184 | 2024-04-13 | Inspection | Stator | Focused Generator Review | 2 | Core, Wedges | NA – Parts were not inspected during this inspection NV – No visible indications / abnormal findings AF – Observed visible / abnormal finding Collector End Components Inspected YES/NO Disposition Peripheral List Below Inspected YES/NO Dispo |  | Focused Generator Review ¦ Core ¦ Wedges | . Interpretation of the photographs should be made by someone familiar with videoscope photography. Unit Access Enter a customized description of how you gained access to each section inspected. GE Gas Power Inspection & Life Extension Services External GE Documents TIL Number TIL Title Internal GE Documents ETC Number ETC Title ER Number ER Title GE Gas Power Inspection & Life Extension Services Areas Inspected Disposition Legend: NA – Parts were not inspected during this inspection NV – No vis
UNI035751 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1747384_EV-138969_C-10371457.pdf | 298018 | Gas Turbine | 9573196165748cd5e7a2d6014c34fcb1 | 541 | 2023-04-05 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . Borescope ports in the turbine casing allowed viewing of the first stage nozzle, first stage buckets, second stage nozzle, second stage buckets, third stage nozzle, and third stage buckets. GE Power Inspection & Life Extension Services Technical Information Letters (TILs) Inspected TIL Number TIL Title 1108-R1 Cast Segmented Turbine Nozzle Acceptance Guidelines 1502-2R1 Active/open 7F AND 9F AFT END COMPRESSOR RUBS 1509-R4 Active/open F-Class Front End (R0, S0, and R1) Compressor Inspections 1
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | eda837f89356bd72544ab5f7ad3d071b | 27 | 2022-07-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The nominal design clearance is 41 to 46 mils.; The minimum, average, and maximum as-found clearances were 45 mils, 55 mils, and 74 mils, respectively.; Although the as-found vertical clearance was ~25 mils over the nominal design clearance, it was still within the 2X-design maintenance clearance normally allowed before component replacement.; The minimum, average, and maximum as-found clearances were 45 mils, 55 mils, and 64 mils, respectively.; The average as-found vertical clearance was ~20 mils over the nominal design clearance, but still well within the 2X-design maintenance clearance normally allowed before component replacement. |  | Oil Deflector Alignment ¦ Oil Deflectors | . The nominal design clearance is 41 to 46 mils. The minimum, average, and maximum as-found clearances were 45 mils, 55 mils, and 74 mils, respectively. Although the as-found vertical clearance was ~25 mils over the nominal design clearance, it was still within the 2X-design maintenance clearance normally allowed before component replacement. This oil seal was deemed suitable for continued service, but will probably need to be replaced during the next inspection of the #2 journal bearing. #2 For
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | 95768e49e5b15d688fb47d2c43083c61 | 31 | 2022-07-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | All new oil control rings and oil deflectors were inspected and measured as they were all to be replaced. | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | Part Condition: Good Part Description: During the outage the thrust bearing assembly was removed and visually inspected. The bearing showed typical light wear evenly on all pads active and inactive. No serious signs of scoring or pitting were noted. The existing pads were reused during this outage and were installed with new thermocouple wires. Both thrust shims were also removed, cleaned, and measured during disassembly. All new oil control rings and oil deflectors were inspected and measured a
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | 9f2d09878859c865ed4bec90b343cd4c | 21 | 2022-07-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The nominal design clearance is 51 to 56 mils.; The minimum, average, and maximum as-found clearances were 51 mils, 56 mils, and 61 mils, respectively.; The nominal design clearance is 46 to 51 mils.; The minimum, average, and maximum as-found clearances were 44 mils, 50 mils, and 61 mils, respectively.; The minimum, average, and maximum as-found clearances were 46 mils, 49 mils, and 54 mils, respectively. |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Condition: Poor Part Description: The number one turbine bearing was removed and inspected during the outage. This bearing was discovered to have the most damage to the lower half pads due to the bucket liberation event. While the upper half of the bearing saw little to no damage, the lower half exhibited heavy wear with the center of the pads whipped down through the babbitt. The oil seals and deflectors were to be replaced during the outage, therefore only the new ones were measured. The
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | 92419a910ca41005a1e0053c5ba78457 | 15 | 2022-07-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Measure journal diameters and oil deflectors and record all opening clearances. |  | Oil Deflector Alignment ¦ Oil Deflectors | Next Outage Services Visually inspect during the next major outage. Measure journal diameters and oil deflectors and record all opening clearances.
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | 7748be6bc2969a19e11df86788586e46 | 108 | 2022-07-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | All oil deflectors were provided by the customer, these were inspected for damage and measured on site.; Measure journal diameters and oil deflectors and record all opening clearances. |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Condition: Poor Part Description: The T2 journal bearing was scheduled to be removed during this outage due to the amount of seismic vibration recorded during the liberation event. The opening clearances were recorded and found to be out of specification. Upon opening, the oil deflector teeth were found to be flattened with deep grooving on the rotor journal. The upper half of the bearing pads were found to be in good condition, however once the rotor was removed the lower half had extensiv
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | f464be280986f3adb96354b9334f7bbb | 11 | 2022-07-28 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted.
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | a15c2f041bd8c04716b64e5f169dc704 | 59 | 2022-07-28 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Part Condition: Good Part Description: The flow sleeves were removed and visually inspected. The liner stops, cross fire clip retainers, and hula skirts all exhibited normal wear and were returned to service. Recommendation Status: Should be planned for next Outage Recommendation Type: Services Recommendation Description: All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. Flow Sleeve Hula Skirt Condition Flow Slee
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | fbae7fd275893a140fac12f894015678 | 36 | 2022-07-28 | Inspection |  | Focused Generator Review | 1 | Greasing | Follow maintenance practices outlined above regarding IGV gears and ring greasing. | ER-20220626-0268 | Focused Generator Review ¦ Greasing ¦ ER-20220626-0268 | Part Condition: Good Part Description: All inlet guide vanes (IGV's) were visually inspected and all clearances and measurements were recorded. A true opening clearance check could not be performed with the correct tooling at that time, however all clearances were measured upon closing with engineering review (ER-20220626-0268) and adjustments performed. All measurements were found to be within GE specifications except for the lower half of backlash measurements which many were at or above the 0
UNI036153 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1737456_EV-136778_C-10370713.pdf | 297545 | Gas Turbine | 50a1dab6ad389c31f9ec883fd96361a3 | 10 | 2022-07-28 | Inspection |  | Focused Generator Review | 1 | Greasing | Next Outage Services Follow maintenance practices outlined above regarding IGV gears and ring greasing. |  | Focused Generator Review ¦ Greasing | Next Outage Services Follow maintenance practices outlined above regarding IGV gears and ring greasing. Take IGV clearance measurements at the next scheduled maintenance interval and compare them to the as left closing values taken during this outage.
UNI035751 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1734332_EV-136170_C-10370464.pdf | 298018 | Gas Turbine | 9b2d63c9917081bd43237abdb797232f | 21 | 2022-06-30 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA 18.689 NA Shaft Grounding Brushes A NA NA NA Outer Oil ; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J Inner Oil Deflector K Middle Oil Deflector L Hydrogen S |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 337X263 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA 18.689 NA Shaft Grounding Brushes A NA NA NA Outer Oil Deflector B 0.009 0.007 0.009 0.009 0.022 0.009 Hydrogen Seal Casing
UNI035751 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1734332_EV-136170_C-10370464.pdf | 298018 | Gas Turbine | 7a772e4935c8a53ef302d3db96874142 | 10 | 2022-06-30 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA 18.689 NA Shaft Grounding Brushes A NA NA NA Outer Oil ; The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J Inner Oil Deflector K Middle Oil Deflector L Hydrogen S |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prior written consent. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE
UNI035751 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1734332_EV-136170_C-10370464.pdf | 298018 | Gas Turbine | 885634ba7c7c50f817d0a59e8b39b7cb | 19 | 2022-06-30 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | Collector Rings, Hydrogen Seal Assembly |  | EM2101 | Focused Generator Review ¦ Collector Rings ¦ Hydrogen Seal Assembly ¦ EM2101 | . 2. G1= generator coupling end bearing, G2 = generator collector end bearing. S1 = Steady rest bearing. A1 = Alterrex coupling bearing, A2 = Alterrex collector bearing. Brg LSL USL Acutal Tolerance # IV OV IT OT (inches) (inches) (inches) Check G1 15.999 15.999 0.023 0.023 0.000 0.002 0.000 Acceptable G2 15.998 15.998 0.023 0.023 0.000 0.002 0.000 Acceptable S1 A1 A2 Brg LSL USL Actual Tolerance # IL OL IR OR (inches) (inches) (inches) Check G1 0.017 0.017 0.016 0.017 -0.005 0.005 -0.001 Accept
UNI035751 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1734332_EV-136170_C-10370464.pdf | 298018 | Gas Turbine | 5921030ef524aa80a133408c2d8f3a1d | 11 | 2022-06-30 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | After performing the as found alignment and lift checks, the outer oil deflectors alignment was checked and the bearing housings on both ends of the generator were removed.; The babbitt was found in good conditions with a normal and expected wear pattern on both bearings, having a wider section wear on the T3 lower half bearing, consistent with the 0 mils lift measurement.; A new pinch check was performed on both ends obtaining the same measurements of the disassembly, the lift oil hoses were connected and the bearing housings were reinstalled taking special care on the bolting torque and the outer oil deflect |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Condition: Good Part Description: After performing the as found alignment and lift checks, the outer oil deflectors alignment was checked and the bearing housings on both ends of the generator were removed. Pinch checks were performed and measurements were found within specifications. The upper half bearings were removed in order to perform the Tilt & Twist checks, finding the measurements to be within specifications. The shaft jacking devices were installed on both ends and the lower half
UNI035721 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1731630_EV-135699.pdf | 298235 | Gas Turbine | a5b1b206f880d07e7e3f7da47da37cd4 | 11 | 2022-06-22 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted.
UNI035721 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1731630_EV-135699.pdf | 298235 | Gas Turbine | 1a00281174a7ff1c7b28cfe35de738fc | 33 | 2022-06-22 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Part Condition: Fair Part Description: The removed flow sleeves were inspected for any signs of hot spots, crack indications, or excessive wear. Slight wear was noted, on the liner stops and cross fire tube retaining clip engagements. The spring seals were checked for lift and inspected for any missing tines. No excessive lift or missing tines were noted. The flow sleeve ring seal at the aft end was found to have a major step in the surface due to wear. New floating seals were provided and insta
UNI035751 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1693592_EV-108196_C-10366341.pdf | 298018 | Gas Turbine | 252d01f2da463724f4ca2ad5f50bb5e7 | 26 | 2022-06-06 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | CR - Cracked D - Distortion W - Wear B - Blockage PW - Liner Stop Pin Wear SW - Liner Stop Side Wear CT - Crossfire Tube Flange Wear Heavy wear was observed on all floating seal rings (piston rings). |  | Focused Generator Review ¦ Seal Rings | service is why they were reused.(inspection details attached below in attachments) All preexisting flow sleeves were installed at assembly. Recommendation Status: Should be planned for next available shut down Recommendation Type: Parts Recommendation Description: Recommendation is to replace all piston rings at the next opportunity. As Found & Reinstalled Flowsleeves (2) Heavy Wear on Piston Rings (4) Heavy Wear on Piston Rings (5) As Found & Reinstalled Flowsleeves (3) GEGEGE GE Confidential a
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1676686_FSP-310992_C-10363356.pdf | 297544 | Gas Turbine | 8ed80549ec3d8f37e309135a2108f6d0 | 10 | 2022-06-02 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | ER-20210727-0910, ER-20210816-0784, ER-20211111-0880 | Oil Deflector Alignment ¦ Oil Deflectors ¦ ER-20210727-0910 ¦ ER-20210816-0784 | . The technical data herein is the property Serial #297544 DYNEGY KENDALL ENERGY, LLC Previous MI- April' 21 Inspection Summary & Focus area Priority Section of the Turbine Previous Inspection Findings 1 Compressor After MI outage, and this will be the first inspection on Compressor section 2 Combustion All CI parts were replaced during MI outage, and this will be the first inspection on Combustion section 3 Hot Gas Path All HGP parts were replaced during MI outage, and this will be the first in
UNI036149 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1665346_EV-122463_C-10360633.pdf | 297543 | Gas Turbine | 576c26f10070d6c8cf91f257cbaf87c2 | 19 | 2022-06-02 | Mechanical | Stator | Wedge Tightness Test | 2 | Wedge Tightness Test, Wedges |  | ER-20200507-1143, ER-20200510-0002, ER-20200510-0004, ER-20200510-0006, ER-20211118-0921 | Wedge Tightness Test ¦ Wedges ¦ ER-20200507-1143 ¦ ER-20200510-0002 | . GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclosed in confidence. The technical data herein is the property Serial #297543 DYNEGY KENDALL ENERGY, LLC Power Service Now ER case of Interest: 1) ER-20211118-0921: Kendall Unit 1 Borescope Findings_S1N Seal Housing Hardware Observation The seal housing has: • 9 missing and 1 loose bolt - At least 2 seal housing segments are not meeting TIL 2302 criteria of fully en
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | b6a153031a1d915d880649c6ff4366cd | 339 | 2022-05-25 | Repair | Field, Stator | Red Eye Repair | 31 | 10-minute 5000 VDC Megger PI, AC Impedance, Amortisseur, Amortisseur Migration, Belly Bands, Belly band inspection, Blocked Vent Ducts, Collector Rings, Core, Core Tightness Test, Core tightness test, DC Leakage, DLRO, End-winding, Field Body, Flux Probe Resistance, Flux probe resistance, Focused Generator Inspection, Greasing, HVB cleaning, High Voltage Bushings, Keybars, Loose End-winding Blocking, MAGIC Inspection, RTD Ohmic resistance and 1-minute Megger, Red Eye Repair, Red eye repair on end winding, Retaining Rings, Visual inspection using MAGIC robot and borescope, Winding Resistance, Winding resistance DLRO | Due to the findings of loose end-winding blocking and amortisseur migration in the field (generator rotor), engineering has deemed it not suitable for service.; Engineering has recommended a complete vent duct blockage map as well as a retaining rings off repair to address the blocking issues before returning to service.; · Visual inspection using MAGIC robot and borescope · RTD Ohmic resistance and 1-minute Megger · Flux probe resistance · Winding resistance DLRO · 10-minute 5000 VDC Megger PI · DC Leakage · Belly band inspection · Core tightness test · HVB; · Visual and borescope inspection (retaining rings on) · Partial mapping of blocked vent ducts using borescope · Winding resistance DLRO · AC Impedance · 10-minute 500 VDC Megger PI · Collector ring cleaning Engineering PAC cases submitted:; · ER-20220409-0300 – Field vent blockage due to amortisseur migration and loose blocks in field end winding Visual and quantitative inspections of the core and end winding system are important in assessing a generators’ overall condition. | ER-20220409-0300 | Red Eye Repair ¦ 10-minute 5000 VDC Megger PI ¦ AC Impedance ¦ Amortisseur ¦ Amortisseur Migration ¦ Belly Bands ¦ Belly band inspection ¦ ER-20220409-0300 | The following report documents all work performed on unit 337X752 (GT3) at Dynegy Corporation, LLC – Moss Landing Power Plant located in Moss Landing, California. The scheduled outage was started on April 03, 2022 and finished April 13, 2022. The intent of this report is to assess the current generator condition and ensure it can safely return to service. Due to the findings of loose end-winding blocking and amortisseur migration in the field (generator rotor), engineering has deemed it not suit
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 31319cc8d073d30d65d22e0277d413f2 | 319 | 2022-05-25 | Inspection | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 10 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Case, Hydrogen Seal Assembly, Inner Gas Shield, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Seal Rings | All oil deflectors were removed, visually inspected, and replaced new.; The new oil deflectors were dimensionally measured with an inside micrometer before reassembly.; All oil deflectors were aligned to the generator field according to clearance diagram 585E2375.; This allows .040'' to be machined from the hydrogen case sealing surface, if necessary.; Prior to installation, the new seals were dimensionally measured and blue checked to verify 100% contact with the hydrogen case sealing surface. |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Case ¦ Hydrogen Seal Assembly ¦ Inner Gas Shield | All oil deflectors were removed, visually inspected, and replaced new. Oil buildup and flattened teeth from rotor rubbing was observed throughout the sets. The new oil deflectors were dimensionally measured with an inside micrometer before reassembly. All oil deflectors were aligned to the generator field according to clearance diagram 585E2375. New Outer Oil Deflector The hydrogen seal casings were removed, cleaned, visually inspected, lapped, and reinstalled. Both cases had a nominal A-Gap mea
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | e4923508ba17b1b3aa842bca1daa57b8 | 3 | 2022-05-25 | Inspection | Field, Hydrogen Seals, Stator | Oil Deflector Alignment | 10 | Belly Bands, Belly band inspection, Core, End Shield, Fan Blades, Focused Generator Inspection, Hydrogen Seal Assembly, Inner Gas Shield, Oil Deflector Alignment, Oil Deflectors | HOT GAS PATH INSPECTION (HGPI) - 297604 DYNEGY MOSS LANDING, LLC MOSS LANDING 3.9 Generator Mechanical __________ 312 3.9.1 Oil Deflectors __________ 312 3.9.2 Hydrogen Seal Assembly __________ 320 3.9.3 End Shield and Inner Gas Shield ____ |  | Oil Deflector Alignment ¦ Belly Bands ¦ Belly band inspection ¦ Core ¦ End Shield ¦ Fan Blades ¦ Focused Generator Inspection | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 EHS __________ 3 1.3 Quality __________ 3 GAS TURBINE (297604 ¦ SY0070881) __________ 4 1 Summary __________ 4 1.1 Timers and Counters __________ 4 1.2 Executive Summary __________ 4 2 Technical __________ 7 2.1 Recommendations __________ 7 3 Turbine __________ 10 3.1 Auxiliaries __________ 10 3.1.1 Lube and Seal Oil Pumps and Motors __________ 10 3.1.2 Piping and Flexible Metal Hoses _______
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | f368f02dd8440a34ffab252f9f50758a | 383 | 2022-05-25 | Inspection | Field, Stator | MAGIC Inspection | 9 | Amortisseur, Amortisseur Migration, Collector Rings, End-winding, Fan Blades, Loose End-winding Blocking, MAGIC Inspection, Retaining Rings, Wedges | GT3 had a poor collector surface film, streaking between brushes, signs of discoloration (potentially due to overheating), and uneven wear (7 mil maximum).; The collector rings, fan blades, and housing were covered in carbon dust contamination and the rings were cleaned before testing.; Amortisseur Migration (Blocked Field Vents):; The permanent resolution for amortisseur migration would be to pull the rotor, remove retaining rings and wedges then reinstall parts in correct position.; End-winding Blocking: | GEK103566, GEK116362 | MAGIC Inspection ¦ Amortisseur ¦ Amortisseur Migration ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ Loose End-winding Blocking ¦ GEK103566 ¦ GEK116362 | Condition of collector ring surfaces, surface film and brushes, provide an excellent indication of overall collector ring health and whether problems existed in service. GT3 had a poor collector surface film, streaking between brushes, signs of discoloration (potentially due to overheating), and uneven wear (7 mil maximum). The collector rings, fan blades, and housing were covered in carbon dust contamination and the rings were cleaned before testing. All collection ring hardware appeared tight
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 78e9ffa82525a9e694d18fb85738a660 | 384 | 2022-05-25 | Electrical | Field, Stator | DLRO; Winding Resistance | 9 | AC Impedance, Bluing, Collector Rings, DLRO, End-winding, Polarization Index, Turn Jumper, Winding Resistance, Winding resistance DLRO | • It is very important to use GE recommended National Carbon 634 brushes to ensure even wear on the collector rings.; Collector Housing - Carbon Dust Contamination 3.10.5 Field (Rotor) Visual Inspection Collector Housing - Carbon Dust Contamination (2) Collector Rings - Poor Surface Film (2) 3.10.5 Field (Rotor) Visual Inspection Collector Rings - Pitting ; Coil Resistance DLRO The field winding resistance was taken with a Digital Low Resistance Ohm meter (DLRO) to obtain the desired accuracy in the low resistance ranges associated with field winding.; The winding resistance test produced satisfactory results within GE’s acceptance criteria.; Coil Insulation Resistance and Polarization Index After completing a successful field winding DLRO, an “as-found” 500VDC megger was performed on the unit to test the integrity of the field winding insulation. | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ AC Impedance ¦ Bluing ¦ Collector Rings ¦ DLRO ¦ End-winding ¦ Polarization Index ¦ TM4010 ¦ TM4020 | . • It is very important to use GE recommended National Carbon 634 brushes to ensure even wear on the collector rings. Collector Housing - Carbon Dust Contamination 3.10.5 Field (Rotor) Visual Inspection Collector Housing - Carbon Dust Contamination (2) Collector Rings - Poor Surface Film (2) 3.10.5 Field (Rotor) Visual Inspection Collector Rings - Pitting Collector Rings - Poor Surface Film (3) 3.10.5 Field (Rotor) Visual Inspection Collector Rings - Streaking Between Brushes Collector Rings -
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | b93190e751d1bc1b528eb876c7383ba2 | 15 | 2022-05-25 | Inspection | Field, Stator | MAGIC Inspection | 8 | Amortisseur, Amortisseur Migration, Collector Rings, End-winding, Loose End-winding Blocking, MAGIC Inspection, Retaining Rings, Wedges | Amortisseur Migration (Blocked Field Vents):; The permanent resolution for amortisseur migration would be to pull the rotor, remove retaining rings and wedges then reinstall parts in correct position.; End-winding Blocking:; • Engineering formally recommended that the field needs to be pulled out with retaining rings off repair to address the blocking issue.; Collector Rings: | GEK103566, GEK116362 | MAGIC Inspection ¦ Amortisseur ¦ Amortisseur Migration ¦ Collector Rings ¦ End-winding ¦ Loose End-winding Blocking ¦ GEK103566 ¦ GEK116362 | Amortisseur Migration (Blocked Field Vents): • Engineering’s formal recommendation is to perform a full mapping of vent ducts to determine the severity of the issue. Since the customer has chosen to run the field as is, it is essential that these findings be addressed as soon as possible during next outage opportunity. The permanent resolution for amortisseur migration would be to pull the rotor, remove retaining rings and wedges then reinstall parts in correct position. During operation the cus
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 555dc5369245468c4f97fdf4a85582fc | 371 | 2022-05-25 | Electrical | Stator | Polarization Index; DC Leakage | 8 | Core, DC Hipot, DC Leakage, Focused Generator Inspection, MAGIC Inspection, Polarization Index, Wedge Tightness Test, Wedges | The MAGIC robot performed a partial wedge tightness test.; A wedge map was created to represent the stator core on a 2D plane and can be found in the datasheet below;; The results of this wedge tightness test are worse than the previous test performed in 2015.; however a full map was not created, nor were end wedges accessible, therefore it cannot be confirmed.; Armature Insulation DC Leakage Test Collector End Date (dd-mm-yyyy) Gen SN Prepared by Manufacturer Turbine SN Equipment Data set Project ID A 10 KV DC voltage was applied to each phase with the other two phases grounded for a period of 10 |  | Polarization Index; DC Leakage ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Polarization Index | The MAGIC robot performed a partial wedge tightness test. Due to the flux probe location, slot 32 was bypassed completely and slot 33 was only partially tapped. A wedge map was created to represent the stator core on a 2D plane and can be found in the datasheet below; Green indicates tight, yellow indicates hollow, red indicates loose. The results of this wedge tightness test are worse than the previous test performed in 2015. From the data collected, technically the unit is within GE’s acceptan
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 98b00103faf5c44aa2371d55ffd9b487 | 341 | 2022-05-25 | Repair | Stator | Red Eye Repair; Wet Tie Repair | 7 | End-winding, Greasing, High Voltage Bushings, Keybars, Red Eye Repair, Water Ingress, Wet Tie Repair | Binding Band - Light Greasing Belly Rust and Corrosion (2) Binding band - Ok (2) Connection Ring - Light Greasing (2) Binding band - OK (3) Binding band - OK Binding band - OK (4) Connection Ring - Existing Red Eye Repair Connection Ring - |  | Red Eye Repair; Wet Tie Repair ¦ End-winding ¦ Greasing ¦ High Voltage Bushings ¦ Keybars ¦ Red Eye Repair ¦ Water Ingress | Binding Band - Light Greasing Belly Rust and Corrosion (2) Binding band - Ok (2) Connection Ring - Light Greasing (2) Binding band - OK (3) Binding band - OK Binding band - OK (4) Connection Ring - Existing Red Eye Repair Connection Ring - Heavy Dusting Connection Ring Tie - Light Greasing Outer Axial Support Hardware Locked Keybar Locking Nut Wet Tie Repair - Existing Red Eye Repair (3) Belly Rust and Corrosion Belly Rust and Corrosion (3) Dust Contamination Connection Ring - Heavy Dusting (2)
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 206676ca8d152c7088c193edfc5f0de2 | 465 | 2022-05-25 | Inspection | Field, Stator | MAGIC Inspection | 7 | Gooseneck, MAGIC Inspection, Main Lead, Pole Jumper, Step Iron, Sub-slots, Wedges | Overview of packages, wedges, and field ~ 104” from CE RR Image 27 Slots 29 - 25 TE step iron and end wedges – grease/dusting Image 28 Slots 29 - 25 Dusting on packages ~ 146” from CE RR Image 29 Slots 29 - 25 Dusting on packages ~ 104” fro; TE RR and end wedges – dowels not flush with wedge surface Image 44 Slots 10 - 5 Dusting on packages ~ 152” from CE RR Image 45 Slot 12 / 66 deg.; Overview of packages, wedges, and field ~ 140” from CE RR Image 46 Slots 10 - 5 Dusting on packages ~ 104” from CE RR Image 47 Slot 11 Foreign material in vent slot ~ 81” from CE RR Image 48 Slot 7 Foreign material in vent slot ~ 78” from C; Overview of packages, wedges, and field ~ 100” from CE RR Image 58 CE RR Main lead and coil jumpers 0 deg.; – twisting, dust/black deposits on coils Image 59 CE RR Pole Jumper and sub slots 270 deg. |  | MAGIC Inspection ¦ Gooseneck ¦ Main Lead ¦ Pole Jumper ¦ Step Iron ¦ Sub-slots | . Blocked field cooling hole ~ 2” from CE RR Image 24 Slot 33 Flux probe on wedge 3 Image 25 300 deg. Partially blocked field cooling hole ~ 36” from CE RR Image 26 Slot 31 / 312 deg. Overview of packages, wedges, and field ~ 104” from CE RR Image 27 Slots 29 - 25 TE step iron and end wedges – grease/dusting Image 28 Slots 29 - 25 Dusting on packages ~ 146” from CE RR Image 29 Slots 29 - 25 Dusting on packages ~ 104” from CE RR Image 30 Slot 30 Foreign material in vent slot ~ 78” from CE RR Imag
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 56c510ad4cfe7ba23f1b7ca89a492e0c | 466 | 2022-05-25 | Inspection | Field | MAGIC Inspection | 6 | Centering Ring, Gooseneck, MAGIC Inspection, Main Lead, Pole Jumper, Sub-slots | Image 78 CE RR Pole jumper 270 deg.; Image 91 CE RR Loose blocking between coil 6 and centering ring between 90 -0 deg.; Image 92 CE RR Loose block between coil 6 and centering ring between 90 to 0 deg.; Possible misalignment Image 93 CE RR Pole jumper and sub slots 90 deg.; Image 100 CE RR Main lead and coil jumpers 180 deg. |  | MAGIC Inspection ¦ Centering Ring ¦ Gooseneck ¦ Main Lead ¦ Pole Jumper ¦ Sub-slots | . Image 78 CE RR Pole jumper 270 deg. Image 79 CE RR Turns and insulation 270 deg. Image 80 CE RR Turns and insulation 270 deg. Image 81 CE RR Sub slot entrance 270 deg. Image 82 CE RR Sub slot cover button 270 deg. Image 83 CE RR Sub slot cooling hole 270 deg. Image 84 337X752 Photo ID g GE Power Inspection & Life Extension Services Magic Photo I.D.Worksheet Job # 10350370 1 River Road, Bldg. 55 Rm. 263 Generator # 337X752 Schenectady, New York 12345 Date 04-11-22 Office: (518) 385-1751, 8*235-
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | dc70311713f0b15073e4015f5b4123f7 | 340 | 2022-05-25 | Repair | Stator | Red Eye Repair | 6 | Core, End-winding, Greasing, High Voltage Bushings, Red Eye Repair, Water Ingress | Evidence of movement in the form of dusting/greasing was observed in multiple locations of the end winding.; Greasing is the result of dust mixed with oil contamination.; Hardware and core compression nuts were locked in place.; There was negligible oil contamination, however there were signs of water ingress in the belly and on the walls of the generator.; Corrosion and rust found in the belly could be a contributor of the red dust observed in stator core and on the end windings. |  | Red Eye Repair ¦ Core ¦ End-winding ¦ Greasing ¦ High Voltage Bushings ¦ Water Ingress | The end winding support system showed no indication of broken components or loose hardware. Negligible oil contamination and partial discharge was observed but moderate dust contamination was found throughout. A section was cleaned to serve as a baseline for the next inspection at the 9 o’clock position. Evidence of movement in the form of dusting/greasing was observed in multiple locations of the end winding. Majority of the findings being connection ring blocks and ties. Greasing is the result
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | ba84c624f06d8af0b6703a2ef84a2ee6 | 382 | 2022-05-25 | Inspection | Field, Stator | MAGIC Inspection | 5 | Amortisseur, Amortisseur Migration, Field Body, MAGIC Inspection, Wedges | The blockage was due to amortisseur migration.; A PAC case was submitted for this migration discovery (ER-20220409-0300) and engineering recommended that a full field body vent map be conducted in addition to information about the unit, such as history, vibration and temperature. | ER-20220409-0300 | MAGIC Inspection ¦ Amortisseur ¦ Amortisseur Migration ¦ Field Body ¦ Wedges ¦ ER-20220409-0300 | Major radial vent duct blockage was observed on the collector end (CE) and turbine end (TE) of the field. The blockage was due to amortisseur migration. Limitations of the MAGIC robot inhibited access to all field vents; therefore we were unable to determine the exact percentage of vents blocked. A single fully blocked vent is not overly concerning but multiple blocked vents could lead to coils overheating, insulation failure, thermal sensitivity, and vibration. A PAC case was submitted for this
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | 91225d4d652819b0fa6166b5d7255664 | 379 | 2022-05-25 | Electrical | Stator | Winding Resistance | 5 | Focused Generator Inspection, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | (a) Rev 2.2 - 03/11/2020 GT3 Stator Winding Resistance Moss… Dynegy Moss Landing / Unit 3 337X752 W E D G E S W E D G E S W E D G E S W E D G E S CE 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 TE S 1 88 92 91 |  | Winding Resistance ¦ Focused Generator Inspection ¦ Stator Winding ¦ Wedge Tightness Test ¦ Wedges | . 4. When comparing to calculated values, each phase should be within +/- 5% of the calculated resistance for that phase. D3162041 Sheet: (a) Rev 2.2 - 03/11/2020 GT3 Stator Winding Resistance Moss… Dynegy Moss Landing / Unit 3 337X752 W E D G E S W E D G E S W E D G E S W E D G E S CE 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 TE S 1 88 92 91 99 98 93 100 100 100 100 99 97 1 S L 2 93 94 94 100 100 94 100 100 100 100 100 99 2 L O 3 100 87 100 100 96 100 100 100 10
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | d4efcf7b06a1d7d2f2a08fa481c910bf | 14 | 2022-05-25 | Inspection | Stator | Wedge Tightness Test | 4 | Focused Generator Inspection, MAGIC Inspection, Wedge Tightness Test, Wedges |  |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Wedges | • Perform a stator wedge tightness integrity test at every minor or major outage to compare results and identify problems inside the slot support system over time. If a rotor-in inspection is chosen by the customer next outage, it is recommended to perform the wedge test using the MAGIC robot that measures deflection opposed to hardness for increased accuracy.
UNI036483 | Moss Landing | Field_Service_Report_ProjectID_A-1376570_EV-113525_C-10350370.pdf | 297604 | Gas Turbine | d8555701dd8f19b3c11d663f8653e484 | 340 | 2022-05-25 | Inspection | Stator | MAGIC Inspection | 4 | Core, Lamination Damage, MAGIC Inspection, Wedges | An in-situ visual inspection of the core was conducted using MAGIC (Miniature Air Gap Inspection Crawler).; The MAGIC robot was able to assess the core inner diameter condition by looking for space block migration, evidence of loose/damaged wedges, bar movement, and oil contamination.; Visually, the core appeared in good health with negligible signs of lamination damage.; Moderate dust contamination was found throughout the core. | GEK103566 | MAGIC Inspection ¦ Core ¦ Lamination Damage ¦ Wedges ¦ GEK103566 | An in-situ visual inspection of the core was conducted using MAGIC (Miniature Air Gap Inspection Crawler). The MAGIC robot was able to assess the core inner diameter condition by looking for space block migration, evidence of loose/damaged wedges, bar movement, and oil contamination. Visually, the core appeared in good health with negligible signs of lamination damage. Moderate dust contamination was found throughout the core. The dust appears red in color and more concentrated at the lamination
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | b807249fc16d15d7ddb00885fa50a3e5 | 213 | 2022-05-22 | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 26 | 10-minute 5000 VDC Megger PI, AC Impedance, Collector Rings, DC Leakage, DLRO, End Shield, End-winding, Fan Blades, Field Body, Flux Probe Resistance, Flux probe resistance, HVB cleaning, High Voltage Bushings, Hydrogen Seal Assembly, Loose End-winding Blocking, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, RTD Ohmic resistance and 1-minute Megger, Red Eye Repair, Red eye repair on end winding, Retaining Rings, Seal Rings, Visual inspection using MAGIC robot and borescope, Winding Resistance, Winding resistance DLRO | Due to the findings of loose/missing end-winding blocking in the field (generator rotor), engineering has deemed it not suitable for service and recommended a field out, retaining rings off repair to address the issues.; · Visual inspection using MAGIC robot and borescope · RTD Ohmic resistance and 1-minute Megger · Flux probe resistance · Winding resistance DLRO · 10-minute 5000 VDC Megger PI · DC Leakage · HVB cleaning · Red eye repair on end winding Fiel; · Visual and borescope inspection (retaining rings on) · Winding resistance DLRO · AC Impedance · 10-minute 500 VDC Megger PI · Collector ring cleaning Engineering PAC cases submitted:; · ER-20220406-1521 – Collector Brushes Chipped/shattered · ER-20220406-1428 – Loose/Broken Field Endwinding Blocking · ER-20220408-1091 – Red Core dusting (Documentation purposes only) The Generator was disassembled at the Collector End & T; • The new seal rings were measured & blue contact checked. | ER-20220406-1428, ER-20220406-1521, ER-20220408-1091 | Red Eye Repair ¦ 10-minute 5000 VDC Megger PI ¦ AC Impedance ¦ Collector Rings ¦ DC Leakage ¦ DLRO ¦ End Shield ¦ ER-20220406-1428 ¦ ER-20220406-1521 | The following section of the report documents all work performed on unit 337X753 (GT4) at Dynegy Corporation, LLC – Moss Landing Power Plant located in Moss Landing, California. The scheduled outage was started on April 03, 2022 and finished April 13, 2022. The intent of this section is to assess the current generator condition and ensure it can safely return to service. Due to the findings of loose/missing end-winding blocking in the field (generator rotor), engineering has deemed it not suitab
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | bda8eb5e969b9d6e8c988b4c9b9cd4b5 | 228 | 2022-05-22 | Repair | Stator | Red Eye Repair | 12 | Belly Bands, Belly band inspection, Core, Core Tightness Test, Core tightness test, End-winding, Focused Generator Inspection, Greasing, Keybars, Red Eye Repair, Water Ingress, Wedges | • Continue to monitor the generator core during normal operation and visually inspect the core at the next minor or major outage.; A belly band inspection and core tightness test of GT4 is recommended to check for signs of a loose core or loose belly bands.; • Inspect slot exits for signs of bar movement thoroughly during next outage to determine if greasing has increased.; • Re-examine core wedges with gaps next outage to ensure gaps haven't increased.; End Winding 6 o'clock End Winding 12 o'clock End Winding 9 o'clock Slight dusting CR 1230 Bar Ties Dusting Binding Band Clearance Water Ingress Generator Walls Blocking from field Connection Ring Heavy Greasing 8 o clock (2) Axial Supprt Ti | GEK103566 | Red Eye Repair ¦ Belly Bands ¦ Belly band inspection ¦ Core ¦ Core Tightness Test ¦ Core tightness test ¦ End-winding ¦ GEK103566 | but nothing was found. Recommendation Description: • Continue to monitor the generator core during normal operation and visually inspect the core at the next minor or major outage. A belly band inspection and core tightness test of GT4 is recommended to check for signs of a loose core or loose belly bands. A Harmonic Noise Index Test should be performed if there is any indication of a change or increase in stator noise during operation. • Inspect slot exits for signs of bar movement thoroughly d
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 40d4082a9ad429e089844d592249408a | 331 | 2022-05-22 | Inspection | Field, Stator | MAGIC Inspection | 10 | Centering Ring, End-winding, Gooseneck, Greasing, MAGIC Inspection, Main Lead, Pole Jumper, Retaining Rings, Sub-slots, Wedges | Image 52 CE RR Raised blocking between centering ring and coils 6 near 270 deg.; Image 55 CE RR Pole jumper 270 deg Image 56 CE RR Pole jumper 270 deg.; Image 61 CE RR Main lead gooseneck and hardware 0 deg.; Image 62 CE RR Main lead brazing and lock nut 0 deg.; – one block laid over Image 74 CE RR Main lead gooseneck and hardware 180 deg. |  | MAGIC Inspection ¦ Centering Ring ¦ End-winding ¦ Gooseneck ¦ Greasing ¦ Main Lead | . Image 52 CE RR Raised blocking between centering ring and coils 6 near 270 deg. Image 53 CE RR Turns and insulation 270 deg. Image 54 CE RR Turns and insulation 270 deg. Image 55 CE RR Pole jumper 270 deg Image 56 CE RR Pole jumper 270 deg. Image 57 CE RR Sub slot entrance and slot armor 270 deg. Image 58 CE RR Sub slot cover button 270 deg. Image 59 CE RR Sub slot cooling hole 270 deg. Image 60 CE RR Rub marks on forging between coil 3 and 4 between 0 and 270 deg. Image 61 CE RR Main lead goo
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | dfd6b0448b03cb980c58ef133777053f | 227 | 2022-05-22 | Repair | Stator | Red Eye Repair | 10 | Belly Bands, Core, Core Tightness Test, Core tightness test, End-winding, Focused Generator Inspection, Greasing, High Voltage Bushings, Red Eye Repair, Water Ingress | Red dust was found throughout the core and a PAC case was submitted for documentation purposes because similar dusting was observed last outage.; A belly band and core tightness test would have to be conducted to confirm it is not dust caused by a loose core.; There was no reported concern about a noisy core, nor was there evidence of dusting/greasing between core laminations.; Evidence of movement in the form of dusting/greasing was observed in multiple locations of the end winding.; Greasing is the result of dust mixed with oil contamination. |  | Red Eye Repair ¦ Belly Bands ¦ Core ¦ Core Tightness Test ¦ Core tightness test ¦ End-winding ¦ Focused Generator Inspection | The end winding support system showed no indication of broken components or loose hardware. Negligible oil contamination and partial discharge was observed. Red dust was found throughout the core and a PAC case was submitted for documentation purposes because similar dusting was observed last outage. A belly band and core tightness test would have to be conducted to confirm it is not dust caused by a loose core. There was no reported concern about a noisy core, nor was there evidence of dusting/
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 70f25770a7a77b30a0c52a1c52bbadcc | 17 | 2022-05-22 | Inspection | Stator | Core Tightness Test | 8 | Belly Bands, Belly band inspection, Core, Core Tightness Test, Core tightness test, Focused Generator Inspection, Greasing, Wedges | • Continue to monitor the generator core during normal operation and visually inspect the core at the next minor or major outage.; A belly band inspection and core tightness test of GT4 is recommended to check for signs of a loose core or loose belly bands.; • Inspect slot exits for signs of bar movement thoroughly during next outage to determine if greasing has increased.; • Re-examine core wedges with gaps next outage to ensure gaps haven't increased. | GEK103566 | Core Tightness Test ¦ Belly Bands ¦ Belly band inspection ¦ Core ¦ Core tightness test ¦ Focused Generator Inspection ¦ GEK103566 | • Continue to monitor the generator core during normal operation and visually inspect the core at the next minor or major outage. A belly band inspection and core tightness test of GT4 is recommended to check for signs of a loose core or loose belly bands. A Harmonic Noise Index Test should be performed if there is any indication of a change or increase in stator noise during operation. • Inspect slot exits for signs of bar movement thoroughly during next outage to determine if greasing has incr
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | f095dfbb36c87ce0fa834d4fe200f9ef | 329 | 2022-05-22 | Inspection | Field, Stator | MAGIC Inspection | 8 | Centering Ring, Gooseneck, MAGIC Inspection, Main Lead, Pole Jumper, Step Iron, Sub-slots, Wedges | (518) 385-3178 Generator Specialist Steve Proctor Cole Blezard Location Comments Photo Identification Slots 29 - 25 TE step iron Image 01 Slots 30 - 32 Overview of TE end wedges – dowels not flush with wedges Image 02 Slot 31 Overview of pa; Overview of packages, wedges, and field ~ 50” from CE RR Image 13 Slot 15 TE end wedge and dowel pin Image 14 Slots 12 - 8 Dusting on packages ~ 106” from CE RR Image 15 Slots 6 - 2 Dusting on packages ~ 60” from CE RR Image 16 Slots 6 - 2 ; Overview of packages, wedges, and field ~ 90” from CE RR Image 18 Slots 1 - 57 TE step iron and end wedges Image 19 Slots 1 - 57 Overview of packages and vent slots ~ 152” from CE RR Image 20 Slot 2 Foreign material in slot ~ 106” from CE R; Overview of packages, wedges, and field ~ 85” from CE RR Image 23 312 deg.; Overview of CE end wedges, RR, step iron, balance weight, and field Image 34 Slot 24 Some of the wedges appear to have excess paint on surface Image 35 Slot 18 Gap between CE end wedge and first body wedge @ CE several like this around unit |  | MAGIC Inspection ¦ Centering Ring ¦ Gooseneck ¦ Main Lead ¦ Pole Jumper ¦ Step Iron | See content below. g GE Power Inspection & Life Extension Services Magic Photo I.D.Worksheet Job # 10350372 1 River Road, Bldg. 55 Rm. 263 Generator # 337X753 Schenectady, New York 12345 Date 04-08-22 Office: (518) 385-1751, 8*235-1751 Operator Ernie Hires Fax: (518) 385-3178 Generator Specialist Steve Proctor Cole Blezard Location Comments Photo Identification Slots 29 - 25 TE step iron Image 01 Slots 30 - 32 Overview of TE end wedges – dowels not flush with wedges Image 02 Slot 31 Overview of
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 2cf615be0b1546659527cb1d7101c056 | 227 | 2022-05-22 | Inspection | Stator | MAGIC Inspection | 5 | Core, Greasing, Lamination Damage, MAGIC Inspection, Wedges | An in-situ visual inspection of the core was conducted using MAGIC (Miniature Air Gap Inspection Crawler).; The MAGIC robot was able to assess the core inner diameter condition by looking for space block migration, evidence of loose/damaged wedges, bar movement, and oil contamination.; Visually, the core appeared in good health with negligible signs of lamination damage.; Several wedge gaps were found in slot between the core wedge and end wedge of the Turbine End.; Though gaps are concerning, the wedge map showed the affected wedges tight. |  | MAGIC Inspection ¦ Core ¦ Greasing ¦ Lamination Damage ¦ Wedges | An in-situ visual inspection of the core was conducted using MAGIC (Miniature Air Gap Inspection Crawler). The MAGIC robot was able to assess the core inner diameter condition by looking for space block migration, evidence of loose/damaged wedges, bar movement, and oil contamination. Visually, the core appeared in good health with negligible signs of lamination damage. Several wedge gaps were found in slot between the core wedge and end wedge of the Turbine End. Though gaps are concerning, the w
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 4a00c794108254f95518e4654f993ad1 | 258 | 2022-05-22 | Inspection | Field | Field Findings Review | 5 | Centering Ring, Gooseneck, Retaining Rings, Turn Insulation Migration, Turn Jumper | A borescope inspection was performed to assess the condition of the CE end windings (retaining rings on).; The rib connecting coil blocks between coil 5-6 (0 degree) broke over the turn-turn jumper;; The snapped rib connection piece was stuck between coil 6 and the centering ring.; Pole-to-pole jumpers, turn-to-turn jumpers, main leads, and gooseneck terminal connections were found to be free of cracks.; No major turn insulation migration was found, the coil stacks appeared aligned and did not present obvious signs of distortion yet. | ER-20220406-1428 | Field Findings Review ¦ Centering Ring ¦ Gooseneck ¦ Retaining Rings ¦ Turn Insulation Migration ¦ Turn Jumper ¦ ER-20220406-1428 | A borescope inspection was performed to assess the condition of the CE end windings (retaining rings on). Upon inspection, major damage was observed. The rib connecting coil blocks between coil 5-6 (0 degree) broke over the turn-turn jumper; Coil 1-2 block (0 degree pole) snapped at the rib connection, became dislodged, and was found in the belly of the generator. It’s connecting block was loose and laying on its side. The snapped rib connection piece was stuck between coil 6 and the centering r
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 89dbaab12a32221376a3f9a10d5b9345 | 255 | 2022-05-22 | Electrical | Stator | Winding Resistance | 5 | Focused Generator Inspection, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | (a) Rev 2.2 - 03/11/2020 GT4 Stator Winding Resistance Moss… Dynegy Moss Landing / unit 4 337X753 W E D G E S W E D G E S W E D G E S W E D G E S CE 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 TE S 1 99 70 91 |  | Winding Resistance ¦ Focused Generator Inspection ¦ Stator Winding ¦ Wedge Tightness Test ¦ Wedges | . 4. When comparing to calculated values, each phase should be within +/- 5% of the calculated resistance for that phase. D3162041 Sheet: (a) Rev 2.2 - 03/11/2020 GT4 Stator Winding Resistance Moss… Dynegy Moss Landing / unit 4 337X753 W E D G E S W E D G E S W E D G E S W E D G E S CE 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 TE S 1 99 70 91 75 92 77 91 94 94 94 91 92 1 S L 2 100 98 74 73 77 74 100 97 100 93 99 100 2 L O 3 97 97 98 95 94 79 99 96 95 94 92 95 3 O
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 76b8f090d16231e74b8c209bcc0a409c | 246 | 2022-05-22 | Inspection | Stator | Wedge Tightness Test | 5 | Core, Focused Generator Inspection, MAGIC Inspection, Wedge Tightness Test, Wedges | The MAGIC robot performed a partial wedge tightness test.; A wedge map was created to represent the stator core on a 2D plane and can be found in the datasheet below;; The results of this wedge tightness test are relatively worse than the previous test performed in 2015.; however a full map was not created, nor were end wedges accessible, therefore it cannot be confirmed. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Wedges | The MAGIC robot performed a partial wedge tightness test. Due to the flux probe location, slot 32 was bypassed completely and slot 33 was only partially tapped. A wedge map was created to represent the stator core on a 2D plane and can be found in the datasheet below; Green indicates tight, yellow indicates hollow, red indicates loose. The results of this wedge tightness test are relatively worse than the previous test performed in 2015. From the data collected, technically the unit is within GE
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 29db183e4685dd1a33232b5fed295fea | 220 | 2022-05-22 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | (a) Rev 0.0 - 09/03/93 GE Energy Proprietary Information CE OIL DEFLECTOR ALIGNMENT g Bearing To Journal Alignment Collector End Date(m/d/y) 4/12/2022 Turbine Serial No. |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . If it is less than 0.005 inches[0.13 mm] contact Product Service for disposition. GE Proprietary – Non-Public Not to be distributed or reproduced to third parties without prior GE approval. D3165012 Sheet: (b) Rev 3.5 - 03/24/2022 D3165012 H2 SEALS & SPRINGS Oil Deflector CE Alignment Date (m,d,y) 4/12/2022 Turbine Serial No. 297605 Prepared by SCOTT CHAPIN Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Median Min. Max Top Bottom Sides CE OUTER 0.003 0.008 0.006 0.006
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 0944cf181c597219c83932d63d9572e3 | 17 | 2022-05-22 | Inspection | Stator | Wedge Tightness Test | 4 | Focused Generator Inspection, MAGIC Inspection, Wedge Tightness Test, Wedges |  |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Wedges | • Perform a stator wedge tightness integrity test at every minor or major outage to compare results and identify problems inside the slot support system over time. If a rotor-in inspection is chosen by the customer next outage, it is recommended to perform the wedge test using the “MAGIC I” robot that measures deflection opposed to hardness for increased accuracy.
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 098c95e1e58dbae7acde7ec8f4e59cab | 274 | 2022-05-22 | Electrical |  | DLRO; Winding Resistance | 3 | DLRO, Polarization Index, Winding Resistance | OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 9.95 1.70 5.85 20.24 3.60 5.62 30.59 5.50 5.56 40.59 7.40 5.49 49.89 9.00 5.54 60.78 10.50 5.79 70.20 12.50 5.62 79.70 14.00 5.69 90.30 15.70 5.75 100.20 17.20 5.83 110.10 18.70 5.89 119.90; 337X759 Date NA Turning Gear Hrs Check per TM4010 8 Point Resistance Check (Optional - Except for 390H and certain 450H & 9A5 units) - TM4010 and TM4030 Factory @25 ºC Megger S1-1052 10kV DLRO #37 Instrument Description 7FH2 Number of Start | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | This test was performed on the field to determine the winding’s impedance at various voltages between 0-120 volts AC. Under some circumstances it is possible to detect the presence of shorted turns or changes in the number of shorted turns in the winding by changes in impedance at the various test voltages when compared to data taken previously. The graph obtained suggests no shorted turns in this field. Field Measurements Date (m/d/y) Turbine No.: 297605 Prepared by: Equipment Generator No.: 33
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 539fdd6ec3b859df62a68e3538dddf62 | 252 | 2022-05-22 | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | Slot 50, Phase 3-6, Collector End DT-GSA-6 Cold Air - Turbine End DT-GGC-10 Frame Hot Gas - Center Frame Common Cold Gas Collector Air - Hot Collector Air - Cold Frame Cold Gas Stator Winding Center Stator Winding CE Stator Winding TE Locat; RTD Location Desription Rev 3.2 - 07/21/2021 GT4 RTD Moss Landing Stator Winding Insulation Resistance / HV Proof Tests Date 04/10/2022 Generator No.:; Left (CE) Center (CE) Right (CE) - - - - - - - - - - - - - - - Failed test at [kV/Time(sec)] Excitation Voltage (Volts) NA Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed a | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | . Prepared By Turbine Serial No. Project ID RTD INSULATION RESISTANCE TEST RESULTS (MEGOHMS) # 1 thru # 29 = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # t
UNI036484 | Moss Landing | Field_Service_Report_ProjectID_A-1377354_EV-121543_C-10350372.pdf | 297605 | Gas Turbine | 0858ab28373b89ee35bfbfb25f700d39 | 224 | 2022-05-22 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | (a) Rev 0.0 - 09/03/93 GE Energy Proprietary Information TE OIL DEFLECTOR ALIGNMENT g Bearing To Journal Alignment Turbine End Date(m/d/y) 4/12/2022 Turbine Serial No. |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . Cleaned Joints Dowels Insp per GN-2151 Top T. Left B. Left T. Right B. Right "A" Gap "A" Gap dimensions Bottom C A B B C D E AIR SIDE HYDROGEN SIDE OIL DEFLECTOR A ST00065 D316512 Sheet: (a) Rev 2.2 - 08/28/2018 D316512 H2 SEAL CASING TE Oil Deflector TE Alignment Date (m,d,y) 4/12/2022 Turbine Serial No. 297605 Prepared by SCOTT CHAPIN Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Median Min. Max Top Bottom Sides TE OUTER 0.009 0.009 0.002 0.004 0.018 0.008 0.009 0.0
UNI035964 | Hanging Rock Energy Facility | Field_Service_Report_ProjectID_A-1675148_EV-114985_C-10362914.pdf | 298127 | Gas Turbine | 83e0e40721e2cf38732aba258399f7ba | 4 | 2022-05-16 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  | ER-20220409-0248 | Focused Generator Review ¦ Wedges ¦ ER-20220409-0248 | During the EBI it was found that the lower left side ISR housing had 3 bolts loose along with finding 2 stray bolts lying on the S1N cooling cavities. ER-20220409-0248 was submitted in response to the found loose bolts. Closing notes stated “It is recommended to follow TIL-2302 recommendations. Since 5 or less bolts are still fully engaged in the seal housing install new bolts with nordlock or wedge lock washers only in the locations of missing / slightly backed out bolts. Account for and recove
UNI036592 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1722784_EV-132410_C-10369435.pdf | 297255 | Gas Turbine | 0ce0e83f314da47907682b37f3a8f6b7 | 139 | 2022-05-03 | Inspection | Stator | Focused Generator Review | 2 | Core, Wedges | NA – Parts were not inspected during this inspection NV – No visible indications / abnormal findings AF – Observed visible / abnormal finding Collector End Components Inspected YES/NO Disposition Peripheral List Below Inspected YES/NO Dispo | ER-20191017-1295, ER-20200320-0817, ER-20201009-0621, ER-20210413-0680 | Focused Generator Review ¦ Core ¦ Wedges ¦ ER-20191017-1295 ¦ ER-20200320-0817 | . Foreword This report describes and documents the borescope examination of the unit that is described in the inspection details section listed on page 3; with respect to abnormal depositing, foreign object damage (FOD) and normal wear. A 4.5m X 6.1mm flexible videoscope was utilized for the examination. The interior of the unit was illuminated by employing fiberoptics to transmit light from an external light source. Color images were captured with the GE Inspection Technologies/Everest Imaging
UNI035717 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1698020_EV-114122_C-10366912.pdf | 298236 | Gas Turbine | f0b6c5334a9de9b96468bad0b6b10639 | 68 | 2022-04-28 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  | ER-20210421-1039, ER-20220121-0673, ER-20220316-0971 | Focused Generator Review ¦ Seal Rings ¦ ER-20210421-1039 ¦ ER-20220121-0673 | . - Rub on R3, R5-S9, R11-R13. - Corrosion on S3, S15, R9, R15-R17. - Discoloration on R4. - FOD on S6, R10, R12, R15, R17. - Rub on R15, R17. - Twisting on S15, R16. 2 Combustion Observed - Deposits on Can 1, Can 3-6, 8-14. - Wear on Can 2, 3 - Linear indication on Can 7 3 Hot Gas Path Observed -TBC spallation on S1N, S1B, S2B. - Discoloration on S1N. - S1N seal ring bolt 7 was missing but found and retrieved - Oxidation/erosion on S2N. - Deposits on S3N/S3B. Lower exhaust flex seals were found
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1682960_EV-114155_C-10364457.pdf | 297256 | Gas Turbine | f5e511818a3973f78864108c7274969f | 15 | 2022-04-25 | Inspection | Field, Stator | MAGIC Inspection | 6 | End-winding, Fan Blades, Gooseneck, MAGIC Inspection, Pole Jumper, Retaining Rings | Recommend to perform a full visual inspection of CE Field End turns and perform electrical testing of the field winding insulation at this time during the MAGIC inspection in the Spring of 2023.; A retaining rings off inspection and repair of the damaged jumper is also recommended the next time the field is removed from the stator.; Lamar Power Unit 12 Field End Turns Collector End – Field End Turns – Lamar Power Plant – Unit 12 – Report Photos P a g e 4 ¦ 8 Borescope guide tube was fitted between the fan blades to access the end winding compartment.; March 2022 Lamar Power Unit 12 Field End Turns Collector End – Field End Turns – Lamar Power Plant – Unit 12 – Report Photos P a g e 7 ¦ 8 Photo of 180-degree Gooseneck and Turn 2 to Turn 3 Jumper – No problems observed.; Side view of the 180-degree Gooseneck – no problems observed. |  | MAGIC Inspection ¦ End-winding ¦ Fan Blades ¦ Gooseneck ¦ Pole Jumper ¦ Retaining Rings | The next six month periodic inspection can be skipped. Recommend to perform a full visual inspection of CE Field End turns and perform electrical testing of the field winding insulation at this time during the MAGIC inspection in the Spring of 2023. A retaining rings off inspection and repair of the damaged jumper is also recommended the next time the field is removed from the stator. GEGEGE GE Confidential and Proprietary Information. Not to be copied, reproduced, or distributed without GE prio
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1682960_EV-114155_C-10364457.pdf | 297256 | Gas Turbine | 45a47b9d17bc7f8b6d23eee6342757f1 | 14 | 2022-04-25 | Inspection | Field, Hydrogen Seals | MAGIC Inspection | 3 | End Shield, MAGIC Inspection, Retaining Rings | Entry point into the end turns of the field was through the inspection port on the CE-end shield of the generator.; The generator is scheduled to undergo a MAGIC inspection in approximately 1 year.; Recommend to perform a full visual inspection of CE Field End turns and perform electrical testing of the field winding insulation at this time during the MAGIC inspection in the Spring of 2023.; A retaining rings off inspection and repair of the damaged jumper is also recommended the next time the field is removed from the stator. | ER-20220310-0018 | MAGIC Inspection ¦ End Shield ¦ Retaining Rings ¦ ER-20220310-0018 | This is a follow up inspection to view the jumper between Turn 4 and Turn 5 (180 degree pole) and see if the damage/distortion has worsened since the last inspection (approximately 6 months of operation). A borescope was used to obtain photographs. Entry point into the end turns of the field was through the inspection port on the CE-end shield of the generator. The field poles were aligned so that the 180-degree pole was sitting roughly at the 6 o'clock position. Please note that this inspection
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1682960_EV-114155_C-10364457.pdf | 297256 | Gas Turbine | feddaf1be0940fdcb0a4a17b7c5f77fd | 9 | 2022-04-25 | Inspection | Field | MAGIC Inspection | 2 | Gooseneck, MAGIC Inspection | Inspection on other jumpers (coil-to-coil, pole-to-pole) and MTS gooseneck connections is also recommended in 2023. | ER-20191017-1295, ER-20200320-0817, ER-20201009-0621, ER-20220308-1100, ER-20220309-1117 | MAGIC Inspection ¦ Gooseneck ¦ ER-20191017-1295 ¦ ER-20200320-0817 | . When the parts are exposed during S3B replacement outage, closely inspect all S1Bs and report the findings to Engineering 4. S1S shows discoloration, rub distress and TBC coating loss. Site should ensure base material is in good condition with no noticeable oxidation erosion or missing material or cracks 5. S2Ns appear to be in good condition with minor TBC loss and discoloration 6. Few S2Bs show impact damages on the LE, LE SS and TE. Adhere to recommendation per ER-20220308-1100 7. S2S appea
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1682960_EV-114155_C-10364457.pdf | 297256 | Gas Turbine | 6870b0c5c7b0e5b0a9db102c1a140e6b | 500 | 2022-04-25 | Inspection | Stator | Focused Generator Review | 2 | Core, Wedges | NA – Parts were not inspected during this inspection NV – No visible indications / abnormal findings AF – Observed visible / abnormal finding Collector End Components Inspected YES/NO Disposition Peripheral List Below Inspected YES/NO Dispo | ER-20191017-1295, ER-20200320-0817, ER-20201009-0621, ER-20210413-0680 | Focused Generator Review ¦ Core ¦ Wedges ¦ ER-20191017-1295 ¦ ER-20200320-0817 | . The images included in the photo report are selected from the inspection that best represent the condition of the unit. They show typical views of the components observed. It is important to note that due to the magnification of the lens, object viewed through the videoscope may be significantly magnified. It is also important to note that videoscopes have certain minor imperfections inherent in their construction, caused by lens distortion. As a result, a surface, which is actually straight o
UNI035747 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1693582_EV-110985_C-10366340.pdf | 298015 | Gas Turbine | 28205c7a95964265ae630acc9a445b4d | 32 | 2022-04-20 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  | ER-20220311-1069 | Focused Generator Review ¦ Seal Rings ¦ ER-20220311-1069 | . Borescope ports in the turbine casing allowed viewing of the first stage nozzle, first stage buckets, second stage nozzle, second stage buckets, third stage nozzle, and third stage buckets. 3. Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 1108-R1 CAST SEGMENTED TURBINE NOZZLE ACCEPTANCE GUIDELINES TIL 1502-2R1 7F AND 9F AFT END COMPRESSOR RUBS TIL 1509-R4 F-CLASS FRONT END (R0, S0, AND R1) COMPRESSOR INSPECTIONS TIL 1562-R1 HEAVY DUTY GAS TURBINE SHIM MIGRATION AND LO
UNI035717 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1676598_EV-114845_C-10363239.pdf | 298236 | Gas Turbine | 3a7add0bd1e737a49a0b1ac2573609e8 | 27 | 2021-12-09 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . 3. Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 1565 Safety Precautions to follow while working on Variable Guide Vanes TIL 2302 S1N Inner Support Rind Seal Housing Inspection TIL 1769 F Class Aft Stator Rocking Inspection TIL 1850-R2 F Class Shrouded Stator 17 Inspection TIL 2049-R2 F Class Inlet Guide Vane to Rub Ring Rubbing TIL 1582-R2 F and H Class Lift Oil Hose Inspection 4. Engineering Requests Engineering Requests (ER) GE Power Inspection & Life Extension Ser
UNI036147 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1672552_EV-107128_C-10362310.pdf | 297546 | Gas Turbine | 57a81c8b1fcbd72a08781b567b02d7d6 | 180 | 2021-12-07 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | Date 11/7/21 Turbine S/N 297546 Prepared by Therrien FSR # NA Sketches Enclosed? No Photos Enclosed? Yes Chamber # S/N # Inspected Seal Condition Seal Diameter Disposition 1 NA W NA RN-GE 2 NA W NA RN-GE 3 NA W NA RN-GE 4 NA W NA RN-GE 5 NA W NA RN-GE 6 NA W NA RN-GE 7 NA W NA RN-GE 8 NA W NA RN-GE 9 NA W NA RN-GE 10 NA W NA RN-GE 11 NA W NA RN-GE 12 NA W NA RN-GE 13 NA W NA RN-GE 14 NA W NA RN-GE Comments: Typical wear no out of the ordinary conditions Typical wear no out of the ordinary condit
UNI036147 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1672552_EV-107128_C-10362310.pdf | 297546 | Gas Turbine | 6de359dc0c9d55156900323083aecffa | 293 | 2021-12-07 | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection |  |  | MAGIC Inspection | . Complex Tooling Inspection Checklist Tool Name Pre-Use Tool Inspection Step Task Quantity Yes/No/NA Verified By: Initial/Date 1 All connecting Hardware (nuts, bolts, pins, etc.) have been checked for tightness and are secure. 2 All unused holes in the tool have been identified and marked 3 All tie wraps on the tool have been counted and checked for secureness. 4 All air and hydraulic lines and connections have been bled and leaks checked and are mechanically secured. 5 All air and hydraulic cy
UNI035721 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1676608_EV-121640_C-10363240.pdf | 298235 | Gas Turbine | 00dbdfd5be832d48075cbbc5e39e8be6 | 47 | 2021-12-02 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . 3. Technical Information Letters (TILs) Inspected TIL Number TIL Title TIL 1565 Safety Precautions to follow while working on Variable Guide Vanes TIL 2302 S1N Inner Support Rind Seal Housing Inspection TIL 1769 F Class Aft Stator Rocking Inspection TIL 1850-R2 F Class Shrouded Stator 17 Inspection TIL 2049-R2 F Class Inlet Guide Vane to Rub Ring Rubbing TIL 1582-R2 F and H Class Lift Oil Hose Inspection 4. Engineering Requests Engineering Requests (ER) GE Power Inspection & Life Extension Ser
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1686570_FSP-313453_C-10365083.pdf | 297493 | Gas Turbine | f5c65da5e4509f3eb75dac2b181d6afd | 9 | 2021-11-29 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | It was determined that none of the grooves exceeded more the 2 mils.; The upper and lower half oil deflectors were inspected and found in good condition.; The oil deflectors cleaned and reused Turbine End Lower Half Turbine End Upper Half Journal As Found Condition Journal As left Condition 3.1.3 Generator Collector End Bearings Part Condition:; A refurbished bearing was installed, and the oil deflectors were cleaned and reused Collector End Lower Half Colector End Upper Half Collector End Journal 4 Quality Checkpoint (QCP) 4.1 Attachments See content below. |  | Oil Deflector Alignment ¦ Oil Deflectors | . The lower half was found to be in poor condition with heavy wear, material loss, and signs of over temp. The journal exhibited scratches and some minor grooving. It was determined that none of the grooves exceeded more the 2 mils. The upper and lower half oil deflectors were inspected and found in good condition. The journal was lapped to remove high spots and a refurbished bearing was installed. The oil deflectors cleaned and reused Turbine End Lower Half Turbine End Upper Half Journal As Fou
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1686570_FSP-313453_C-10365083.pdf | 297493 | Gas Turbine | ab684a3391561830bf90174dcfad4013 | 16 | 2021-11-29 | Inspection | Field | Focused Generator Review | 1 | Collector Rings |  | EM2101 | Focused Generator Review ¦ Collector Rings ¦ EM2101 | . Signs of the readings were inverted if neccessary, to reflect a Standard Seasurement reading. 3. Values represent the true axis location. 4. The left and right convention is looking thowards the piece of equipment whose flange is being measured, independently to the left and right definition for the turbine or generator. VERTICAL Shaft 2 Top Bottom HORIZONTAL Shaft 1 Shaft 2 Left Right Shaft 1 Shaft 2 Shaft 1 Top Bottom VERTICAL Shaft 2 3.1 3.2 3.3 3.4 3.5 1.2 1.4 1.3 2.1 2.2 2.3 2.4 5.1=3.1-4
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | c1fff511c7320972b2ac248577f02ae4 | 186 | 2021-06-15 | Electrical | Field, Hydrogen Seals, Stator | Winding Resistance; Polarization Index | 14 | AC Impedance, Core, DC Hipot, DC Leakage, End Shield, End-winding, Fan Blades, Greasing, MAGIC Inspection, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges, Winding Resistance | Should be planned for next Outage During the outage the CE axial fan blades were removed to allow access for the MAGIC inspection.; Jeff Kuehn FieldCore Generator Specialist Approved By:; William Martin FieldCore Service Manager Kendall GTG2 _ STG2 Final Generator… 2 Work Scope GTG2:; During the MAGIC inspection, a wedge tap was also performed.; The collector-end upper half end shield was removed. |  | Winding Resistance; Polarization Index ¦ AC Impedance ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End Shield ¦ End-winding | . It was visually inspected and appeared to be in good condition. Twist and tilt was recorded and is included below. Recommendation Status: Should be planned for next Outage During the outage the CE axial fan blades were removed to allow access for the MAGIC inspection. After removal they were visually inspected with only one indication noted. The one blade with visual indication had NDE performed because the indication was in a high stress area. No findings were noted. The report is included in
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 70866bd1623a251cb7b68d98e32a4cf0 | 195 | 2021-06-15 | Electrical | Stator | DLRO; Winding Resistance | 10 | Core, DLRO, End-winding, Greasing, Loose End-winding Blocking, MAGIC Inspection, Polarization Index, Wedge Tightness Test, Wedges, Winding Resistance | of 4.8 at 10.75 GΩ *The field PASSED all electrical tests.; Remove the field at your next outage to do a more in-depth visual inspection and cleaning of the stator core;; Due to the considerable amount of greasing found on the body wedges and the vintage of this unit, a re-wedge may be considered.; Monitor greasing on end-winding blocking and ties.; Take note of any corona activity on the end-winding at the next outage interval. | GEK103566, TM2010, TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ Core ¦ DLRO ¦ End-winding ¦ Greasing ¦ Loose End-winding Blocking ¦ MAGIC Inspection ¦ GEK103566 ¦ TM2010 | . of 4.8 at 10.75 GΩ *The field PASSED all electrical tests. For readings and test data please reference Generator and Field Electrical Testing section. Kendall GTG2 _ STG2 Final Generator… 6 Recommendations/Parts GTG2: Recommendations: Remove the field at your next outage to do a more in-depth visual inspection and cleaning of the stator core; you may want to do an Equitip wedge tap as well. Due to the considerable amount of greasing found on the body wedges and the vintage of this unit, a re-w
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | fb45db2081351201d06c5e89548ce9c8 | 268 | 2021-06-15 | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 10 | Core, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges | Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Pre-outage test:; Partial Discharge 1 Stator Winding Insulation Localized deterioration X X X O 1 O-R 2 O-R 2 Visual Inspection All Visible Components within the End Winding Compartment Cleanliness, foreign material, loose or displaced parts, damage, wear, d; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Insulation Resistance (aka Megger™) and Polarization Index (PI) ; Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In 1 DC Leakage and Partial Discharge testing are optional but high |  | Polarization Index; DC Leakage ¦ Core ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings ¦ Hydrogen Seal Assembly | . Generator Turbine Generator Turbine Kendall GTG2 _ STG2 Final Generator… GEK 103566M Creating a More Effective Generator Maintenance 9 without prior permission of the copyright owner. Table 4 Recommended Stator Tests and Inspections Stator and Core Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescop e Robotic Rotor-In Pre-outage test: H2 sniff test Generator Check any H2 leaks when unit under the H2 pressure X X X-R X-R X-R Pre-outage test: Partial Disch
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 63295accbf2401d9bc077a91c92db0eb | 193 | 2021-06-15 | Electrical | Field, Stator | Winding Resistance; Polarization Index | 10 | AC Impedance, DC Leakage, Greasing, MAGIC Inspection, Polarization Index, Retaining Rings, Stator Winding, Step Iron, Turn Insulation Migration, Winding Resistance | of 9.83 at 36.63 GΩ • Stator DC Leakage and Hipot Test o Passed Electrical tests @ 39.8 kVDC with an average of 93.3 µA of leakage to ground *Stator windings PASSED all electrical tests.; Minimal signs of movement/greasing were found on the axial support system.; There was significant greasing at the end of the slot on both ends of the unit between the top bar and step iron.; Winding resistance on each phase, a 5 kVDC megger, DC leakage to 28kVDC, and Hipot 30.5kVDC were then performed on the unit.; • Stator RTD resistance and 500 VDC Insulation and Polarization Index Test o RTDs 1-3 passed electrical testing at 248.0 GΩ o RTDs 5-13 passed electrical testing at 98.0 GΩ • Stator Winding Resistance (Phase to Phase) o Passed all electrica |  | Winding Resistance; Polarization Index ¦ AC Impedance ¦ DC Leakage ¦ Greasing ¦ MAGIC Inspection ¦ Polarization Index ¦ Retaining Rings | . of 9.83 at 36.63 GΩ • Stator DC Leakage and Hipot Test o Passed Electrical tests @ 39.8 kVDC with an average of 93.3 µA of leakage to ground *Stator windings PASSED all electrical tests. For readings and test data please reference Generator and Field Electrical Testing section. Kendall GTG2 _ STG2 Final Generator… 4 STG2: Visual Inspection: A thorough visual inspection was carried out on this unit. Before initial stator inspection began, it should be noted that there was obvious oil ingress so
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 6311425a8cda436462ca64ebd39e5f88 | 266 | 2021-06-15 | Electrical | Field, Stator | DC Leakage | 7 | Core, DC Leakage, Focused Generator Inspection, Retaining Rings, Stator Winding, Wedge Looseness, Wedges | Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened materia; As the stator core is exposed during a rewind, a detailed inspection of the core is recommended including at minimum a visual inspection, EL-CID (or low flux test) and core tightness testing.; However, this is also an opportune time to perform a Core Ring Test (High Induction Test/ Core Ring Test or PULSAR) and to retighten the core compression features if/where applicable. |  | DC Leakage ¦ Core ¦ Focused Generator Inspection ¦ Retaining Rings ¦ Stator Winding ¦ Wedge Looseness | . Kendall GTG2 _ STG2 Final Generator… GEK 103566M Creating a More Effective Generator Maintenance 7 without prior permission of the copyright owner. Table 3 Rotor Removal Events or Trends Predicating Rotor Removal Required Maintenance or Repair Activities Abnormal operating events (as listed in Section 2 of this GEK) Rotor tooth and wedge inspection and repair to remove hardened material Rotor vibration trends coupled with flux probe shorted turns or blocked ventilation passages May range from
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | df20677bc2b5162d64cfb138145fe0eb | 275 | 2021-06-15 | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically constructed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . Many of the tests require special equipment that has been properly maintained and calibrated to ensure accurate results. 5 . Visual Inspection A visual inspection, performed at every inspection by an experienced individual, can uncover unit conditions previously undetected or can validate monitoring findings. In some instances, electrical testing will only detect issues when the stator and rotor insulation systems have been significantly compromised. For example, there is no definitive test fo
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 333dca058baebb5ced71b2ad197424b3 | 271 | 2021-06-15 | Electrical | Stator | DC Hipot | 5 | DC Hipot, End-winding, High Voltage Bushings, Stator Winding, Wedges | 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 5 This test does not apply to units with asphalt stator windings, GVPI windings (Global Vacuum Pressure Impregnated) or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds.; 13 Alfa coefficient test is applicable to stator winding with the flat lateral support system. |  | DC Hipot ¦ End-winding ¦ High Voltage Bushings ¦ Stator Winding ¦ Wedges | . 2 For hydrogen cooled generators Off-Line Partial Discharge Testing with the unit open to air may provide additional diagnostic information. 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators. 4 An equivalent inspection via digital trending and analysis may be suitable; contact your local GE Service Representative. Dimensional and NDT test are recommended o
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 75a5276f0668a352d3e4a7ad09027a5c | 174 | 2021-06-15 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Fan Blade J 0.047 0.038 0.062 0.061 0.057 0.049 Inner Oil Deflector; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z NA NA NA NA NA Shaft Grounding Brushes A NA NA NA Outer Oil Deflect; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H x x x x x x Fan Blade J 0.059 0.058 0.049 0.057 0.061 0.060 Inner Oil Def |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Typical As Found Air Side Cond ition Generator Field Clearance Equip Code: Collector End (Axial Fan) Date(m/d/y) 4/25/2021 Turbine Serial No. 297544 Prepared by Generator Serial No. 337X758 ERP Project ID Units recorded in Data set Notes: 1) Coupling should be the the cold setting when reading is taken. The collector brushes should ride fully on the collector rings when the unit is at running tempeature. 2) Applicable for units where the collector house has a brush seal to the shaft. 3) Left / R
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 6627f6a79b29e032f60a5532a81b830f | 271 | 2021-06-15 | Electrical | Field, Stator | AC Impedance | 5 | AC Impedance, End-winding, Gooseneck, Main Lead, Stator Winding | Phos-Free 3 H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Test Inspection Objectives and Assessment Borescope Robotic Rotor-In Borescope Robot; Table 6 Recommended Rotor Test Rotor Air Hyd Water Inspection Test Component Inspection Objectives and Assessment First Borescope Robotic Rotor-In Winding Copper Resistance Rotor Winding Checks for poor connections and breaks X X X O X X In |  | AC Impedance ¦ End-winding ¦ Gooseneck ¦ Main Lead ¦ Stator Winding | . Test requires rotor removal. Kendall GTG2 _ STG2 Final Generator… GEK 103566M Creating a More Effective Generator Maintenance 12 without prior permission of the copyright owner. Table 5 Recommended Water-Cooled Stator Leak Tests for High Oxygen Systems 1,2 What about legacy Alstom stainless steel windings?? Stator Clip-Strand Braze: Phos Containing Global Epoxy Injection or Clip-Strand Braze: Phos-Free 3 H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 638829a96eaded7cbaab85519817b2fe | 245 | 2021-06-15 | Inspection | Field | MAGIC Inspection | 5 | Gooseneck, MAGIC Inspection, Main Lead, Pole Jumper, Sub-slots | (518) 385-3178 Generator Specialist Jeff Kuehn BORESCOPE Coil to coil jumper 3 to 4 Image 45 BORESCOPE Typical view of stacking and insulation Image 46 BORESCOPE Typical view of blocking Image 47 BORESCOPE Typical view of blocking Image 48 |  | MAGIC Inspection ¦ Gooseneck ¦ Main Lead ¦ Pole Jumper ¦ Sub-slots | . 55 Rm. 263 Generator # 337X758 Schenectady, New York 12345 Date 4-18-21 Office: (518) 385-1751, 8*235-1751 Operator S. Schmeltzer / J. Kopetchny Fax: (518) 385-3178 Generator Specialist Jeff Kuehn BORESCOPE Coil to coil jumper 3 to 4 Image 45 BORESCOPE Typical view of stacking and insulation Image 46 BORESCOPE Typical view of blocking Image 47 BORESCOPE Typical view of blocking Image 48 BORESCOPE Image of opposite turns and insulation Image 49 BORESCOPE Typical view of pole to pole jumper Imag
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 3f1ad85455a142088af59f256d996e4f | 244 | 2021-06-15 | Inspection | Field, Stator | MAGIC Inspection | 5 | Greasing, MAGIC Inspection, Main Lead, Step Iron, Wedges | (518) 385-3178 Generator Specialist Jeff Kuehn Location Comments Photo Identification Slot 23 View of potential hot spot ~ 157” from CE RR Image 01 Slot 23 View of missing paint on wedge ~ 168” from CE RR Image 02 Slot 27 View of heavy grea |  | MAGIC Inspection ¦ Greasing ¦ Main Lead ¦ Step Iron ¦ Wedges | . 55 Rm. 263 Generator # 337X758 Schenectady, New York 12345 Date 4-18-21 Office: (518) 385-1751, 8*235-1751 Operator S. Schmeltzer / J. Kopetchny Fax: (518) 385-3178 Generator Specialist Jeff Kuehn Location Comments Photo Identification Slot 23 View of potential hot spot ~ 157” from CE RR Image 01 Slot 23 View of missing paint on wedge ~ 168” from CE RR Image 02 Slot 27 View of heavy greasing on end wedge @ TE RR Image 03 Slot 27 Typical view of end wedge dowel pin @ TE RR Image 04 Slot 27 Typi
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | f899512f32e0f3a4aad1f1f525ea4e9b | 165 | 2021-06-15 | Inspection | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | Should be planned for next Outage During the outage the inner and outer oil deflectors were removed from CE.; The oil deflectors were reinstalled and aligned per GE specification.; Should be planned for next Outage During the outage only the CE upper half bearing was removed to prepare for MAGIC inspection. |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | . During inspection and measurement, no issues were found. The coupling studs and nuts were hand cleaned. The studs were visually inspected and measured prior and post stretch after final alignment was completed. All nuts were visually inspected and some damaged set screws were replaced. Recommendation Status: Should be planned for next Outage During the outage the rotor was removed and inspected as part of the MI. During compressor mapping there were several minor damages found that were blend
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 030f0b23bd1a5d5f54a48b0345c4f24b | 276 | 2021-06-15 | Inspection | Field, Stator | Focused Generator Review | 4 | Centering Ring, Collector Rings, Retaining Rings, Wedges | All structural components removed as part of the rewind (wedges, retaining rings, centering rings, radial fans, axial fan hubs, collector rings, coupling rings, etc.) should also be inspected. |  | Focused Generator Review ¦ Centering Ring ¦ Collector Rings ¦ Retaining Rings ¦ Wedges | . Earlier generators may have had different start/stop configuration criteria, particularly large fossil & nuclear units. For older (25+ years) generators that have changed operating profile (base load to cyclic / peaking duty), GE Product Service should be contacted for an appropriate inspection plan. However, with proper inspections and maintenance, generators may last much longer. Common issues with aged rotor forgings are typically related to the number of start/stop cycles. Several Technica
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | db52b8871233f861bd37863a80b877ae | 202 | 2021-06-15 | Electrical |  | Winding Resistance; 10-minute Megger | 4 | 10-minute Megger, DC Leakage, Polarization Index, Winding Resistance | RTD Megger Rev 3.1 - 05/15/2020 Kendall GTG2 _ STG2 Final Generator… Armature Winding Resistance Equip Code Date (m/d/y) 4/19/2020 Turbine Serial No.; of Equipment 1 Calibration date 2 3 NA NA NA Comments Winding resistance measurements are within spec per GE procedure 533160913 Terminal Labels Turbine End Collector End Resistance Fact.; 8/31/2021 Polarization Index PI = 10min/1min D3162047 Sheet:; (a) Rev 0.0 - 05/01/05 Kendall GTG2 _ STG2 Final Generator… Armature Insulation DC Leakage Test Date(m/d/y) 4/20/2021 Generator Serial No. |  | Winding Resistance; 10-minute Megger ¦ 10-minute Megger ¦ DC Leakage ¦ Polarization Index ¦ Winding Resistance | . Prepared By Turbine Serial No. Project ID RTD INSULATION RESISTANCE TEST RESULTS (MEGOHMS) # 1 thru # 18 = megohms (Excluding OL) Megger SN: Calibration Date: 8/31/20 Due Date: Fluke SN: Calibration Date: 8/31/20 Due Date: 8/31/21 8/31/21 101579633 0631X-B1 17970.00 RTD INSULATION RESISTANCE (MEGOHMS) @ 500 Volts DC 337X758 Jeff Kuehn 297546 I01-062627 D316403 Sheet: RTD Megger Rev 3.1 - 05/15/2020 Kendall GTG2 _ STG2 Final Generator… Armature Winding Resistance Equip Code Date (m/d/y) 4/19/20
UNI036151 | KENDALL POWER STATION | Field_Service_Report_ProjectID_A-1488512_FSP-270381_C-10333878.pdf | 297544 | Gas Turbine | 358d3ef93443306af69d373e7edb3e2a | 265 | 2021-06-15 | Inspection | Hydrogen Seals, Stator | Focused Generator Review | 4 | Core, End Shield, End-winding, Wedges | The upper end shields or end plates do not require removal to permit inspection of the end winding area and the rotor remains in place.; The upper end shields or end plates may not need to be removed to permit inspection of the end winding area and the rotor remains in place.; The inspection includes a series of inspections and test (including visual, electrical, wedges assessment).; Note that this inspection may not eliminate the need to remove the rotor if an issue is discovered that requires rotor removal to correct, such as loose stator core wedges or significant end winding maintenance or repairs. |  | Focused Generator Review ¦ Core ¦ End Shield ¦ End-winding ¦ Wedges | . In addition to offline inspections and maintenance, there are online tests that can be performed to provide insight to the unit health and scope of upcoming outages. One such test is the use of flux probes to monitor the relative magnetic flux and determine if the field winding has experience shorted turns. If equipped with flux probes, at minimum a flux probe test should be performed in the planning stages for an inspection outage to help define the outage scope. Additionally, it is recommend
UNI036482 | Moss Landing | Field_Service_Report_ProjectID_A-1613270_FSP-294850_C-10350768.pdf | 270T484 | Steam Turbine | 955899493634795175895ac83208cf94 | 33 | 2021-06-14 | Mechanical | Hydrogen Seals | Blue Check | 2 | Blue Check, Seal Rings | Pressure seal head back seats were lapped and blue checked.; Allowable from FE Manual 4 1/2 Mils/Ft G I K Max Allowable Bowed? 2 0 1 2 1 2 2 0 2 2 Stem Lgth 39.75 In.; Allowable from FE Manual 6 Mils/Ft Comments:; Date STEM RUNOUT Clearance Left Reheat Stop Stem Right Left Intercept Stem Over Travel of RHSV G Stem OD Total lift of RHSV (As Found/As Left) Crew Right Jeromiha 5/13-5/20/21 As Found / Left Seal Rings OD Balance Clearance Stem OD Disk ID |  | Blue Check ¦ Seal Rings | Part Description: Reheat Stop Valve’s Combined Intercept Valve’s. Disassembled, cleaned, and inspected. Pressure seal head back seats were lapped and blue checked. Bushing were honed and try bar check. All components were NDE’ed. The seats were stoned with cracking stones heavily and required many hours of lapping. Blue contact checks on seat to dics showed good. The left side Intercept valve had thread damage on 7 studs that were removed and replaced with new studs by UPS Machining. The actuato
UNI035717 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1636080_FSP-300585_C-10355244.pdf | 298236 | Gas Turbine | 0e8e67ed9e6ae448b3b4bfe0998806c9 | 18 | 2021-06-14 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . The technical data herein is the property Inspection Summary Inspection summary table: Percent Inspected defines the approximate inspection coverage for a section or stage. Since a portion of each component in a section or stage is not visible for inspection, 100 percent inspection coverage of every component is not feasible using remote visual inspection methods. Legend: NA – Parts were not inspected. NV – No visible indications. AF – Observed visible abnormal finding Compressor % Inspected T
UNI035717 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1636080_FSP-300585_C-10355244.pdf | 298236 | Gas Turbine | a8c35ab2cc2b8b51a1a9d9c85662eca0 | 3 | 2021-06-14 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | __________ 469 3.1 Attachments __________ 469 GEGEGE BORESCOPE - 298236 OUTAGE DETAILS 1 Summary 1.1 Site Personnel Name Category Role Tim Weiser GE CSL William Mueller FieldCore SM John Dejewski FieldCore PM Joseph Harrell FieldCore FE Colin Ryan FieldCore FE Rob Losoya GE LES Borescope Technician 1.2 Executive Summary On April 8th, 2021, FieldCore & APM personnel began supporting the annual Enhanced Borescope Inspections on Block 2. During the borescope inspection on GT2A several indications w
UNI036482 | Moss Landing | Field_Service_Report_ProjectID_A-1613270_FSP-294850_C-10350768.pdf | 270T484 | Steam Turbine | a1974fb4fa4a25d726c0a052556f716d | 39 | 2021-06-14 | Mechanical |  | Blue Check | 1 | Blue Check | GEGEGE CALL OUT - 270T484 Blue check disk look Blue check on the disk seat Admission valves. |  | Blue Check | GEGEGE CALL OUT - 270T484 Blue check disk look Blue check on the disk seat Admission valves.
UNI036482 | Moss Landing | Field_Service_Report_ProjectID_A-1613270_FSP-294850_C-10350768.pdf | 270T484 | Steam Turbine | f1d0ecffd8bc9fb515640e36107e7298 | 8 | 2021-06-14 | Mechanical |  | Blue Check | 1 | Blue Check | ST00075 L A B C D E F G H I J K Combined Control Stop Valve left side Control valve blue check MSV PSH Back Seat #2 Componet fitment on stop valves, disk to stem Piolet valve nut contact check after macining to get proper lift Right side MS |  | Blue Check | AS Found / Left Over Travel of MSV Total lift of MSV Turbine # Jeromiha 5/13 - 5/20 Crew Disc ID NOTE: Stem, bushing, balance chamber, and ring diameters should be recorded both before and after cleaning. Try bar diameters must be recorded. ST00075 L A B C D E F G H I J K Combined Control Stop Valve left side Control valve blue check MSV PSH Back Seat #2 Componet fitment on stop valves, disk to stem Piolet valve nut contact check after macining to get proper lift Right side MSV seat blue and PSH
UNI035721 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1636070_FSP-300586_C-10355243.pdf | 298235 | Gas Turbine | 38a079173d4a5acb0a67ccda8c18ddff | 185 | 2021-06-10 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . The technical data herein is the property of GE and Section HGP Stage 3 Component Blade Location Platform Sub-Location Leading Edge SS Observation Typical Comments HGP_3_Blade_Platform_Leading_Edge_SS001.JPG Section HGP Stage 3 Component Blade Location Platform Sub-Location Trailing Edge SS Observation Typical Comments HGP_3_Blade_Platform_Trailing_Edge_SS001.JPG GE Power Inspection & Life Extension Services The information contained in this document is GE proprietary information and is disclo
UNI035721 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1636070_FSP-300586_C-10355243.pdf | 298235 | Gas Turbine | 2c577c6bf1a245ab0e6fd92c6b52fbad | 17 | 2021-06-10 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . Legend: NA – Parts were not inspected. NV – No visible indications. AF – Observed visible abnormal finding Compressor % Inspected Total Parts Disposition % Inspected Total Parts Disposition % Inspected Total Parts Disposition % Inspected Total Parts Disposition IGV 100 64 AF R4/S4 90 42 AF R9/S9 33 66 AF R14/S14 45 64 AF R0/S0 100 32 AF R5/S5 90 46 AF R10/S10 33 70 AF R15/S15 90 64 AF R1/S1 100 32 AF R6/S6 90 58 AF R11/S11 33 70 AF R16/S16 90 64 AF R2/S2 90 34 AF R7/S7 33 62 AF R12/S12 33 70 A
UNI035721 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1636070_FSP-300586_C-10355243.pdf | 298235 | Gas Turbine | 9cd6fcfa2f57c0ac9dbe2fd641953c83 | 192 | 2021-06-10 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . The technical data herein is the property of GE and Section Peripheral Stage Peripheral Component Peripheral Location Peripheral Sub-Location General Observation S1N Seal Ring Comments Missing Pin Peripheral_Peripher_l_Peripheral_General007-FLAG.JPG Section Peripheral Stage Peripheral Component Peripheral Location Peripheral Sub-Location General Observation S1N Seal Ring Comments Peripheral_Peripher_l_Peripheral_General008.JPG GE Power Inspection & Life Extension Services The information conta
UNI036481 | Moss Landing | Field_Service_Report_ProjectID_A-1375356_FSP-293536_C-10349934.pdf | 297603 | Gas Turbine | 514f28cd1499aca4d0aa3021d9a06444 | 10 | 2021-05-25 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The No.2 Bearing Housing components were reconditioned or replaced in Exhaust Casing such as bearing liners, oil deflectors and oil seals. | FMI F6441G19 | Oil Deflector Alignment ¦ Oil Deflectors ¦ FMI F6441G19 | . A review of post inspection results revealed significant cracking on the Stage 13, 15, 16, and 17 wheel slots. (A replacement Stage 14 wheel, with round bottom slots, had been previously installed on this rotor, and therefore did not require Ultrasonic Testing). The results have been submitted to GE engineering and resolution for these findings is still pending. See report attachment for further details. The removed rotor was packaged and shipped to the Vistra Energy storage facility. The inst
UNI036481 | Moss Landing | Field_Service_Report_ProjectID_A-1375356_FSP-293536_C-10349934.pdf | 297603 | Gas Turbine | 78d5946c3ee325a4c0e820d5497c6f34 | 36 | 2021-05-25 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | . Refer to EM5260 to confirm rotor position. • All views with turbine flow. SEAL INSPECTION Clearances Visual Inspection DIM Left Right Top Bottom Condition Disposition Comments 1S1 0.018 RN 1S2 0.022 N 1S3 0.021 0.022 N 1S4 0.022 0.021 N 1S5 0.022 0.022 N 1S6 0.022 0.023 N 1S7* 0.005 0.004 0.009 R 1S8* 0.004 0.003 0.008 R 1S9* 0.003 0.003 0.007 R 1S10* 0.003 0.004 0.009 R 1WF1 0.023 N DIM Description Measurement Insp. Date T1 Rotor Float * Measure total ring clearance at T1S Inactive Thrust U.H
UNI036481 | Moss Landing | Field_Service_Report_ProjectID_A-1375356_FSP-293536_C-10349934.pdf | 297603 | Gas Turbine | e7f7a5e0d6df8553550cf0328772d9bf | 141 | 2021-05-25 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Typical wear observed at aft end component floating seal rings. |  | Focused Generator Review ¦ Seal Rings | IMG_1771 IMG_1772 IMG_1773 Combustion Section MS 7001FA, 7001FA+, 7001FA+e Flow Sleeve - General Inspection (DLN-2.6) FSR # 10349934 Sketches Enclosed? Photos Enclosed? Yes Chamber # S/N # Inspected Defect Code and Location Seal Condition Seal Diameter Disposition 1 N/A Minor Wear RN-GE 2 N/A Minor Wear RN-GE 3 N/A Minor Wear RN-GE 4 N/A Minor Wear RN-GE 5 N/A Minor Wear RN-GE 6 N/A Minor Wear RN-GE 7 N/A Minor Wear RN-GE 8 N/A Minor Wear RN-GE 9 N/A Minor Wear RN-GE 10 N/A Minor Wear RN-GE 11 N
UNI036481 | Moss Landing | Field_Service_Report_ProjectID_A-1375356_FSP-293536_C-10349934.pdf | 297603 | Gas Turbine | d5d58e8676bbc3700122d8111d1f2f48 | 31 | 2021-05-25 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Grabowski 10349934 As Left All new seal rings installed C C B B A A GE Energy Proprietary Information D309104 Sheet: | EM5260 | Focused Generator Review ¦ Seal Rings ¦ EM5260 | IMG_1721 IMG_1722 IMG_1723 g Bearing Oil Ring Measurements Date Turbine Serial No. Prepared by FSR # Data Type INSPECTIONS & CHECKS CODE Ring Inspected x X Work Carried Out Journals Inspected x N Not Done NA Not Applicable C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Location Oil Rings Journal Clearance Condition Number A-Dia B-Dia C-Dia Dia Average Min. Max. Comment T-1 Fwd. 16.508 16.508 16.508 16.499 0.009 0.009 0.009 T-1 Aft 16.507 16.507 16.507 16.499 0.008
UNI035748 | FORNEY POWER PLANT | Field_Service_Report_ProjectID_A-1655918_FSP-305393_C-10358660.pdf | 298016 | Gas Turbine | a13f4ec1be37a2e8240afea9bbdb0bd2 | 26 | 2021-04-28 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | Mils Mils/In 4 Elliptical 16.041 16.041 16.023 16.040 16.039 16.021 15.999 23 1.4 Shim 0.015 Ball Seat Pinch Fits Bearing Pinch* Bearing Pinch* Leadwire 0.025 Number Mils Number 4 fwd 6.0 4 aft 5.0000 * Pinch equals wire thickness minus shi; (a) Rev 0.0 - 09/03/93 GE Energy Proprietary Information T4 Outer Oil Deflector Alignment (As… Oil Deflector Alignment Date (m,d,y) 4/1/2021 Generator Serial No.; (a) Rev 0.0 - 09/03/93 GE Energy Proprietary Information T4 Outer Oil Deflector Alignment (As l… Bearing To Journal Alignment For Bearings With Ball Seats Date(m/d/y) 3/31/2021 Turbine Serial No.; TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check 4 16.022" 16.023" 21.0 Mils 22.0 Mils 2.0 Mils 0.0 Mils ü TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual ; TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check 4 16.023" 16.023" 24.0 Mils 24.0 Mils 2.0 Mils 0.0 Mils ü TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . 337X259 Prepared by J. Drumgole INSPECTIONS & CHECKS CODE Ball Contact Check Megger Bearing Insulation X Work Carried Out Ball Pinch Check Inspect Bearing Insulation N Not Done Ball Torque Check Inspect Pipe Flange Insulation NA Not Applicable Twist & Tilt Check C See Comments Journal Inspection V Visual Inspection Babbit Inspection MP Mag. Particle Screens & Orifices UT Ultrasonic T/C Calib. PT Penetrant Bearing Bearing Inboard Outboard Journal Vertical Clearance No. Type A-Dia B-Dia C-Dia A-
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1656076_FSP-305414_C-10358674.pdf | 297493 | Gas Turbine | 49040cdd53262e4ae6ace0f218c5aca7 | 18 | 2021-04-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | 16.042 +.002/-.000 6 Babbitt Certificate 3.1.2 Outer Oil Deflectors Part Condition:; Non CBM Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date S/N Prepared by Sketches Enclosed? Photos Enclosed? No Data Type Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Med; 4/4/21 337X155 No As Found FieldCore Team INSPECTION REPORT Gas Turbine Maintenance TE Outer oil deflector Alignment - As found and As left.; (a) Rev 0.0 - 08/01/98 GE Energy Proprietary Information GT21125 TE Oil Deflector Alignment … Oil Deflector Clearances Date(m/d/y) 4/6/2021 Turbine Serial No.; (a) Rev 1.0 - 02/18/2016 GE Power Services Proprietary Information D309301 - TE Oil Deflector Diameter … Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date S/N Prepared by Sketches Enclosed? Photos E |  | Oil Deflector Alignment ¦ Oil Deflectors | V : 16.021 H : 16.042 +.002/-.000 4-12-21 Customer GE - FieldCore JD’s Project Number 15149 P.O. 4900153734 Project Type T-4 – CE (Spare) – 16 X 10-3/4 Bearing Work Scope Full Repair Target Bore Diameter V : 16.021 H : 16.042 +.002/-.000 1 Outgoing Report Customer GE - FieldCore JD’s Project Number 15149 P.O. 4900153734 Project Type T-4 – CE (Spare) – 16 X 10-3/4 Bearing Work Scope Full Repair Target Bore Diameter V : 16.021 H : 16.042 +.002/-.000 2 Outgoing Photos Customer GE - FieldCore JD’s P
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1656076_FSP-305414_C-10358674.pdf | 297493 | Gas Turbine | d01353ce8d661bab78cf27abcc9ace97 | 28 | 2021-04-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | (a) Rev 0.0 - 08/01/98 GE Energy Proprietary Information GT2125 - TE Generator Oil Deflectors … Oil Deflector Clearances Date(m/d/y) 4/7/2021 Turbine Serial No.; (a) Rev 1.0 - 02/18/2016 GE Power Services Proprietary Information D309301 - CE Oil Deflector Diameter … Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 4/10/2021 Turbine S/N 337X155 Prepared by F; INSPECTION REPORT Gas Turbine Maintenance CE Outer Oil Deflector Alignment - As Left.; (a) Rev 0.0 - 08/01/98 GE Energy Proprietary Information GT2125 - CE Oil Deflector Alignment -… |  | Oil Deflector Alignment ¦ Oil Deflectors | . Max Top Bottom Sides Open TE Outer TE Inner CE Outer CE Inner Close TE Outer 0.010 0.009 0.009 0.010 0.023 0.011 10 9 23 21.33333 10.66667 10 TE Inner CE Outer CE Inner Comments: 4/6/21 337X155 No As Left FieldCore Team INSPECTION REPORT Gas Turbine Maintenance TE Outer Oil Deflector - As Left 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor GT2125 Sheet: (a) Rev 0.0 - 08/01/98 GE Energy Proprietary Information GT2125 - TE Generator Oil Deflectors … Oil Deflector Clearances Date(m/d/y) 4/7/2021 Turb
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1656076_FSP-305414_C-10358674.pdf | 297493 | Gas Turbine | b49e7be27eadd656fbd06b6554caf5d1 | 5 | 2021-04-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Forced Outage Generator Bearings, Oil Deflectors |  | Oil Deflector Alignment ¦ Oil Deflectors | Outage Type: Forced Outage Generator Bearings, Oil Deflectors
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1656076_FSP-305414_C-10358674.pdf | 297493 | Gas Turbine | b0bc59f34f4cee2f9a9917abbccd4273 | 2 | 2021-04-28 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 GAS TURBINE (297493 ¦ SY0070937) __________ 2 1 Summary __________ 2 1.1 Timers and Counters __________ 2 1.2 Executive Summary __________ |  | Oil Deflector Alignment ¦ Oil Deflectors | Table Of Contents OUTAGE DETAILS __________ 1 1 Summary __________ 1 1.1 Site Personnel __________ 1 GAS TURBINE (297493 ¦ SY0070937) __________ 2 1 Summary __________ 2 1.1 Timers and Counters __________ 2 1.2 Executive Summary __________ 2 1.3 Work Scope __________ 3 2 Technical __________ 4 2.1 Recommendations __________ 4 3 Turbine __________ 5 3.1 Generator Mechanical __________ 5 3.1.1 T3 and T4 Elliptical Bearing __________ 5 3.1.2 Outer Oil Deflectors __________ 23 GE Power Power Service
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1656076_FSP-305414_C-10358674.pdf | 297493 | Gas Turbine | 5ee28afe1c3ec87ec5af7222eceb57e2 | 7 | 2021-04-28 | Inspection | Field | Focused Generator Review | 1 | Collector Rings |  | EM2101 | Focused Generator Review ¦ Collector Rings ¦ EM2101 | During the outage, visual inspections were conducted on T3 and T4 bearings. Findings revealed both bearings experienced some distress on the lower half bearing lining. Lower half T3 bearing was found to have wiped babbitt or peeling babbitt on one corner of the bearing lining. Additionally, a small dent was found around the oil groove at the top. Upper half of the T3 was in good condition. Lower half T4 bearing had some tiny marks on babbitt but upper half was in acceptable condition. Both T3 an
UNI036549 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_Support_of_Major_Inspection_Gas_Turbine_4_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT4_Gas_Turbine_297493_2012-03-17 | 297493 | Gas Turbine | 960ec457fe2237105f5bbbba4368d87a | 30 | 2012-06-13 | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection | ENCLOSURES Generator Auxiliary Equipment Leads;Load Equipment The flex leads were disconnected from the primary and neutral bus for generator testing and magic inspection. |  | MAGIC Inspection | . The motors should be bumped tested after being reconnected for the proper rotation and current draw, and instrumentation should be calibrated back to Mark V. Turbine Enclosure Instrumentation;Cont Devices - Turb The instrumentation, wiring and tubing were disconnected on the turbine in preparation for the major inspection. The sparkplugs and flame detectors were tested prior to being reinstalled in the turbine. New wheelspace thermocouples were installed during the outage and have been tested
UNI036549 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_Support_of_Major_Inspection_Gas_Turbine_4_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT4_Gas_Turbine_297493_2012-03-17 | 297493 | Gas Turbine | 40779a901d2e83353bbfdc30f3182d05 | 161 | 2012-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | Found oil in the generator, pulled the end shields to inspect the seals and found seals and generator shaft with scratches. |  | Focused Generator Review ¦ End Shield | . Found oil in the generator, pulled the end shields to inspect the seals and found seals and generator shaft with scratches. A start was executed on 05/14/2012 on GT4 at 0715; flame was detected at 0728, unit came up smoothly and with only 362 "COMP DISCHARGE TEMP HIGH SPREAD"coming into alarm to FSNL @ 0735 and placed online at 0738. Checked the compressor discharge thermocouples once the unit was online all three reading the same within 2 degrees of each other, alarm in currently cleared. The
UNI036549 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_Support_of_Major_Inspection_Gas_Turbine_4_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT4_Gas_Turbine_297493_2012-03-17 | 297493 | Gas Turbine | c55bd387584987ae4ca108c8854eebc1 | 158 | 2012-06-13 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | Found oil in the generator, pulled the end shields to inspect the seals and found seals and generator shaft with scratches |  | Focused Generator Review ¦ End Shield | . To avoid this, users may upgrade the ControlST version for the Mark Ve and VIe control platform to a ControlST version V03.06.10C or higher. All the equipment on the Unit Data Highway (UDH) must be upgraded at the same time, and the unit must be shut down to perform this modification. TIL# 1806 GENERATOR VENTILATION TROUBLE SHUTDOWN RECOMMENDATIONS PURPOSE: To inform users to check, and modify if required, the Generator Ventilation Trouble Shutdown sequence, to mitigate the risk of potential o
UNI035721 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_Unit_2B_Hot_Gas_Path_Inspection_for_DOMINION_ENERGY_Fairless_Unit_2B_GT_Gas_Turbine_298235_2012-03-24 | 298235 | Gas Turbine | 05071f1af3bc762e8d7c33f78c24e616 | 1 | 2012-05-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Combustion Inspection (complete) Coupling / Alignment Hot Gas Path Inspection (complete) Minor (rotor in) Compressor Section (partial) End Shield(s) Off Bearings Hydrogen Seals |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | GAS TURBINE INSPECTION REPORT Unit 2B Hot Gas Path Inspection for DOMINION ENERGY Fairless, Unit 2B GT Equipment Serial #: 298235 Job Start Date: March 24, 2012 Report Issued: May 17, 2012 FSR #: 10128810 Report Printed: June 15, 2012 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: DAVID HASSON Field Engineer Approved By: JOSEPH S DAMATO Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 RECOMMENDATIONS 7 PARTS USED & REC
UNI035721 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_Unit_2B_Hot_Gas_Path_Inspection_for_DOMINION_ENERGY_Fairless_Unit_2B_GT_Gas_Turbine_298235_2012-03-24 | 298235 | Gas Turbine | 1be897e86590fa4e11340773d70b9e97 | 37 | 2012-05-17 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | CR - Cracked D - Distortion W - Wear B - Blockage PW - Liner Stop Pin Wear SW - Liner Stop Side Wear CT - Crossfire Tube Flange Wear All piston seal rings were replaced with new ones. |  | Focused Generator Review ¦ Seal Rings | . The cross fire tubes and retainer clips where replaced with new ones. COMBUSTION SECTION Combustion MS7001F Crossfire Tube & Retainer Date 2012-04-17 Turbine S/N Prepared by HASSON DAVID FSR # 10128810 Sketches Enclosed? Photos Enclosed? Defect & Location Disposition Defect & Location Disposition 1 RN-GE 2 RN-GE 2 RN-GE 3 RN-GE 3 RN-GE 4 RN-GE 4 RN-GE 5 RN-GE 5 RN-GE 6 RN-GE 6 RN-GE 7 RN-GE 7 RN-GE 8 RN-GE 8 RN-GE 9 RN-GE 9 RN-GE 10 RN-GE 10 RN-GE 11 RN-GE 11 RN-GE 12 RN-GE 12 RN-GE 13 RN-GE 1
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 96e497f44b124d4174fe89ca866ea8f5 | 1 | 2012-01-26 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Combustion Inspection (complete) Bearings Major Inspection (complete) Hydrogen Seals Hot Gas Path Inspection (complete) Major (rotor out) Oil Deflectors Coupling / Alignment Gas |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | GAS TURBINE INSPECTION REPORT Major Inspection for LAMAR POWER PARTNERS, Unit GT3 Equipment Serial #: 297258 Job Start Date: October 28, 2011 Report Issued: January 26, 2012 Oracle Project Id: 10071621 Report Printed: January 31, 2012 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: MICHAEL RICHARDS Field Engineer Approved By: JAMES HEAD Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 PARTS USED & RECOMMENDED 6 COMPRESS
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 5d320132424bb75df05eb08fb949c10f | 102 | 2012-01-26 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | 42691 Turbine Serial Inspected By Customer FPL Lamar Date Description TE H2 Seals As Found As Left x Measurement of Seal Rings to be accomplished in accordance with GEK 46130A or current revision.; 42692 Turbine Serial Inspected By Customer FPL Lamar Date Description CE H2 Seals As Found As Left x Measurement of Seal Rings to be accomplished in accordance with GEK 46130A or current revision. | EM3404 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings ¦ EM3404 | . 337X711 Prepared by Daniel Ray INSPECTIONS & CHECKS CODE Cleaned Joints X X Work Carried Out Dowels X N Not Done Assembly per NA Not Applicable EM3404 X C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant "A' GAP DIMENSIONS LOCATION PINS IN PINS OUT Top Left 1.627 Top 1.627 Top Right 1.627 Bottom Left 1.627 Bottom 1.627 Bottom Right 1.627 JOINT STEP CHECK LOCATION RIGHT LEFT "B" 1.000 .000 "C" .000 1.000 "D" 1.000 1.000 NOTE: <0.0015 = 0.000 "E" OIL DEFLECTOR LOCATIO
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | af8bb75dddfbd549e478a7056b085aaf | 111 | 2012-01-26 | Mechanical | Field, Hydrogen Seals | Blue Check | 3 | Blue Check, End Shield, Fan Blades | Incoming inspection noted in tolerance TIR, Dowel Measurements, and Joint Blue Check.; Stationary 99% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center:; Incoming inspection noted in tolerance measurements for hook fit run- out, dowel fit, and joint blue check.; Stationary 98% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center:; OPENING FAN BLADE ALIGNMENT 2 4 5 6 Left Right 1 3 End Shield Bearings; |  | Blue Check ¦ End Shield ¦ Fan Blades | . Incoming inspection noted in tolerance TIR, Dowel Measurements, and Joint Blue Check. Seals were lapped in to Casing with 100% contact. Turbine Code: - Prepared by: DG Component: Stationary 99% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center: 12/6/2011 1 4 2 3 5 6 A B C D F G I J H K E Parts & Repair Services H2 Casing As Found Turbine End As Left X Collector End X Insulated X Non-Insulated 1 2 3 4 5 6 1.6220 1.6220 1.6220 1.6220 1.6220 1.6220 0.0010 0.0003 0.0003
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 4dee209a0fb2a315d6c41c5c024aa79b | 93 | 2012-01-26 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Oil deflectors were removed, cleaned and reinstalled.; GENERATOR ALIGNMENT & CLEARANCES Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 12-10-11 Turbine S/N 337X711 Prepared by B Cannon FSR # Sketches Enclosed? No Photos Enclosed? No Data Type Close D; OPENING OIL DEFLECTOR ALIGNMENT 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 10-31-11 Turbine S/N 297257 Prepared by B Cannon FSR # Sketches Enclosed?; OPENING OIL DEFLECTOR ALIGNMENT 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor Alignment - Internal Gib; | EM3404 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . Clearances - Generator Oil Deflector; Oil deflectors were removed, cleaned and reinstalled. Clearance checks were taken and were within limits. GENERATOR ALIGNMENT & CLEARANCES Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 12-10-11 Turbine S/N 337X711 Prepared by B Cannon FSR # Sketches Enclosed? No Photos Enclosed? No Data Type Close Deflector POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Median Min. Max Top Bottom Sides #3 inner 0
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 21869cb34a8e9ab06647f8ba83287059 | 105 | 2012-01-26 | Mechanical | Hydrogen Seals | Blue Check | 2 | Blue Check, Seal Rings | 42773 Turbine Serial Inspected By Customer FPL Lamar Date Description TE H2 Seals As Found As Left x Measurement of Seal Rings to be accomplished in accordance with GEK 46130A or current revision.; 42774 Turbine Serial Inspected By Customer FPL Lamar Date Description CE H2 Seals As Found As Left x Measurement of Seal Rings to be accomplished in accordance with GEK 46130A or current revision.; Incoming inspection noted in tolerance TIR, Dowel Measurements, and Joint Blue Check. |  | Blue Check ¦ Seal Rings | . Incoming inspection noted in tolerance bore dimensions. UT inspection noted excellent Babbitt bond. Seals were lapped in with CE casing to 100% contact. 16.0080 16.0070 16.0074 16.0097 ---- ---- ---- ---- 337X711 GAS: 2 16.0080 EP 16.0070 16.0070 16.0095 ---- ---- ---- ---- AIR: 1 ---- 16.0090 16.0105 16.0100 16.0095 11/14/2011 0.0074 0.0097 16.000 16.000 ---- ---- ---- 180° Babbit Lined Steel Seal Ring 3 4 4 3 2 1 5 2 1 5 Turbine Bearings Floating Rings Dimensional Checks Job No. 42773 Turbin
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 8304df7425535beaea136c7d2d5d2f9c | 89 | 2012-01-26 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Oil deflectors were removed, cleaned and reinstalled. |  | Oil Deflector Alignment ¦ Oil Deflectors | . See PAC case listed for the stage 1 dove tail crack pictures and documentation. TURBINE SECTION MS6001, MS7001, MS9001 Customer: Unit Hours: 56498 Date: Site: Unit Starts: 2460 FSR # Frame Size Unit Trips: 63 Day Shift TA: ML#: PAC Case Night Shift TA: Unit S/N: Measurement: inch Photos Enclosed: 1 Rotor 17 1 Dove tail slot Crack 0.128 Rotor 17 2 Dove tail slot Crack 0.120 Rotor 17 3 Dove tail slot Crack 0.125 Rotor 17 4 Dove tail slot Crack 0.155 Rotor 17 5 Dove tail slot Crack 0.135 Rotor 17
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | e30d1a49cd46f1dc2893271724c9f6a7 | 118 | 2012-01-26 | Inspection | Hydrogen Seals | Focused Generator Review | 2 | End Shield, Hydrogen Seal Assembly | Bearing Cap Pinch Check Shim Thickness Lead Wire Thickness Interference End Shield Hydrogen Seal Casing; |  | Focused Generator Review ¦ End Shield ¦ Hydrogen Seal Assembly | . PT Penetrant Bearing Bearing Forward or Turbine End Aft or Generator End Journal Vertical Clearance No. Type A-Dia B-Dia C-Dia A-Dia B-Dia C-Dia Dia. Mils Mils/In 3 Journal 16.036 16.039 16.020 16.040 16.036 16.021 16.000 20 1.3 4 Journal 16.037 16.041 16.024 16.036 16.041 16.021 16.000 23 1.4 3 Strongback 4 Strongback Shim Ball Seat Pinch Fits Bearing Pinch* Bearing Pinch* Leadwire Number Mils Number 3 4 3 4 * Pinch equals wire thickness minus shim Comments Closing dimensions C C B B A A Bear
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 237be14390fe395d0e16b8b64bf2035b | 108 | 2012-01-26 | Mechanical |  | Blue Check | 1 | Blue Check | Incoming inspection noted in tolerance TIR, Dowel Measurements, and Joint Blue Check.; Stationary 98% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center:; Stationary 90% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center:; Stationary 99% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center: |  | Blue Check | . Incoming inspection noted in tolerance TIR, Dowel Measurements, and Joint Blue Check. Seals were lapped in to Casing with 100% contact. Turbine Code: - Prepared by: DG Component: Stationary 98% Joint Blue Check Hook Opening ("A") TIR Gas TIR Air Dowel Hole Service Center: 11/15/2011 1 4 2 3 5 6 A B C D F G I J H K E Parts & Repair Services H2 Casing As Found Turbine End As Left X Collector End X Insulated X Non-Insulated 1 2 3 4 5 6 1.6250 1.6253 1.6253 1.6250 1.6250 1.6250 0.0005 -0.0009 0.00
UNI036594 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT3_Gas_Turbine_297258_2011-10-28 | 297258 | Gas Turbine | 77517a696c6cb39817a48255174706ed | 7 | 2012-01-26 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | . Section Location Description: Action: 17 Nozzle Arrangement, Stage 2 Removed & Inspected Component Removed And Inspected 18 Nozzle Arrangement, Stage 3 Cleaned and Inspected Good Condition - No Visual Defects 19 Shroud, Stage 1 Turbine Removed & Inspected Component Removed And Inspected 20 Shroud, Stage 2 Turbine Removed & Inspected Component Removed And Inspected 21 Shroud, Stage 3 Turbine Cleaned and Inspected Good Condition - No Visual Defects 22 Cracked Repaired 23 Spacer Damaged Ground 24
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 8da04b2522e8240eaf04fd621591a52b | 152 | 2012-01-17 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 5 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check CE 16.021" 16.023" 21.0 Mils 23.0 Mils 1.6 Mils 0.0 Mils  TE 16.022" 16.022" 22 Mils 22 Mils 1.6 Mils 0.0 Mils  TWIST Brg Reading; No major defect observed ST00078 End Shield Bearings;Turbine End The turbine end bearing was removed and visually inspected.; No major defect observed ST00078 End Shield Assembly;Collector H2 seal and casing The collector end H2 seal and casing was removed and visually inspected. | EM3404 | Wedge Tightness Test; Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test ¦ EM3404 | . 298127 Prepared by J Dixson NOTE: 1. On most generator bearings, the end leakage groove is on the outboard end. 2. On hood bearings, the outboard end is set low to compensate for vacuum deflection. TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check CE 16.021" 16.023" 21.0 Mils 23.0 Mils 1.6 Mils 0.0 Mils  TE 16.022" 16.022" 22 Mils 22 Mils 1.6 Mils 0.0 Mils  TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual Chec
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 258c1c57a4d8b59382ec230cd10293f6 | 300 | 2012-01-17 | Mechanical | Field, Hydrogen Seals | Blue Check; Oil Deflector Alignment | 5 | Blue Check, End Shield, Oil Deflector Alignment, Oil Deflectors, Retaining Rings | Collector End Generator Pictures DHR 2011 outage 8 8 CE final reassembly picture Collector End Generator Pictures DHR 2011 outage 9 9 CE closing FME QC Collector End Generator Pictures DHR 2011 outage 10 10 New CE grounding wire installed C; Journal Size Incoming Inspected By Date Final X 17 17 0 Joint Blue Check Pad2E1 Pad2E2 TC Readings (Ohms) 66.5 66.6 66.1 66.1 Right 85% 75% Pad 1E1 Pad 1E2 Left A 24.500 298127 42711 16.500'' PG 11/08/11 115A1083-12 0.5015 Oil Seal 3202 Man; Casing inspection noted damage to anti-rotation holes in upper retaining rings. |  | Blue Check; Oil Deflector Alignment ¦ Blue Check ¦ End Shield ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Retaining Rings | . Collector End Generator Pictures DHR 2011 outage 8 8 CE final reassembly picture Collector End Generator Pictures DHR 2011 outage 9 9 CE closing FME QC Collector End Generator Pictures DHR 2011 outage 10 10 New CE grounding wire installed Collector End Generator Pictures DHR 2011 outage 11 11 CE inner oil deflector Collector End Generator Pictures DHR 2011 outage 12 12 As found CE bearing Collector End Generator Pictures DHR 2011 outage 13 13 As found CE bearing condition Collector End Generat
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 19e9430674357c70be5376cf04fcdaa4 | 157 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 298127 Prepared by A .181" D N/A B .193" E N/A C .181" F N/A READING TAKEN WITH READINGS TAKEN WITH FEELER GAUGES A .012" SNAP GAUGES B .018" C .018" A .189" D N/A B .189" E N/A C .185" F N/A READING TAKEN WITH READINGS TAKEN WITH FEELER GA |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . Left B. Left T. Right B. Right "A" Gap "A" Gap dimensions Bottom C A B B C D E AIR SIDE HYDROGEN SIDE OIL DEFLECTOR A ST00065 Seal Oil System Date(m,d,y) 11/5/2011 Serial No. 298127 Prepared by J Dixson INSPECTIONS & CHECKS Main Seal Oil Pump NA Seal Oil Press. Gages CODE Emerg. Seal Oil Pump NA at Unit Centerline NA X - Work Carried Out Gas Side Drain Float, High Level Alarm on Hydrogen N - Not Done Trap and Valves NA Detraining Tank NA NA - Not Applicable Vacuum Pump NA Gage Calibration NA C
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 3ccb616a50291b96ba3d007843beb10c | 161 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 298127 Prepared by A .181" D N/A B .189" E N/A C .183" F N/A READING TAKEN WITH READINGS TAKEN WITH FEELER GAUGES A .018" SNAP GAUGES B .037" C .020" A .186" D N/A B .189" E N/A C .186" F N/A READING TAKEN WITH READINGS TAKEN WITH FEELER GA; No major defects were observed.Components were cleaned and returned to service Perform routine inspection of the generator oil deflectors as recommended in GE O&M manuals GENERATOR STATOR Generator Oil Deflectors Oil Deflector Date(m,d,y) 1; No major defects observed A B B A C C Generator Oil Deflectors Outer Oil Deflector Date(m,d,y) 11/2/2011 Turbine Serial No.; A B B A C C Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 11/2/11 Turbine S/N 298127 Prepared by J Dixson FSR # 10101395 Sketches Enclosed? Photos Enclosed? Data Type As found Deflector POSITION | EM3404 | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . Perform routine inspection of the generator H2 system as recommended in GE O&M manuals GENERATOR STATOR Hydrogen Seal Casing TURBINE END Date 11/4/2011 Turbine Serial No. 298127 Prepared by J Dixson INSPECTIONS & CHECKS CODE Cleaned Joints V X Work Carried Out Dowels V N Not Done Assembly per NA Not Applicable EM3404 X C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant "A' GAP DIMENSIONS LOCATION PINS IN PINS OUT Top Left 1.624 - Top 1.624 - Top Right 1.624 - Bottom
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 75ee01d199081d8e91186f68dd2c428f | 167 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | End Shield, Oil Deflector Alignment, Oil Deflectors | INSPECTION REPORT Gas Turbine Maintenance CE inner oil deflector alignment not taken.; 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 11/21/11 Turbine S/N 298127 Prepared by J Dixson FSR # 10101395 Sketches Enclosed? Photos Enclosed? Data ; INSPECTION REPORT Gas Turbine Maintenance 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor End Shield Assembly;Collector end inner/outer oil deflectors The collector end inner and outer oil deflectors were removed and visually inspected.; No major defects were observed.Components were cleaned and returned to service Perform routine inspection of the generator oil deflectors as recommended in GE O&M manuals GENERATOR STATOR Gas turbine and Generator alignments and clearances |  | Oil Deflector Alignment ¦ End Shield ¦ Oil Deflectors | . Max Top Bottom Sides CE Inner CE outer 0.006 0.013 0.009 0.007 0.025 0.003 0.008 0.003 0.025 0.025333 0.012667 0.00625 TE Inner 0.012 0.004 0.005 0.005 0.025 0.012 0.0085 0.004 0.025 0.019333 0.009667 0.0085 TE Outer 0.006 0.007 0.007 0.007 0.021 0.006 0.007 0.006 0.021 0.018667 0.009333 0.0065 Comments: INSPECTION REPORT Gas Turbine Maintenance CE inner oil deflector alignment not taken. 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oi
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | df90cfe55cb2305b4e3e6b815f9bfbc5 | 1 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Combustion Inspection (complete) Coupling / Alignment Enhanced Package 4 Compressor Upgrade Major Inspection (complete) Bearings Case Alignment Checks Hot Gas Path Inspection (c; - Major inspection of gas turbine S/N 298127 - Clean and inspection of collector end and turbine end bearings, oil deflectors, and H2 seals on associated generator The planned extra workscope for this outage included: |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | GAS TURBINE INSPECTION REPORT Major Inspection for Excessive Vibrations for DUKE ENERGY HANGING ROCK LLC HANGING ROCK, Unit 2GT1 Equipment Serial #: 298127 Job Start Date: October 25, 2011 Report Issued: January 17, 2012 Oracle Project Id: 10101395 Report Printed: January 17, 2012 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: JASON S DIXSON Field Engineer Approved By: MARK RUEFER Service Manager PAGE JOB SUMMARY 1 INSPECTION
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 50281c9440048a5cd21a317bded7c72e | 11 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | End Shield, Oil Deflector Alignment, Oil Deflectors | End Shield;Bearings;Collector End Perform routine inspection of generator bearings as recommended in GE O&M manuals.; End Shield;Bearings;Turbine End Perform routine inspection of generator bearings as recommended in GE O&M manuals.; End Shield;Assembly;Collector H2 seal and casing Perform routine inspection of the generator H2 system as recommended in GE O&M manuals RECOMMENDATIONS 11.; End Shield;Assembly;Turbine end H2 seal and casing Perform routine inspection of the generator H2 system as recommended in GE O&M manuals 12.; End Shield;Assembly;Turbine end inner/outer oil deflectors Perform routine inspection of the generator oil deflectors as recommended in GE O&M manuals 13. |  | Oil Deflector Alignment ¦ End Shield ¦ Oil Deflectors | . Inspect for loose bolting, rubs, and cracking. Repair damage as soon as possible, as component failure could cause severe damage to gas turbine. 6. Turbine Enclosure;Assembly - outer;Gas Turbine Compartment Perform routine inspection of the turbine compartment enclosure as recommended in GE O&M manuals. Inspect for loose bolting, gaps, and sealing. Repair damage as soon as possible, as component failure could cause severe damage to gas turbine. 7. Alignment - Coupling;Assembly;Gas turbine to L
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | a6efbb8743e20ea5cc0995aea67c6be1 | 9 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | 22 Casing, Compressor CDC Removed & Inspected Component Removed And Inspected 23 Exhaust Case Removed & Inspected Component Removed And Inspected 24 Turbine Case Removed & Inspected Component Removed And Inspected 44 1st, 2nd, and 3rd Visua |  | Oil Deflector Alignment ¦ Oil Deflectors | . Section Location Description: Action: 27 Forward Casing, Combustion Flow Sleeves Removed & Inspected Component Removed And Inspected 28 Forward Casing, Combustion Inner crossfire tubes and retainers Removed & Inspected Component Removed And Inspected 29 Forward Casing, Combustion Combustion Liner Removed & Inspected Component Removed And Inspected 30 Forward Casing, Combustion Spark plugs Removed & Inspected Component Removed And Inspected 31 Forward Casing, Combustion Flame Detectors Removed
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 78a95f456f4da79a4ea9bdbd252e9c30 | 88 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | . 18.544" 18.555" 18.530" 18.500" .043" .030" .054" Comments: A B B A C C Air/Oil Seals 1S6 position Date(m,d,y) 11/1/2011 Turbine Serial No. 298127 Prepared by J Dixson INSPECTIONS & CHECKS CODE Teeth Inspected V X Work Carried Out Journals Inspected V N Not Done Drain Holes Inspected V NA Not Applicable Inspect for Rubs V C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Location Oil Deflector Journal Clearance Condition Number A-Dia B-Dia C-Dia Dia Average Min. Ma
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 945510780e5916fd73b7207034856ba4 | 83 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | . 7 0.801 0.805 0.810 0.809 N/A Pad No. 8 0.801 0.806 0.808 0.809 N/A Average INSPECTION REPORT Gas Turbine Maintenance Thrust Bearing Pads Refer to EM5260 to confirm rotor position. Bearings MS 3002, 5001, 5002, 6001F, 7001, 7001F Active / Inactive Thrust Bearing Date 11/1/2011 Turbine S/N 297127 Prepared by J Dixson FSR # 10101395 Sketches Enclosed? Photos Enclosed? Data Type Final THRUST CLEARANCE SHIM THICKNESS Opening Closing Opening Closing .017" 0.013 Active 0.543 0.513 Inactive 0.446 0.4
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 3c03dad70219ceda22f84e37f3d45f55 | 6 | 2012-01-17 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | . Customer performed a on-site balance check of the turbine rotor. This was performed by a 3rd party contracted by the customer. No major issues were found during a low speed run (108 rpms). No further information provide for this report. At customer request and PAC approval tip grinding was performed on all compressor rotor blades (R0-R17). This was performed to ensure enough compressor clearance was maintained during baseload operations. JOB SUMMARY Standard gas turbine workscope performed dur
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | c22cb36e0082c415303f6cfda25a957c | 147 | 2012-01-17 | Mechanical | Hydrogen Seals | Wedge Tightness Test | 2 | End Shield, Wedge Tightness Test | End Shield Bearings;Collector End The collector end bearing was removed and visually inspected.; TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check CE 16.024" 16.022" 21.0 Mils 23.0 Mils 1.6 Mils -4.0 Mils  TE 16.021" 16.021" 21 Mils 21 Mils 1.6 Mils 0.0 Mils  TWIST Brg Readin |  | Wedge Tightness Test ¦ End Shield | . (E) 30.000 30.000 30.000 30.000 ** Rabbet Interference - Positive value means there is an interference fit. Comments: Bolt extension data on different form. Coupling s were in good conditions. No major defects found. 1 0° 180° Fig. 1 Fig. 2 270° 90° 8 7 6 5 4 B C E D A 3 2 Rotation ST00100a Alignment MS 7001F, 9001F Load Coupling Date 11/21/11 Turbine S/N Prepared by Zac Bonenberg FSR # 10101395 Sketches Enclosed? Photos Enclosed? Data Type Final Alignment Readings Position Top Left Bottom Rig
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | 81fd6cdc368f19e49ec462b68c5b3ae4 | 259 | 2012-01-17 | Mechanical |  | Blue Check | 1 | Blue Check | DHR fall 2011 outage 9 9 New exhaust Inconel gasket installed General GT pictures DHR fall 2011 outage 10 10 General condition L/H case before rotor installation General GT pictures DHR fall 2011 outage 11 11 New 14,15,16 stage stator blade |  | Blue Check | DHR fall 2011 outage 9 9 New exhaust Inconel gasket installed General GT pictures DHR fall 2011 outage 10 10 General condition L/H case before rotor installation General GT pictures DHR fall 2011 outage 11 11 New 14,15,16 stage stator blades General GT pictures DHR fall 2011 outage 12 12 General condition inner barrel before rotor installation General GT pictures DHR fall 2011 outage 13 13 New IGV installation General GT pictures DHR fall 2011 outage 14 14 Load dam drilling guide General GT pict
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | a22fbbbdb8f1a5e71e5cd18699d49df0 | 323 | 2012-01-17 | Inspection | Field | Focused Generator Review | 1 | Retaining Rings | The based on similar sizes on both the FWD and AFT retaining rings it is clear that the pad rocked back and forth but did not skew where the front of the pad moved more or less in relation to the back. |  | Focused Generator Review ¦ Retaining Rings | . New TC's and checkvalves were installed in bearing, and bearing was prepped for shipping. Customer Part Description Drawing No. Turbine Serial Job No. Journal Size Incoming Inspected By Date Final X 42711 16.500'' PG 11/08/11 Shaft Diameter Average Mandrel Diameter Clearance 16.500 16.5220 3202 Manor Way Dallas, TX 75235 214-902-6600 Duke Hanging Rock T1 Tilt Pad Bearing 115A1083-12 298127 ---- ---- Wire #3 0.0085 0.0079 0.0220 0.0116 Average Wire Reading (Vertical Clearance to Mandrel) A = Ma
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Major_Inspection_for_Excessive_Vibrations_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-10-25 | 298127 | Gas Turbine | b06b7aede793205a2268337dfb0de96c | 103 | 2012-01-17 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . Combustion Chamber Number (Out) Dwg Number / Part Number (Out) Serial Number (Out) Combustion Chamber Number (In) Dwg Number / Part Number (In) Serial Number (In) 1 N/A 1656 1 N/A 1656 2 N/A 1657 2 N/A 1657 3 N/A 1633 3 N/A 1633 4 N/A 1644 4 N/A 1644 5 N/A 1655 5 N/A 1655 6 N/A 1471 6 N/A 1471 7 N/A 1636 7 N/A 1636 8 N/A 1447 8 N/A 1447 9 N/A 1430 9 N/A 1430 10 N/A N/A 10 586E2416G001 151 11 N/A 1649 11 N/A 1649 12 N/A 1486 12 N/A 1486 13 N/A 1490 13 N/A 1490 14 N/A 1459 14 N/A 1459 http://sup
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | dbbf0de670c7aac54a2b5d52946dcdb9 | 32 | 2012-01-04 | Mechanical | Field, Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 6 | End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 60 Thrust Bearing Preventive Maintenance Replaced 61 #2 Bearing Cap Disassembled And Inspected Good Condition - No Visual Defects 62 #2 Journal Bearing #2 Journal Bearing Worn Repaired 63 #2 Bearing Seals Preventive Maintenance Cleaned 64 #; 99 Inner end shields Removed & Inspected Component Removed And Inspected 100 Outer end shields Removed & Inspected Component Removed And Inspected 105 Stator Air Test Generator Air Leakage Test Results Acceptable 102 Generator Gas Cooling S |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | . Section Location Description: Action: 60 Thrust Bearing Preventive Maintenance Replaced 61 #2 Bearing Cap Disassembled And Inspected Good Condition - No Visual Defects 62 #2 Journal Bearing #2 Journal Bearing Worn Repaired 63 #2 Bearing Seals Preventive Maintenance Cleaned 64 #2 bearing lift oil hoses TIL 1582-R2 Preventive Maintenance Replaced 65 TIL 1781 TIL TIL Satisfied 98 #3 & #4 Elliptical bearings #3 & #4 Elliptical bearings Worn Repaired 77 Load Coupling Guard Load Coupling Guard Disas
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 8218f1e0d82032aef5d3c92024f065e4 | 276 | 2012-01-04 | Mechanical | Hydrogen Seals | Generator Pressure Test; Blue Check | 6 | Blue Check, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | Prepared by Jeff LaBarge CLOSING INSPECTIONS & CHECKS CODE Review EM 3404 Measure Resistance x X Work Carried Out Blue Check x Measure Seal Oil Flow x N Not Done Seal Joint Check x Inspect Insulation x NA Not Applicable Measure Rings x Insp; .187" BOTTOM Clearances - Generator Generator oil deflectors;Generator oil deflectors The generator inner and outer oil deflectors were removed from the generator and inspected for damage and wear.; The oil deflectors were cleaned and dimensional checks were performed.; Once the oil deflectors were reinstalled into the generator clearance checks were taken. | EM 3404 | Generator Pressure Test; Blue Check ¦ Blue Check ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ EM 3404 | . C See Comments Measure Step Inspect Springs V Visual Inspection Center Seal Assembly Perform Air Test MP Mag. Particle Replace Stl. Dowels UT Ultrasonic with Glass Dowels PT Penetrant Non-Condutive Thd. Lube OIL PASSAGES CLEANED? TURBINE END (YES OR NO) Yes GAS SIDE Not taken AIR SIDE TOP .024" N/A BOTTOM N/A LEFT .017" N/A RIGHT .016" Horizontal joint Step check - after assembly 0.000 inch Not taken Not taken .190" Top .180" Left .183" Right OIL PASSAGES CLEANED? COLLECTOR END .180" Bottom (Y
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 3f6a2bb1b2ef30ebd1bc9641e92a46c4 | 273 | 2012-01-04 | Mechanical | Hydrogen Seals | Blue Check; Oil Deflector Alignment | 5 | Blue Check, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | Prepared by Jeff LaBarge Opening INSPECTIONS & CHECKS CODE Review EM 3404 Measure Resistance X Work Carried Out Blue Check Measure Seal Oil Flow N Not Done Seal Joint Check Inspect Insulation NA Not Applicable Measure Rings Inspect Seal Rin | EM 3404 | Blue Check; Oil Deflector Alignment ¦ Blue Check ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ EM 3404 | . DIA. CLEARANCE A 16.042 16.000 .042 B 16.037 16.000 .037 C 16.049 16.000 .049 AVERAGE .043 Note: All dimensions must be entered into Oil Deflector table in order to calculate average clearance Comments: Turbine end Hydrogen seal casing. This casing is a new bolted hydrogen seal casing. Top T. Left B. Left T. Right B. Right "A" Gap "A" Gap dimensions Bottom C A B B C D E AIR SIDE HYDROGEN SIDE OIL DEFLECTOR A ST00065 Hydrogen Seal Oil System Date(m/d/y) 11/8/2011 Generator Serial No. Prepared b
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 58e58c4dd59fcaf11f1fdb73b8095e39 | 9 | 2012-01-04 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | JOB SUMMARY IGV Actuator Replaced #1 Journal Cleaned and Inspected #2 Journal Cleaned and Inspected Generator Alignment correction Generator field Removed and Repaired (GE approved) Generator fan blades Removed and Inspected Generator beari; Hydrogen coolers Removed and inspected (Cleaned) Generator oil deflectors Removed and Inspected. |  | Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . Removed and inspected Load coupling. Removed and inspected Load coupling studs, Turbine and generator Removed and inspected (TIL 1702 RIVERHAWK LOAD COUPLING HARDWARE & TOOLING SAFETY CONCERNS ) GE completed Compressor stator blades. Removed and inspected (Blend repaired and Replaced- GE approved) (TIL 1562-R1 HEAVY-DUTY GAS TURBINE SHIM MIGRATION AND LOSS ) GE completed (TIL 1769 F-CLASS AFT STATOR ROCKING INSPECTION ) GE completed Exhaust flex seals. Removed and inspected (Replaced) Inlet gu
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 1f337a6cbca4aff5e5dacb7a68b39696 | 1 | 2012-01-04 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Major Inspection (complete) Coupling / Alignment Exhaust (MLI 0706,A042,A096) Gas Coolers Fuel Gas System Generator Modification Inlet (MLI A40,A41) Balance End Shield(s) Off Be |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | GAS TURBINE INSPECTION REPORT GT 22 MAJOR INSPECTION AND GENERATOR MAJOR INSPECTION for LAMAR POWER PARTNERS, Unit GT4 Equipment Serial #: 297257 Job Start Date: October 22, 2011 Report Issued: January 04, 2012 FSR #: 10071621 Report Printed: January 17, 2012 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: JEFFERY LABARGE Field Engineer Approved By: JAMES HEAD Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 25 RECOMMENDA
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 0bcb5065cc7e21029c3115068f52da9c | 284 | 2012-01-04 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 3 | Fan Blades, Oil Deflector Alignment, Oil Deflectors | C C B B A A Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 10-26-11 Turbine S/N Prepared by Jeff LaBarge FSR # Sketches Enclosed? No Photos Enclosed? No Data Type OPENING Deflector POSITION (Mils; OPENING OIL DEFLECTOR ALIGNMENT 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 12-10-11 Turbine S/N Prepared by Jeff LaBarge FSR # Sketches Enclosed? No; CLOSING OIL DEFLECTORS ALIGNMENT 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor Field Generator field;Generator field The generator field was removed and shipped to a certified GE repair facility for inspection and repair.; Fan Generator fan blades;Generator fan blades The generator fan blades were removed on both sides of the generator field.; (see attached data sheets.) The fan blades were cleaned and inspected for damage and wear. |  | Oil Deflector Alignment ¦ Fan Blades ¦ Oil Deflectors | . Prepared by Jeff LaBarge INSPECTIONS & CHECKS CODE Bearing Bearing Forward or Turbine End Aft or Generator End Journal Vertical Clearance No. Type A-Dia B-Dia C-Dia A-Dia B-Dia C-Dia Dia. Mils Mils/In 3 oil deflector inner 19.022 19.024 19.027 19.021 19.021 19.026 19.000 26 1.4 3 oil deflector outer 18.034 18.021 18.039 18.037 18.022 18.037 18.000 38 2.1 4 oil deflector inner 19.023 19.022 19.030 19.022 19.020 19.030 19.000 30 1.6 4 oil deflector outer 18.024 18.033 18.040 18.026 18.034 18.036
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 21e518176007d58a7bfe23a7451553a9 | 269 | 2012-01-04 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  | EM3404 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . Once received on site, we again recorded dimensional checks of the hydrogen seal casings and again blued the seals into there respective casings. The new bolted seals and new casings were installed into the machine. All seal and casing clearances can be found in this report. All clearances were within specification at the time of this outage. GENERATOR ALIGNMENT & CLEARANCES Hydrogen Seal Casing Date 11/8/2011 Turbine Serial No. Prepared by Jeff LaBarge INSPECTIONS & CHECKS CODE Cleaned Joints
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | b64f05d42080ef5249964121e18f78fb | 310 | 2012-01-04 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Rotor Position Opening and closing Compressor half shell Opening and closing Turbine half shell Opening and closing Bearing clearances Opening and closing Generator bearings Opening and closing Hydrogen seals Opening and closing Oil deflect |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . This inspection interval may be adjusted if repeated inspections show little or no corrosion build-up. The annulus wall thickness does not need to be measured after subsequent cleanings. Following these recommendations will reduce or eliminate the risk of operational issues and forced outages resulting from quaternary annulus corrosion. TIL# 1742 F-CLASS TURBINE WHEEL 1 BALANCE WEIGHT GROOVE INSPECTIONS TIL 1742 was completed by the GE LES team with their inspection. TIL# 1769 F-CLASS AFT STAT
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 4a8597fe75687f0b9d5cc56765d9cf1d | 295 | 2012-01-04 | Mechanical | Hydrogen Seals | Generator Pressure Test | 2 | End Shield, Generator Pressure Test | Particle UT Ultrasonic PT Penetrant Collector End Shield CLOSING CHECK CLOSING CHECKS Location Feeler Location Feeler Location Feeler A .0000" Readings taken 1 .0000" 13 .0000" B .0000" approx.; 12 11 10 9 8 7 6 5 4 3 2 1 24 23 22 21 20 19 18 17 16 15 14 13 A F B G C H D I E R2 J R1 L2 L1 ST00063 End Shield Distortion Check Feeler Gauges Date(m,d,y) 10/25/2011 Serial No.; Particle UT Ultrasonic PT Penetrant Turbine end End Shield OPENING CHECK OPENING CHECKS Location Feeler Location Feeler Location Feeler A .0000" Readings taken 1 .0000" 13 .0000" B .0000" approx.; 12 11 10 9 8 7 6 5 4 3 2 1 24 23 22 21 20 19 18 17 16 15 14 13 A F B G C H D I E R2 J R1 L2 L1 ST00063 End Shield Distortion Check Feeler Gauges Date(m,d,y) 12/10/2011 Serial No.; Particle UT Ultrasonic PT Penetrant Turbine end End Shield CLOSING CHECK CLOSING CHECKS Location Feeler Location Feeler Location Feeler A .0000" Readings taken 1 .0000" 13 .0000" B .0000" approx. |  | Generator Pressure Test ¦ End Shield | . Prepared by Jeff LaBarge INSPECTIONS & CHECKS CODE Vertical Face Runout X Work Carried Out N Not Done NA Not Applicable C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Collector End Shield CLOSING CHECK CLOSING CHECKS Location Feeler Location Feeler Location Feeler A .0000" Readings taken 1 .0000" 13 .0000" B .0000" approx. 12" apart. 2 .0000" 14 .0000" C .0000" 3 .0000" 15 .0000" D .0000" 4 .0000" 16 .0000" E .0000" 5 .0000" 17 .0000" F .0000" Location Feeler 6
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 1b8d32c529c6db97346fc8c0a88c309f | 289 | 2012-01-04 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | End Shield, Fan Blades | ST00078 End Shield Inner end shields;Inner end shields The inner gas shields were removed from the generator stator and inspected for damage and wear.; End Shield Outer end shields;Outer end shields The outer end shields were removed from the generator stator and inspected for damage and wear.; The outer end shields were installed back onto the stator frame and pumped with dow corning to ensure a proper seal.; A clearance check was taken on the horizontal and vertical joints to ensure there was proper seating on the end shields.; (See attached data sheets) GENERATOR STATOR End Shield Distortion Check Feeler Gauges Date(m,d,y) 10/26/2011 Serial No. |  | Focused Generator Review ¦ End Shield ¦ Fan Blades | . Max Top Bottom Sides TE 0.061 0.056 0.054 0.054 0.056 0.061 0.056 0.054 0.061 0.075 0.037 0.058 CE 0.065 0.047 0.065 0.063 0.066 0.070 0.065 0.047 0.070 0.075 0.038 0.066 Exciter 0.080 0.060 0.072 0.065 0.065 0.080 0.069 0.060 0.080 0.083 0.042 0.074 Comments: CLOSING FAN BLADE ALIGNMENT 2 4 5 6 Left Right 1 3 Field #3 and #4 Journal - Shaft;#3 and #4 Journal - Shaft The generator field was removed from the stator and prior to sending to the service shop, dimensional checks were taken on the j
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | a177f2298028a811220e05443e734893 | 264 | 2012-01-04 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly | In addition, the turbine coupling flange in relation to the generator flange is 4 mils open at the top. |  | Focused Generator Review ¦ Hydrogen Seal Assembly | . In addition, the turbine coupling flange in relation to the generator flange is 4 mils open at the top. Generator Feet Shim Packs Left Side - As Found & Final As Found Date Final Date FSR # L1 L2 L3 L4 L5 L6 L7 L8 0.240 0.245 0.240 0.245 0.245 0.245 0.115 0.115 0.115 0.115 0.114 0.118 0.061 0.061 0.061 0.061 0.100 0.061 0.058 0.031 0.028 0.031 0.028 0.031 0.008 0.012 0.012 0.008 0.010 0.008 0.006 0.010 0.010 0.003 0.003 0.003 0.010 0.008 0.003 0.003 0.006 0.008 0.006 0.006 0.003 0.003 Total 0.
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 74a4e0ff00ad4e37d85c447c13f65fc8 | 5 | 2012-01-04 | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | . Inspected, Replaced cooling coils (TIL 1579-R1 TURBINE COMPARTMENT WATER SYSTEMS MAINTENANCE RECOMMENDATIONS ) GE completed Water wash tubing. Inspected (TIL 1579-R1 TURBINE COMPARTMENT WATER SYSTEMS MAINTENANCE RECOMMENDATIONS ) Pending customers operational test. Compressor extraction piping. Removed and inspected. JOB SUMMARY Combustion cans Removed and inspected. (Replaced) (TIL1397-1R2 DLN 2.0 AND DLN 2.6 COMBUSTION FORWARD CASING INSPECTIONS ) Service shop completed (TIL 1724 INSPECTION
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 0087b6519672ccbd998b4b8123a93588 | 239 | 2012-01-04 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | 42732 Turbine Serial Inspected By Customer FPL Lamar Date Description T1 Floating Seals As Found As Left x Measurement of Seal Rings to be accomplished in accordance with GEK 46130A or current revision. |  | Focused Generator Review ¦ Seal Rings | . Prepared by Jeff LaBarge CLOSING DIMENSIONS INSPECTIONS & CHECKS Bearing Seal Forward seal location Aft seal location Journal Vertical Clearance No. Location A-Dia B-Dia C-Dia A-Dia B-Dia C-Dia Dia. Mils Mils/In 1 1S1 18.557 18.555 18.570 18.557 18.555 18.570 18.500 70 3.8 1 1S2 18.555 18.553 18.565 18.555 18.553 18.565 18.500 65 3.5 1 1S3 17.549 17.545 17.552 17.549 17.545 17.552 17.500 52 3.0 1 1S4 18.554 18.552 18.563 18.554 18.552 18.563 18.500 63 3.4 1 1S5 18.554 18.553 18.563 18.554 18.5
UNI036595 | LAMAR POWER PARTNERS | GAS_TURBINE_INSPECTION_REPORT_GT_22_MAJOR_INSPECTION_AND_GENERATOR_MAJOR_INSPECTION_for_LAMAR_POWER_PARTNERS_LP_LAMAR_POWER_PARTNERS_Unit_GT4_Gas_Turbine_297257_2011-10-22 | 297257 | Gas Turbine | 7d9f8d8159dea7b0db8ced673f836693 | 247 | 2012-01-04 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | 42733 Turbine Serial Inspected By Customer FPL Lamar Date Description T2 Floating Seals As Found As Left x Measurement of Seal Rings to be accomplished in accordance with GEK 46130A or current revision. |  | Focused Generator Review ¦ Seal Rings | . See the attached shop repair report the the T2 floating seals. BEARINGS Bearings MS 6001F, 7001F, 9001F Bearing & Seal Clearances, No. 2 Date 11/1/2011 Turbine S/N Prepared by Jeff LaBarge FSR # Sketches Enclosed? No Photos Enclosed? No Data Type AS FOUND SEAL INSPECTION Clearances Visual Inspection DIM Left Right Top Bottom Condition Disposition Comments 2S1 0.024 0.024 Good N 2S2 0.018 0.024 Good N 2S3* 0.007 0.016 0.002 Worn R Service shop repair 2S4* 0.011 0.010 0.008 Worn R Service shop r
UNI036335 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 297198 | Gas Turbine | 925b506a76ab261be197dc163d62a55e | 106 | 2011-11-29 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Right "A" Gap "A" Gap dimensions Bottom C A B B C D E AIR SIDE HYDROGEN SIDE OIL DEFLECTOR A ST00065 End Shield Oil Deflector; | EM3404 | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . END POSITION AIR HYD AIR HYD 1 16.0085 16.0045 16.0080 16.0055 2 16.0085 16.0045 16.0080 16.0055 3 16.0085 16.0060 16.0080 16.0060 4 16.0095 16.0075 16.0090 16.0060 5 16.0095 16.0075 16.0090 16.0060 6 16.0090 16.0060 16.0080 16.0050 AVERAGE 16.0089 16.0060 16.0083 16.0057 SHAFT DIA. 15.9995 15.9995 15.9990 15.9990 CLEARANCE 0.0094 0.0065 0.0093 0.0067 H2 SEAL SPRING MEASUREMENTS TURBINE END COLL. END UPPER LOWER UPPER LOWER LENGTH (±1/16 in.) 27.00 27.00 26.94 26.94 WIRE DIA. 0.12 0.12 0.12 0.
UNI036335 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 297198 | Gas Turbine | db219f041f7abcaf52a1247dac951ae9 | 111 | 2011-11-29 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 4 | End Shield, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | A B B A C C g Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date Generator S/N GT2 VEAZIE Prepared by P.; 10/12/2011 INSPECTION REPORT Gas Turbine Maintenance Inner oil deflectors were not removed.; 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor End Shield Bearings;Turbine End The turbine end generator bearing was found to have displaced babbitt by one of the thermocouples.; TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check 3 as found GEN TE 22.0 Mils 19.0 Mils 3 as left GEN TE 21 Mils 22 Mils TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR L |  | Wedge Tightness Test; Oil Deflector Alignment ¦ End Shield ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . Particle UT Ultrasonic PT Penetrant Location Oil Deflector Journal Clearance Condition Number A-Dia B-Dia C-Dia Dia Average Min. Max. Comment T-3 OUTER 18.016" 18.016" 18.020" 17.989" .028" .026" .031" Comments: A B B A C C g Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date Generator S/N GT2 VEAZIE Prepared by P. Garibotto FSR # 10132307 Sketches Enclosed? No Photos Enclosed? No Data Type Final Assembly Deflector POSITION (Mils) CLEARANCE IDEAL POSITI
UNI036334 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 297197 | Gas Turbine | b08164ec9b6188dbaa6c7abeea868395 | 34 | 2011-11-29 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 12 11 10 9 8 7 6 5 4 3 2 1 A B C ST00064 C End Shield Deflector - Oil;; A clearance check of the generator oil deflectors was performed during re-assembly.; GENERATOR STATOR Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date Generator S/N GT1 VEAZIE Prepared by S LEE FSR # Sketches Enclosed? No Photos Enclosed? No Data Type Final Assembly Deflector POSIT; 10/14/2011 10132304 INSPECTION REPORT Gas Turbine Maintenance Inner oil deflectors were not removed.; 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor End Shield Hydrogen Seal Casing; |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . END POSITION AIR HYD AIR HYD 1 16.0080 16.0055 16.0080 16.0040 2 16.0080 16.0055 16.0080 16.0040 3 16.0080 16.0050 16.0080 16.0055 4 16.0080 16.0055 16.0090 16.0070 5 16.0080 16.0050 16.0090 16.0070 6 16.0080 16.0050 16.0080 16.0055 AVERAGE 16.0080 16.0053 16.0083 16.0055 SHAFT DIA. 15.9990 15.9990 15.9985 15.9985 CLEARANCE 0.0090 0.0062 0.0098 0.0070 H2 SEAL SPRING MEASUREMENTS TURBINE END COLL. END UPPER LOWER UPPER LOWER LENGTH (±1/16 in.) 26.94 26.94 26.94 27.00 WIRE DIA. 0.12 0.12 0.12 0.
UNI036335 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 297198 | Gas Turbine | 13a55322951a42ddc15032f5a346ffed | 85 | 2011-11-29 | Inspection | Hydrogen Seals | Hydrogen Seal Findings Review | 3 | End Shield, Greasing, Hydrogen Seal Assembly | Add IGV rack greasing as a regular maintenance activity.; MISC End Shield Hydrogen Seal Casing;TE and CE The turbine end and collector end hydrogen seals and casings were upgraded from the 180 degree unbolted style seals to the 180 degree bolted style seals and casings. |  | Hydrogen Seal Findings Review ¦ End Shield ¦ Greasing ¦ Hydrogen Seal Assembly | . GT#2 - S/N 297198 NEW S2 STATOR BLADES ASSY DWG 100T4577G001, 101T8127G001 SEGMENT # SERIAL NUMBER 1 11E0024B-14 2 11E024C-2 3 11E024B-2 4 11E024B-4 5 11E024B-5 6 11E024B-3 7 11E024B-1 8 11E024B-15 9 11E024B-11 10 11E024B-12 11 11E024B-10 12 11E024B-8 13 11E024B-7 14 11E024B-9 15 11E024B-6 16 11E024B-13 CASCO BAY ENERGY COMPANY LLC. GT#2 - S/N 297198 NEW S3 STATOR BLADES ASSY DWG 100T4578G001 SEGMENT # SERIAL NUMBER 1 11E020B-13 2 11E020B-2 3 11E020B-3 4 11E020B-5 5 11E020B-1 6 11E020B-4 7 11E
UNI036334 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 297197 | Gas Turbine | b751844f785f39298c410a29692e70db | 19 | 2011-11-29 | Inspection | Hydrogen Seals | Hydrogen Seal Findings Review | 3 | End Shield, Greasing, Hydrogen Seal Assembly | Add IGV rack greasing as aroutine maintenance item.; MISC End Shield Hydrogen Seal Casing;TE and CE The turbine end and collector end hydrogen seals and casings were upgraded from the 180 degree unbolted style seals to the 180 degree bolted style seals and casings. |  | Hydrogen Seal Findings Review ¦ End Shield ¦ Greasing ¦ Hydrogen Seal Assembly | . Investigation revealed that the shims were pinned to the blades in accordance with TIL - 1562-R1, but the edge of the shims had not been dressed flush with the inside diameter of the blade base. The shims in question were dressed and the blades re-installed. Inlet Guide Vane Assembly; The inlet guide vane angles were measured prior to unit disassembly and following unit reassembly to verify they were all within tollerance of each other and to verify that none had jumped a pinion tooth during d
UNI036334 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 297197 | Gas Turbine | a5fe6ef55326725fb86959ea605c5ba2 | 30 | 2011-11-29 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  | EM3404 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . The collector end casing installed is DWG 203D4645G0001 with a gas side bolted seal DWG 585D2468G022 and air side bolted seal DWG 585D2468G0001. The turbine end casing installed is 203D4657G0001 with a gas side bolted seal DWG 585D2468G022 and air side bolted seal DWG 585D2468G0001. New TE and CE springs were supplied DWG 01271J40P0001. New collector end insulated bolts and washers were also supplied DWG 02149J46G0003. All items were dimensionally checked and the seals lapped to the casings pr
UNI036335 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 297198 | Gas Turbine | 895f52554535da1f852d11b7c022049e | 115 | 2011-11-29 | Inspection | Hydrogen Seals | Focused Generator Review | 2 | End Shield, Hydrogen Seal Assembly | BEARING DWG 11E6690G0001 REV E, VC 51670, IT04480-2 V Dimensional Checks ½" ½" H1 H2 End Shield Hydrogen Seal Casing; |  | Focused Generator Review ¦ End Shield ¦ Hydrogen Seal Assembly | . DISPOSITION CODES N - No repair or replacement necessary. RG - Repaired by GE RC - Repaired by Customer RO - Repaired by Other RN - Replaced with new component. RR - Replacement Recommended V Dimensional Checks ½" ½" H1 H2 g Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Journal Bearing – General Condition Date Turbine S/N Prepared by FSR # Sketches Enclosed? Photos Enclosed? Data Type YES NO INSPECTION REPORT Gas Turbine Maintenance 2 FWD. FWD. FWD. FWD. FWD. (Upstream) AFT FWD.
UNI036335 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 297198 | Gas Turbine | d09be6a7c6cb1849f6a9aa6d3efefb3e | 6 | 2011-11-29 | Inspection | Hydrogen Seals | Hydrogen Seal Findings Review | 2 | Greasing, Hydrogen Seal Assembly | Add IGV rack greasing as a regular maintenance activity. |  | Hydrogen Seal Findings Review ¦ Greasing ¦ Hydrogen Seal Assembly | . Pickup Bracket extension Modified 9 Hydrogen Seal Casing TE and CE FMI FMI Satisfied 18 Dimensional Checks Ok - Measurements Are Within Tolerance 19 Turbine End Blistered Weld Repaired 21 Hydrogen Seal Casing Visual Inspection Good Condition - No Visual Defects 13 Visual Inspection Good Condition - No Visual Defects INSPECTION SUMMARY Page No 4 Inspection No. Section Location Description: Action: 14 Pump, Emergency Visual Inspection Good Condition - No Visual Defects 15 Pump, Main Seal Oil Vis
UNI036334 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 297197 | Gas Turbine | 586921c7389aed10e8943e55dea425ef | 1 | 2011-11-29 | Inspection | Hydrogen Seals | Hydrogen Seal Findings Review | 2 | Greasing, Hydrogen Seal Assembly | Add IGV rack greasing as aroutine maintenance item |  | Hydrogen Seal Findings Review ¦ Greasing ¦ Hydrogen Seal Assembly | GAS TURBINE INSPECTION REPORT UNIT 1 COMPRESSOR UPGRADE for MAINE INDEPENDENCE, Unit GT-1 Equipment Serial #: 297197 Job Start Date: October 01, 2011 Report Issued: November 29, 2011 Oracle Project Id: 27492 Report Printed: December 14, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: PETER GARIBOTTO Field Engineer Approved By: MICHAEL KERKMANN Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 RECOMMENDATIONS 6 PARTS
UNI036335 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_2_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-2_Gas_Turbine_297198_2011-10-01 | 297198 | Gas Turbine | 283b0806ca0f19678ba16029f1d46811 | 1 | 2011-11-29 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | GAS TURBINE INSPECTION REPORT UNIT 2 COMPRESSOR UPGRADE for MAINE INDEPENDENCE, Unit GT-2 Equipment Serial #: 297198 Job Start Date: October 01, 2011 Report Issued: November 29, 2011 Oracle Project Id: 27492 Report Printed: December 14, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: PETER GARIBOTTO Field Engineer Approved By: MICHAEL KERKMANN Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 RECOMMENDATIONS 6 PARTS
UNI036334 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 297197 | Gas Turbine | cba1e31c32485f4bc1017d69eccdb462 | 46 | 2011-11-29 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | . max. min. max. Left Right Left Right R0 0.059 0.099 0.059 0.099 0.004 0.094 0.103 S0 0.042 0.082 0.042 0.082 -0.006 0.036 0.052 R1 0.050 0.090 0.050 0.090 0.060 0.069 S1 0.043 0.083 0.043 0.083 0.062 0.076 R2 0.057 0.097 0.057 0.097 0.064 0.076 S2 0.050 0.090 0.050 0.090 0.075 0.085 R3 0.062 0.102 0.062 0.102 0.062 0.076 S3 0.055 0.095 0.055 0.095 0.086 0.088 R4 0.055 0.095 0.055 0.095 0.068 0.075 S4 0.048 0.088 0.048 0.088 0.068 0.078 R5 0.070 0.090 0.070 0.090 0.078 0.078 S5 0.052 0.092 0.05
UNI036334 | Casco Bay Power Station | GAS_TURBINE_INSPECTION_REPORT_UNIT_1_COMPRESSOR_UPGRADE_for_CASCO_BAY_ENERGY_COMPANY_LLC_MAINE_INDEPENDENCE_Unit_GT-1_Gas_Turbine_297197_2011-10-01 | 297197 | Gas Turbine | d8a6660884a52a35f387323b525b5a76 | 8 | 2011-11-29 | Inspection |  | Focused Generator Review | 1 | Greasing | Add IGV rack greasing as aroutine maintenance item. |  | Focused Generator Review ¦ Greasing | . Inlet Guide Vane;Gear - Rack; Add IGV rack greasing as aroutine maintenance item. RECOMMENDATIONS (No Parts Used or Recommended for this report) PARTS USED & RECOMMENDED PU=Part Used During the Inspection RI=Part Recommended for Immediate Restock RO=Part Recommended for the Next Inspection Page No 7 Inlet Guide Vane Assembly;Backlash The inlet guide vanes were checked for proper backlash in accordance with TIL- 517CR-1 . Many blades were found with backlash in excess of .030" with a maximum me
UNI037113 | Washington Energy Facility | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 297623 | Gas Turbine | 6405620ca88dc28c2361029a589e8b9d | 121 | 2011-11-14 | Mechanical | Hydrogen Seals | Generator Pressure Test; Blue Check | 5 | Blue Check, Generator Pressure Test, Oil Deflector Alignment, Oil Deflectors, Seal Rings | 297623 Units recorded in INSPECTIONS & CHECKS CODE Review EM 3404 Measure Resistance X X Work Carried Out Blue Check X Measure Seal Oil Flow N Not Done Seal Joint Check X Inspect Insulation X NA Not Applicable Measure Rings X Inspect Seal R; (a) Rev 0.0 - 10/01/04 GE Energy Proprietary Information Page No 119 g Oil Deflector Alignment Date (m,d,y) October 12, 2011 Turbine Serial No. | EM 3404 | Generator Pressure Test; Blue Check ¦ Blue Check ¦ Generator Pressure Test ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ EM 3404 | . 337X768 Prepared by Turbine Serial No. 297623 Units recorded in INSPECTIONS & CHECKS CODE Review EM 3404 Measure Resistance X X Work Carried Out Blue Check X Measure Seal Oil Flow N Not Done Seal Joint Check X Inspect Insulation X NA Not Applicable Measure Rings X Inspect Seal Ring Surf. X C See Comments Measure Step X Inspect Springs X V Visual Inspection Center Seal Assembly X Perform Air Test X MP Mag. Particle Replace Stl. Dowels UT Ultrasonic with Glass Dowels PT Penetrant Non-Condutive T
UNI037113 | Washington Energy Facility | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 297623 | Gas Turbine | dd81c071239bf7bed45332a40c5d954f | 1 | 2011-11-14 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Combustion Inspection (complete) Coupling / Alignment Hot Gas Path Inspection (complete) Minor (rotor in) Compressor Section (partial) End Shield(s) Off Bearings Hydrogen Seals | FMI F6229G21 | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ FMI F6229G21 | GAS TURBINE INSPECTION REPORT HGPI and package 4 enhancement for DUKE ENERGY CORPORATION WASHINGTON ENERGY FACILITY, Unit 1 Equipment Serial #: 297623 Job Start Date: October 08, 2011 Report Issued: November 14, 2011 Oracle Project Id: 10089331 Report Printed: November 14, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: DAVID HASSON Field Engineer Approved By: MARK RUEFER Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMM
UNI037113 | Washington Energy Facility | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 297623 | Gas Turbine | 49a886fe072431c7ef527a071e147271 | 117 | 2011-11-14 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  | EM3404 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ EM3404 | . Particle UT Ultrasonic PT Penetrant 'A' GAP DIMENSIONS (inches) LOCATION PINS IN PINS OUT Top Left 1.625 Top 1.625 Top Right 1.625 Bottom Left 1.625 Bottom 1.625 Bottom Right 1.625 JOINT STEP CHECK (inches) LOCATION RIGHT LEFT "B" .000 .000 "C" .000 .000 "D" .000 .000 NOTE: <0.0015 in. = 0.000 in. "E" OIL DEFLECTOR LOCATION DIAMETER JOUR. DIA. CLEARANCE A B C AVERAGE Note: All dimensions must be entered into Oil Deflector table in order to calculate average clearance Comments: Hasson English -
UNI037113 | Washington Energy Facility | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 297623 | Gas Turbine | 02050ff61f331a85f058cffb57edbbdd | 112 | 2011-11-14 | Mechanical | Hydrogen Seals | Wedge Tightness Test | 3 | End Shield, Hydrogen Seal Assembly, Wedge Tightness Test | TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check 4 24.0 Mils 25.0 Mils 3 23 Mils 23 Mils TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual Check 4 19.0 Mils ; EXHAUST SYSTEM 297623 DUKE ENERGY CORPORATION Page No 113 End Shield Hydrogen Seal Casing; | EM3404 | Wedge Tightness Test ¦ End Shield ¦ Hydrogen Seal Assembly ¦ EM3404 | . 297623 Prepared by Hasson NOTE: 1. On most generator bearings, the end leakage groove is on the outboard end. 2. On hood bearings, the outboard end is set low to compensate for vacuum deflection. TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check 4 24.0 Mils 25.0 Mils 3 23 Mils 23 Mils TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual Check 4 19.0 Mils 16.0 Mils 15.0 Mils 15.0 Mils -1.5 Mils 3 16.0 Mils 17.0 Mils
UNI037113 | Washington Energy Facility | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 297623 | Gas Turbine | a2593ee3bf878967b457787cefc818b1 | 106 | 2011-11-14 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test |  |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . Turb End Diameter 16.4990 16.4990 16.4990 16.4990 16.4990 16.4990 Diameter 16.4980 16.4980 16.4990 16.4990 16.4990 Gen 16.4980 End OUT OF ROUNDNESS Diameters Out of JOURNAL SIZES 0º 90º Round 0º 90º All 16.499 16.498 0.001 Maximum 16.4990 16.4990 16.4990 16.499 16.498 0.001 Minimum 16.4990 16.4980 16.4980 16.499 16.499 0.000 Difference 0.0000 0.0010 -0.0010 16.499 16.499 0.000 Average 16.4990 16.4985 16.4988 16.499 16.499 0.000 16.499 16.498 0.001 Comments: INSPECTION REPORT Gas Turbine Mainte
UNI037113 | Washington Energy Facility | GAS_TURBINE_INSPECTION_REPORT_HGPI_and_package_4_enhancement_for_DUKE_ENERGY_CORPORATION_WASHINGTON_ENERGY_FACILITY_Unit_1_Gas_Turbine_297623_2011-10-08 | 297623 | Gas Turbine | 95f0a6b4969a51d5732a17eeede6d992 | 5 | 2011-11-14 | Inspection | Hydrogen Seals | Focused Generator Review | 2 | End Shield, Hydrogen Seal Assembly | 7 Combustion Liner Assembly Removed & Inspected Replaced 8 Liner Cap, Combustion Assembly Removed & Inspected Replaced 9 Flow Sleeve, Combustion Assembly Removed & Inspected Component Removed And Inspected 10 Transition Piece, Combustion As |  | Focused Generator Review ¦ End Shield ¦ Hydrogen Seal Assembly | . Attached to this report you will find the controls report for this unit. DEMOB from site on November. 8, 2011 JOB SUMMARY 297623 DUKE ENERGY CORPORATION Page No 3 Inspection No. Section Component Location Description: Action: 1 Shroud, Stage 3 Turbine Assembly Damaged Replaced 2 Shroud, Stage 1 Turbine Assembly Damaged Replaced 3 Shroud, Stage 2 Turbine Assembly Damaged Replaced 4 Nozzle Arrangement, Stage 1 Assembly Damaged Replaced 14 Nozzle Arrangement, Stage 2 Assembly Removed & Inspected
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_High_Bearing_Vibration_and_H2_Seal_Inspection_for_DUKE_ENERGY_HANGING_ROCK_LLC_HANGING_ROCK_Unit_2GT1_Gas_Turbine_298127_2011-06-18 | 298127 | Gas Turbine | 538573fc9b262c24ca6c292d05ea84ce | 1 | 2011-08-23 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | GAS TURBINE INSPECTION REPORT High Bearing Vibration and H2 Seal Inspection for HANGING ROCK, Unit 2GT1 Equipment Serial #: 298127 Job Start Date: June 18, 2011 Report Issued: August 23, 2011 Oracle Project Id: 100101295 Report Printed: August 23, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: PETER MONZON Field Engineer Approved By: MARK RUEFER Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 4 PARTS USED & RECOMME
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | 2bfe0f79ed45696622aa9216322d3866 | 1 | 2011-06-03 | Inspection | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | Steam Turbine Generator Mechanical Support Systems Other Systems Balance Coupling / Alignment Valves (Steam) Hydrogen Seals Centerline - Sectional Oil Deflectors Bearings Coupling /Alignment JOB SUMMARY Site Personnel:; Valve inspections, turning gear inspection, and generator MAGIC inspections were also done during this outage. |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | STEAM TURBINE INSPECTION REPORT D11 L-0 bucket replacement and valve outage Jan. 2011 for CASCO BAY ENERGY COMPANY LLC, Unit ST Equipment Serial #: 270T432 Job Start Date: January 15, 2011 Report Issued: June 03, 2011 Oracle Project Id: 10079907 Report Printed: July 12, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: MICHAEL THERIAULT Field Engineer Approved By: MICHAEL KERKMANN Service Manager PAGE JOB SUMMARY 1 INSPECTI
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | 121be7e19a60820e0a9a8078d0a528df | 13 | 2011-06-03 | Inspection | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | A 5 mil shim was added which was determined to be too much.; Two 1 mil shims were removed from the same pad and the contact was satisfactory.; Bearing, Generator Journal Assembly;T5 The T5 upper half bearing was removed during the partial disassembly of the generator for MAGIC inspection.; During the inspection, the test lead for the online insulation test was removed from the end shield tunnel and found to be damaged with some of the insulation missing.; The oil deflectors at T4 turbine end and T4 generator end both had rubs on the lower halves and excessive clearance. |  | Oil Deflector Alignment ¦ End Shield ¦ MAGIC Inspection ¦ Oil Deflectors | . TIL 1719 “Modification to Double Tilt Pad Bearing Geometry” was discussed with the customer to forward to the bearing vendor. The bearing was returned to site with documentation attached to this report and returned to service. The customer’s mandrel was also returned with the bearing and stored with the turbine specialty tools on the turbine deck. BEARINGS T3 Bearing T3 stray shaft currents Bearing, Turbine Journal Babbitt;T 4 The T4 bearing showed evidence of stray shaft currents. The bearing
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | 32e7ace37d354eef0f5417013b2ddf47 | 26 | 2011-06-03 | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check T6 Gen 16.000" 16.000" 25.0 Mils 25.0 Mils 1.6 Mils 0.0 Mils T5 Gen 16.000" 16.000" 25 Mils 24 Mils 1.6 Mils 1.0 Mils T4 LP 17. |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . Crescentville Rd. Cincinnati, OH 45246 (800-848-7994) ISO 9001:2008 Registered Licensee of: Siemens Energy, Inc. OIL DEFLECTOR TOOTH INSPECTION PME JOB #: 50-45271 CUSTOMER: CASCO BAY ENERGY COMPANY LLC CUSTOMER PO#: 62037-0000002652 LOCATION: MAINE INDEPENDENCE STATION C A B Split Line Split Line B A C TOOTH DIMENSIONS Tooth # A-A (Horizontal) B-B (Horizontal) C-C (Vertical) Profile Thickness 1 19.031” 19.030” 19.0315” .015” 2 19.032” 19.0325” 19.0325” .015” 3 19.030” 19.0305” 19.031” .015” 4
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | 3e8e68048a51cdeb920a4182e3b9b44e | 45 | 2011-06-03 | Inspection | Hydrogen Seals | MAGIC Inspection | 3 | End Shield, Hydrogen Seal Assembly, MAGIC Inspection | The test leads for the online bearing insulation test were removed from the collector end shield tunnel and found to be damaged with some of the insulation missing.; GENERATOR AUXILIARIES Damaged Test Leads T6 Bearing Test Lead GENERATOR AUXILIARIES H2 Seal Oil System Ring;Hydrogen Seal - Air,Hydrogen Seal - Gas The generator hydrogen seals were inspected during the MAGIC inspection. | GEK 46091 | MAGIC Inspection ¦ End Shield ¦ Hydrogen Seal Assembly ¦ GEK 46091 | . The bearing retainer was also bent and damaged. The bearing clamping rails were slightly bowed. The turning gear assembly was shipped to DURST (turning gear OEM) by the customer for repairs and the replacement of broken parts. After returning to site, the turning gear was reinstalled in the original dowelled position and the backlash was measured at .115”. This is the same backlash as documented previously and was not changed at this time as there were no unusual signs of wear or unusual noise
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | b03dbf971bbcfc613d9bb458ac687d09 | 30 | 2011-06-03 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | T4 repaired, and remeasured- OK Repair teeth from T3 A B B A C C Oil Deflector Alignment Final Date (m,d,y) 03/18/2011 Turbine Serial No. |  | Oil Deflector Alignment ¦ Oil Deflectors | . Prepared by Ivan Dominguez Journal Number T3 NOTE: Mark on sketch to show grooving, discoloration, carbon inclusions, or irregularities in the journal surface. Gen End Diameter 15.9960 15.9970 15.9970 15.9960 15.9970 15.9960 Diameter 15.9960 15.9970 15.9970 15.9960 15.9960 Turb 15.9960 End OUT OF ROUNDNESS Diameters Out of JOURNAL SIZES 0º 90º Round 0º 90º All 15.996 15.996 0.000 Maximum 15.9970 15.9970 15.9970 15.997 15.997 0.000 Minimum 15.9960 15.9960 15.9960 15.997 15.997 0.000 Difference
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | c9fd1ae168e71f4854a7dc705d645600 | 18 | 2011-06-03 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  | GEK 92569 | Focused Generator Review ¦ Wedges ¦ GEK 92569 | . direct, consequential or special that may be alleged to have been incurred as result of applying this information regardless of whether it is claimed that GE is strictly liable, in breach of contract, in breach of warranty, negligent, or is in other MODIFICATION TO DOUBLE TILT PAD BEARING GEOMETRY APPLICATION This TIL is applicable to Steam Turbines with six-pad Double Tilt Pad (DTP) bearings exhibiting Babbitt leading edge damage. PURPOSE To address potential damage to Double Tilt Pad (DTP) b
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | c7e48b0c032d0c292b6d54502f341d1e | 10 | 2011-06-03 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | . Valve, Combined Stop/CV;Seat;#1 and #2 Recommend spare seats be ordered with extra stock at the body fit in the future. Part#190D4587P0001 2. Bearing, Generator Journal;Assembly;T5 Recommend a spare T5 bearing be available should issues arise from the likely wear effects of the stray shaft currents observed at other locations of this unit. 3. Bearing, Generator Journal;Babbitt;T6 The T6 bearing should be replaced or repaired at next outage. Note this is an insulated bearing and an insulation k
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | 76479afbe9fe312d02387389ce678a40 | 5 | 2011-06-03 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | . The outage began at 0700 on January 16th working two 12 hour shifts and was put on turning gear April 28th at 2200 hrs. JOB SUMMARY Inspection No. Section Location Description: Action: 1 Bearing, Turbine Journal Babbitt T 3 Frosted Rebabbitt 24 Bearing, Turbine Journal Babbitt T 4 Frosted Rebabbitt 25 Bearing, Turbine Journal T3 Contact Check No Problems - 100% Contact 26 Bearing, Turbine Journal T4 Contact Poor Corrected 27 Bearing, Generator Journal T5 Preventive Maintenance Used As Is - Mon
UNI036336 | Casco Bay Power Station | STEAM_TURBINE_INSPECTION_REPORT_D11_L-0_bucket_replacement_and_valve_outage_Jan._2011_for_DYNEGY_INC_CASCO_BAY_ENERGY_COMPANY_LLC_Unit_ST_Steam_Turbine_270T432_2011-01-15 | 270T432 | Steam Turbine | 7de2bae82a7320765fa1a03648cf3dd8 | 34 | 2011-06-03 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Crosshead OD 7.242 7.242 Clearance 0.016 0.015 B Bushing ID 2.997 2.998 TRY BAR Stem OD 2.996 2.996 2.996 Clearance 0.001 0.002 Bushing ID 2.998 2.998 D Stem OD 2.987 2.987 Clearance 0.011 0.011 H Bushing ID 4.503 4.506 TRY BAR Stem OD 4.50; Allowable from FE Manual 4 Mils/Ft Reheat Stop Stem G I K Max Allowable Bowed? Left 0 0 0 0 20 1/2 OK Right 0 0 0 0 20 1/2 OK Stem Lgth 61 In.; Allowable from FE Manual 4 Mils/Ft NOTE: |  | Focused Generator Review ¦ Seal Rings | . The strainer was shipped to Fitchburg Welding for refurbishment and mesh replacement. Valve, Combined Reheat Strainer;L/S The L/S CRV strainer had a loose rivet which was replaced on site. Valve, Combined Reheat Linkage; The CRV linkage was disassembled, cleaned, and routine inspections were performed. No problem areas were found and all parts were returned to service. VALVES, COMBINED REHEAT The linkage was greased after reassembly. Valve, Combined Reheat Stop Pressure Seal Head; The CRV stop
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | 6e0453b0f69969c5d7c3eef33e897edf | 5 | 2011-05-11 | Inspection | Field, Hydrogen Seals, Stator | Generator Pressure Test; Oil Deflector Alignment | 8 | Belly Bands, Belly band inspection, End Shield, Fan Blades, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | JOB SUMMARY 298158 DUKE ENERGY CORPORATION Page No 3 DRAFT REPORT Generator- Generator CE was disassembled for Magic inspection which involved removing oil deflectors, Bearing, H2 seals & casing, Inner oil deflector, Outer UH End shield, UH; Magic inspection was performed from CE of generator.; CE& TE were then reassembled, CE fan blades installed and locktabs locked over, inner end shield installed, outer end shield, CE & TE H2 seals and casing & bearing.; A belly band inspection and tightening was also performed in parallel, removing the middle and two end H2 coolers. |  | Generator Pressure Test; Oil Deflector Alignment ¦ Belly Bands ¦ Belly band inspection ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ MAGIC Inspection | . IGV backlash, x gaps, and busing clearances were taken and all were acceptable. The IGV's and inlet bellmouth were cleaned to help ensure efficient operation. Combustion parts were prepped for re-assembly, Fuel nozzles were switched to FWD cans and DLN caps were installed. A Crossfire bellows modification was performed on the AFT cans replacing the need for packing ensuring a longer and more useful lifespan of the outer crossfire tubes. #1 and #2 bearings were opened, clearances taken and a vi
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | ca1c0639be9f60164b5b81dd74cffe63 | 6 | 2011-05-11 | Mechanical | Field, Hydrogen Seals, Stator | Generator Pressure Test; Blue Check | 8 | Belly Bands, Blue Check, End Shield, Fan Blades, Generator Pressure Test, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 1 End Shield Bearing CE, TE Bearing Twist tilt pinch Removed & Inspected Component Removed And Inspected 2 End Shield Oil Deflector CE Oil deflector- opening Clearance Check Clearance Check Was Satisfactory 3 End Shield Oil Deflector CE oil |  | Generator Pressure Test; Blue Check ¦ Belly Bands ¦ Blue Check ¦ End Shield ¦ Fan Blades ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly | . A customer performed air test was performed and it passed. JOB SUMMARY 298158 DUKE ENERGY CORPORATION Page No 4 DRAFT REPORT Inspection No. Section Component Location Description: Action: 1 End Shield Bearing CE, TE Bearing Twist tilt pinch Removed & Inspected Component Removed And Inspected 2 End Shield Oil Deflector CE Oil deflector- opening Clearance Check Clearance Check Was Satisfactory 3 End Shield Oil Deflector CE oil deflectors Closing Clearance Check Clearance Check Was Satisfactory 4
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | 101f64a4dafce9d01af016c2bbe01cd0 | 24 | 2011-05-11 | Mechanical | Hydrogen Seals, Stator | Wedge Tightness Test; Blue Check | 7 | Belly Bands, Blue Check, End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | GENERATOR STATOR 298158 DUKE ENERGY CORPORATION Page No 25 DRAFT REPORT End Shield Hydrogen Seal Casing;Hydrogen Seal Blue check CE & TE New TE seals were blue checked to TE H2 seal casing.; New CE gas H2 seal and existing air CE H2 seal were blue checked to existing H2 seal casing.; GENERATOR STATOR 298158 DUKE ENERGY CORPORATION Page No 26 DRAFT REPORT H2 seal blue check.; All seals lapped to have 100% radial contact H2 seal blue check.; All seals lapped to have 100% radial contact GENERATOR STATOR 298158 DUKE ENERGY CORPORATION Page No 27 DRAFT REPORT H2 seal blue check. |  | Wedge Tightness Test; Blue Check ¦ Belly Bands ¦ Blue Check ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflector Alignment ¦ Oil Deflectors | . Seals were severely burnt, had massive amounts of missing babbitt, coking, and disfiguration. See photos. Seals were replaced with new. A collection of babbitt powder was found at the bottom of the casing. GENERATOR STATOR 298158 DUKE ENERGY CORPORATION Page No 22 DRAFT REPORT TE H2 seals, both in severe condition, both replaced. TE H2 seals, both in severe condition, both replaced. GENERATOR STATOR 298158 DUKE ENERGY CORPORATION Page No 23 DRAFT REPORT TE H2 seals, both in severe condition, b
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | 0f5a84dce47bcd616efb5f0c3b6a26c2 | 13 | 2011-05-11 | Mechanical | Hydrogen Seals, Stator | Generator Pressure Test; Oil Deflector Alignment | 7 | Belly Bands, End Shield, Generator Pressure Test, Hydrogen Seal Assembly, Keybars, Oil Deflector Alignment, Oil Deflectors | End Shield Oil Deflector;CE Oil deflector- opening The CE outer oil deflector, H2 seal case, Mid oil deflector and Inner oil deflector clearances were taken and components were removed.; End Shield Oil Deflector;CE oil deflectors Closing The oil deflectors on the CE were reinstalled and set to an even setting within the specified tolerances.; End Shield Oil Deflector;TE closing oil deflectors The oil deflectors on the TE were reinstalled and set to an even setting within the specified tolerances.; Stator Assembly - Inner;Belly Band Tightening Belly bands were inspected and tightened, and tightened per P12A-AL-5010 and site specific direction.; GENERATOR STATOR 298158 DUKE ENERGY CORPORATION Page No 11 DRAFT REPORT Bellybands existing condition End Shield Hydrogen Seal Casing;Meggar H2 Seal Casing The CE Hydrogen seal casing was re-installed and meggared to test the insulation of |  | Generator Pressure Test; Oil Deflector Alignment ¦ Belly Bands ¦ End Shield ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ Keybars ¦ Oil Deflector Alignment | . End Shield Oil Deflector;CE Oil deflector- opening The CE outer oil deflector, H2 seal case, Mid oil deflector and Inner oil deflector clearances were taken and components were removed. A few of of the oil deflector clearances were slightly tight, the H2 seal casing was also slightly off center. End Shield Oil Deflector;CE oil deflectors Closing The oil deflectors on the CE were reinstalled and set to an even setting within the specified tolerances. The Hydrogen seal case was ensured to be cen
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | 994206fdac6a44ad0de3755d0c80e6d4 | 1 | 2011-05-11 | Inspection | Hydrogen Seals, Stator | Oil Deflector Alignment | 6 | Belly Bands, End Shield, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Combustion Inspection (complete) Minor (rotor in) Generator Belly Bands Hot Gas Path Inspection (complete) End Shield(s) Off #1 & 2 Bearing Inspection Bearings Xfire Bellows FMI |  | Oil Deflector Alignment ¦ Belly Bands ¦ End Shield ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | DRAFT REPORT GAS TURBINE INSPECTION REPORT Duke Fayette HGP with Magic for DUKE ENERGY CORPORATION DUKE ENERGY NORTH AMERICA, Unit GT1 Equipment Serial #: 298158 Job Start Date: March 06, 2011 Report Issued: May 11, 2011 FSR #: 10078943 Report Printed: June 22, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: BENJAMIN R PECORA Field Engineer Approved By: MARK RUEFER Service Manager DRAFT REPORT PAGE JOB SUMMARY 1 INSPECTIO
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | f23dc60fed1e370813fbde865d9de581 | 33 | 2011-05-11 | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Fan Blades, Oil Deflector Alignment, Oil Deflectors | Max Top Bottom Sides Outer oil 0.007 0.010 0.007 0.006 0.018 0.007 0.007 0.006 0.018 0.019 0.009 0.007 H2 seal case 0.185 - 0.185 0.185 0.188 0.186 0.185 0.185 0.188 #VALUE! #VALUE! 0.185 inner oil 0.010 - 0.013 0.014 0.018 0.008 0.013 0.00; INSPECTION REPORT Gas Turbine Maintenance 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor 2.xls GE Energy Services Company Proprietary Information Page No 31 g MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 3/; INSPECTION REPORT Gas Turbine Maintenance 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor 3.xls GE Energy Services Company Proprietary Information Page No 32 g End Shield Distortion Check Feeler Gauges Date(m/d #######enerator Serial No.; Particle UT Ultrasonic PT Penetrant CE End Shield Units recorded in:; ECORA BENJAMIN Click Here 962X011 g End Shield Distortion Check Feeler Gauges Date(m/d/y) 3/20/2011 Generator Serial No. |  | Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ Oil Deflectors | . Max Top Bottom Sides Outer oil 0.007 0.010 0.007 0.006 0.018 0.007 0.007 0.006 0.018 0.019 0.009 0.007 H2 seal case 0.185 - 0.185 0.185 0.188 0.186 0.185 0.185 0.188 #VALUE! #VALUE! 0.185 inner oil 0.010 - 0.013 0.014 0.018 0.008 0.013 0.008 0.018 #VALUE! #VALUE! 0.011 Fan Blades 0.055 0.048 0.052 0.059 0.059 0.055 0.048 0.059 0.039 0.020 0.054 Comments: INSPECTION REPORT Gas Turbine Maintenance 2 4 5 6 Left Right 1 Oil 3 Deflector Rotor 2.xls GE Energy Services Company Proprietary Information
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | 9de14f2648b5a09e5741ee2e8698ddad | 36 | 2011-05-11 | Inspection | Field, Hydrogen Seals | MAGIC Inspection | 3 | End Shield, Fan Blades, MAGIC Inspection | Particle UT Ultrasonic PT Penetrant CE End Shield Units recorded in:; Pecora Click Here 298158 .00015 feeler should insert no more than .25" 12 11 10 9 8 7 6 5 4 3 2 1 24 23 22 21 20 19 18 17 16 15 14 13 A F B G C H D I E R2 J R1 L2 L1 ST00063 Page No 34 DRAFT REPORT Fan Assembly;CE fan blade clearance The CE; GENERATOR FIELD 298158 DUKE ENERGY CORPORATION Page No 35 DRAFT REPORT CE Fan blades, condition and installed CE Fan blades, condition and installed GENERATOR FIELD 298158 DUKE ENERGY CORPORATION Page No 36 DRAFT REPORT CE Fan blades, condi; Max Top Bottom Sides Opening Fan Blades 0.046 0.036 0.052 0.052 0.056 0.052 0.052 0.036 0.056 0.061 0.031 0.051 Closing Fan Blades 0.055 0.048 0.052 0.059 0.059 0.055 0.048 0.059 0.039 0.020 0.054 Comments: |  | MAGIC Inspection ¦ End Shield ¦ Fan Blades | . Prepared by INSPECTIONS & CHECKS CODE Vertical Face Runout X Work Carried Out N Not Done NA Not Applicable C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant CE End Shield Units recorded in: OPENING CHECK OPENING CHECKS Location Feeler Location Feeler Location Feeler A Pass Readings taken 1 Pass 13 Pass B Pass approx. 12" apart. 2 Pass 14 Pass C Pass 3 Pass 15 Pass D Pass 4 Pass 16 Pass E Pass 5 Pass 17 Pass F Pass Location Feeler 6 Pass 18 Pass G Pass L1 Pass 7 Pas
UNI035727 | Fayette Energy Facility | GAS_TURBINE_INSPECTION_REPORT_Duke_Fayette_HGP_with_Magic_for_T_R_DUKE_ENERGY_CORPORATION_O_DUKE_ENERGY_NORTH_AMERICA_Unit_GT1_P_Gas_Turbine_298158_2011-03-06 | 298158 | Gas Turbine | f5817aacc8768f6b36110f5b2ebb2aa2 | 9 | 2011-05-11 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | End Shield, Oil Deflector Alignment, Oil Deflectors | RECOMMENDATIONS 298158 DUKE ENERGY CORPORATION Page No 9 DRAFT REPORT (No Parts Used or Recommended for this report) PARTS USED & RECOMMENDED PU=Part Used During the Inspection RI=Part Recommended for Immediate Restock RO=Part Recommended f; End Shield Oil Deflector;CE Oil deflector- opening The CE outer oil deflector, H2 seal case, Mid oil deflector and Inner oil deflector clearances were taken and components were removed |  | Oil Deflector Alignment ¦ End Shield ¦ Oil Deflectors | . Section Component Location Description: Action: 31 Bucket, 2nd Stage Assembly S2B Removed & Inspected Component Removed And Inspected 32 Bucket, 3rd Stage Assembly S3B Removed & Inspected Component Removed And Inspected 33 Bucket, 1st Stage Lockwire S1B & S2B Lockwire Associated Parts 34 Nozzle Arrangement, Stage 1 Assembly S1N Removed & Inspected Component Removed And Inspected 35 Nozzle Arrangement, Stage 1 Assembly S1N measurement checks Dimensional Checks Ok - Measurements Are Within Toler
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | fc1e637c2b113a739dd2e77be5873912 | 1 | 2011-05-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | End Shield, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Support Systems Other Systems Major Inspection (complete) Coupling / Alignment LCI Turbine Modification End Shield(s) Off Excitation Operation / Diagnostics Bearings Turbine Controls Hydrogen Seals Exhaust (MLI 0706,A0 |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | GAS TURBINE INSPECTION REPORT GAS TURBINE MAJOR INSPECTION for DOMINION RESOURCES, INC DOMINION ENERGY, Unit 1B GT Equipment Serial #: 298177 Job Start Date: March 26, 2011 Report Issued: May 06, 2011 FSR #: 10075682 Report Printed: May 18, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: SANG S LEE Field Engineer Approved By: JOSEPH S DAMATO Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMARY 6 RECOMMENDATIONS 9 PARTS U
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | 39a9c190e4497c090e6c84fe85a2cdc6 | 16 | 2011-05-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | All oil deflectors showed little or no wear on teeth.; Tilt pad journal oil seal rings were found with disturbed babbitt.; (a) Rev 0.0 - 08/01/98 GE Energy Proprietary Information Page No 17 g Oil Seal Rings Date(m,d,y) 4/4/2011 Turbine Serial No. | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ EM5260 | . Ensure all TC's are reading after the bearing cap is reinstalled. Ensure new packing glands are available. BEARINGS 298177 DOMINION RESOURCES, INC Page No 14 BEARINGS 298177 DOMINION RESOURCES, INC Page No 15 g Bearings MS 6001, 6001F, 7001F, 9001F Bearing & Seal Clearances, No. 1 Date 4/1/2011 Turbine S/N 298177-1B Prepared by FSR # 10075682 Sketches Enclosed? NO Photos Enclosed? NO Data Type AS FOUND • All axial clearances are measured with rotor against the loaded thrust face. Refer to EM52
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | c289625973624a093d2711b3f857dbf1 | 15 | 2011-05-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | Oil seal rings were cleaned and measured.; The journal seal rings were found with moderate wear on the inner diameter at both T-1 and T-2 locations.; All journal seal rings, forward and aft, were replaced with new.; The oil deflectors were removed from their fits, cleaned, and inspected.; All oil deflectors were cleaned out along with the drain holes. |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | . At the plant's request, all bearing metal thermocouples at the tilt pads were replaced with new. Packing glands at the T-1 and T-2 were replaced with new and resealed. Oil seal rings were cleaned and measured. The journal seal rings were found with moderate wear on the inner diameter at both T-1 and T-2 locations. All journal seal rings, forward and aft, were replaced with new. Please see attached datasheet. The oil deflectors were removed from their fits, cleaned, and inspected. The T-2 inboa
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | 53087a60fa2b1fe0e33d8942e5028245 | 20 | 2011-05-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | Replaced T-1 and T-2 forward and aft seal rings.; AS FOUND All oil deflectors were cleaned and inspected.; No action was necessary and all oil deflectors were returned to service.; S LEE INSPECTION REPORT Gas Turbine Maintenance CONDITION CODE M - Missing Metal W - Worn CR - Cracked DISPOSITION CODE N - No Repair or Replacement Necessary R - Repaired RN - Replaced with New Component Replaced oil seal rings @ 1S9 and 1 | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ EM5260 | . Particle UT Ultrasonic PT Penetrant Location Oil Deflector Journal Clearance Condition Number A-Dia B-Dia C-Dia Dia Average Min. Max. Comment OLD Thrust FWD 16.013" 16.014" 16.012" 15.999" .014" .013" .015" Thrust AFT 16.007" 16.006" 16.016" 15.999" .010" .007" .017" T1 FWD 16.513" 16.514" 16.500" 16.499" .010" .001" .015" Worn T1 AFT 16.506" 16.507" 16.505" 16.499" .007" .006" .008" Worn T2 FWD 16.500" 16.497" 16.420" 16.497" -.024" -.077" .003" Worn T2 AFT 16.503" 16.502" 16.510" 16.497" .00
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | 275a4e386f8f187710ee52a78febe920 | 141 | 2011-05-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The generator was de-gassed overnight with plans to remove the outer oil deflectors in order to replace the lift oil hoses on the generator bearings.; Another lift check was performed and a 3 mil left was measured with a dial indicator on all bearings (proximity probes measured a 3 mil lift at turbine T-2 bearing).; A 0.55 mil / sec vibration was steady at the T-1 gas turbine bearing. |  | Oil Deflector Alignment ¦ Oil Deflectors | . Hydraulic header pressure remained at 3400 PSIG. No lift oil lines were changed out at the generator bearings during this outage. The generator was de-gassed overnight with plans to remove the outer oil deflectors in order to replace the lift oil hoses on the generator bearings. On Tuesday April 26, the lift oil hoses at T-3 and T-4 generator bearings were replaced. The turning gear SSS clutch housing and coupling guard was removed for inspection. The SSS clutch was manually engaged and diseng
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | 9f4b625cf9ee7b9446ba53e238343640 | 129 | 2011-05-06 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | . Post bigfoot modification, the new clearance diagram 101T2161, as issued under the FMI, was used. PLEASE NOTE S14 TIP CLEARANCE ON 101T2161 SHOWS INCORRECT VALUE FOR MAXIMUM ALLOWABLE. IT SHOWS A HIGH VALUE OF 0.199 INCH. THE CORRECT VALUE SHOULD BE 0.119 INCH AS HIGHLIGHTED ON THE ATTACHED DATASHEET. Bearing seal and oil deflector clearances were compared against the specifications. Closing bearing clearances showed little deviation when compared to values derived from inner diameter readings
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | 048a45962c18a376710fd802b2f41f39 | 67 | 2011-05-06 | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | . Visual inspections showed moderate wear of the diaphragm seals from radial rubs to the rotor. Damage to the rotor from these rubs were blend repaired followed by flapper peening and NDE inspections. Minor wear was also evident on the discourager seal from contact with the 2nd stage bucket angel wings. Nozzle Arrangement, Stage 3 Assembly; The 3rd stage nozzles were CBM inspected and passed. Please review attached inspection report for details. The 3rd stage nozzle cloth seals were inspected pr
UNI035718 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_GAS_TURBINE_MAJOR_INSPECTION_for_DOMINION_RESOURCES_INC_DOMINION_ENERGY_Unit_1B_GT_Gas_Turbine_298177_2011-03-26 | 298177 | Gas Turbine | 88f490e403ec26611eda2e2c0ad384ac | 23 | 2011-05-06 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | N - No Repair or Replacement Necessary R - Repaired RN - Replaced with New Component Replaced oil seal rings @ 2S3 and 2S4. |  | Focused Generator Review ¦ Seal Rings | . 2 Date 4/11/2011 Turbine S/N 298177 - 1B Prepared by FSR # 10075682 Sketches Enclosed? NO Photos Enclosed? NO Data Type AS LEFT SEAL INSPECTION Clearances Visual Inspection DIM Left Right Top Bottom Condition Disposition Comments 2S1 0.022 0.018 OK OK 2S2 0.022 0.021 OK OK 2S3* 0.007 0.010 0.010 NEW RN 2S4* 0.006 0.007 0.011 NEW RN FWD STRAP AFT STRAP DIM LEFT RIGHT LEFT RIGHT * Measure total ring float at each BC1 0.000 0.000 0.000 0.000 location. BC2 0.000 0.000 0.000 0.000 Comments: S LEE I
UNI035961 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_1GT1_Hot_Gas_Path_Inspection_Spring_2010_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_HANGING_ROCK_LLC_Unit_1GT1_Gas_Turbine_298112_2010-05-01 | 298112 | Gas Turbine | cac45f329e4cbb34d6fe282a95f1a1f9 | 1 | 2010-06-23 | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection |  |  | MAGIC Inspection | GAS TURBINE INSPECTION REPORT 1GT1 Hot Gas Path Inspection Spring 2010 for DUKE ENERGY HANGING ROCK LLC ,Unit 1GT1 Equipment Serial #:298112 Job Start Date :May 01,2010 Report Issued :June 23,2010 FSR #:97JD0730 Report Printed :June 23,2010 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: BRIAN TOOHEY Field Engineer Approved By: MARK RUEFER Mark A Ruefer PAGE JOB SUMMARY 1 PARTS USED & RECOMMENDED 4 ALIGNMENT & CLEARANCES OVERV
UNI035964 | Hanging Rock Energy Facility | GAS_TURBINE_INSPECTION_REPORT_2GT1_2_Bearing_Inspection_for_DUKE_ENERGY_CORPORATION_DUKE_ENERGY_HANGING_ROCK_LLC_Unit_2GT1_Gas_Turbine_298127_2010-05-04 | 298127 | Gas Turbine | fb3b73f8d9ec2aaa8c86877ee9625460 | 7 | 2010-05-19 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | PAC case number 200 was opened and engineering recommended an inspection of the bearing seal rings. |  | Focused Generator Review ¦ Seal Rings | . Diffuser, Exhaust;Assembly;'W' Seal Purchase a new 'W' seal for future outages. 2. Bearing, Journal;Housing;Parts Replace used stock for next outage. RECOMMENDATIONS Item InsRec PU RI QTY UM PartsDescription CustStk Catalog Drawing 1 1 X 1 Each Bearing, Journal,Assembly,Inboard seal ring G1502 159A0601P001 2 1 X 1 Each Bearing, Journal,Assembly,Outboard seal ring G1502 159A0601P002 3 2 X 32 Each Inlet Guide Vane,Spring,Spring washer G0811 158A7887P001 4 3 1 Each Diffuser, Exhaust,Assembly,Flex
UNI036336 | Casco Bay Power Station | g_GE_Energy_Services_D11_Major_Inspection_Technical_Direction_for_Dynergy__LS_Power_MAINE_INDEPENDENCE_Unit_1_Steam_Turbine_270T432_2007-04-09 | 270T432 | Steam Turbine | 4f879efab5587f8a053e5323c7d0b8e7 | 35 | 2007-07-12 | Inspection | Stator | Focused Generator Review | 2 | Stator Winding, Wedges |  |  | Focused Generator Review ¦ Stator Winding ¦ Wedges | Core Wedge; Collector End Stator Generator Serial #290X432 sustained damage to an "End Wedge" Assembly during the Major Inspection. The Customer requested GE Product Service to evaluate the damage and issue a repair recommendation. (Refer to PAC # 20070427-0097). GE Product Service evaluated the damage and issued instruction to inspect the Generator in accordance with GEK103566c. They instructed to replace the damaged end wedge during this outage. A thorough visual inspection of the stator bar b
UNI036336 | Casco Bay Power Station | g_GE_Energy_Services_D11_Major_Inspection_Technical_Direction_for_Dynergy__LS_Power_MAINE_INDEPENDENCE_Unit_1_Steam_Turbine_270T432_2007-04-09 | 270T432 | Steam Turbine | 9dc55c49533969f1dde4e6a55fa281fc | 14 | 2007-07-12 | Mechanical |  | Blue Check | 1 | Blue Check | 0.001 0.001 0.001 0.001 0.001 0.001 Comments GE Apparatus Service Center - Medford RHTSTPVLV (97) Page 9 WRNG = Warning Duke-Veazie Left Blue Check DESIGN Turbine Serial No.; 117E2250 G1000 Hone & Try Bar Dye Check Duke-Veazie Right Blue Check -- Elongated stem pin hole, Weld repair stem nut -- Replace Key -- Replace stem pin -- Hammer Mark on SV Disc, Polish / Grind Disc -- Skim Cut Pressure Seal Head Seal Area; 117E2250 G1000 Hone & Try Bar Dye Check Duke-Veazie Right Blue Check -- Weld repaired, drilled, and reamed stem nut -- Replaced Key -- Replaced stem pin -- Polished / Ground Disc -- Machined .008" off of Pressure Seal Head Seal Area to clea |  | Blue Check | Combined Stop Valve Stem; both Universal Plant Services contracted the Wood Group Inc. to disassemble and Inspect the Main Stop Valve Stems for total indicated run-out and Stem to Bushing Clearances. The Wood Group was "unable" to disassemble the valve stems without causing damage the assemblies. They returned the Valve Assemblies to site untouched. The Customer requested the GE Medford Service Shop to disassemble and inspect the Valve Stems for total indicated run-out as well as Stem to Bushing
UNI036336 | Casco Bay Power Station | g_GE_Energy_Services_D11_Major_Inspection_Technical_Direction_for_Dynergy__LS_Power_MAINE_INDEPENDENCE_Unit_1_Steam_Turbine_270T432_2007-04-09 | 270T432 | Steam Turbine | 41f913810ab795ebd871d0bddac1f657 | 11 | 2007-07-12 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | RI=Part Recommended for Immediate Restock RO=Part Recommended for the Next Inspection Page 11 Item Ins Rec PU QTY UM Parts Description Cust Stk # Catalog # Drawing # 1 8 4 Each HP Diaphragm,Key,Clearance Key Stg1&2 0900 142C5824P0005 2 8 4 Each HP Diaphragm,Key,Clearance Keys 0900 244A2827P0001 3 9 14 Each LP Diaphragm,Key,Clearance Key all 0900 142C5824P0005 4 9 14 Each LP Diaphragm,Key,Clearance Keys 0900 244A2827P0001 5 3 0 Shaft Packing,Assembly, 6 6 0 Packing Casing,Assembly, 7 14 1 Each Co
UNI036336 | Casco Bay Power Station | g_GE_Energy_Services_D11_Major_Inspection_Technical_Direction_for_Dynergy__LS_Power_MAINE_INDEPENDENCE_Unit_1_Steam_Turbine_270T432_2007-04-09 | 270T432 | Steam Turbine | 89069556f00022e5ca94404817b9f53d | 4 | 2007-07-12 | Inspection | Stator | Focused Generator Review | 1 | Wedges |  |  | Focused Generator Review ¦ Wedges | Page 4 Inspec tion No. Shift No. n Descri ption Action ned V 11 1 Crack ed Repair ed ned Stop 12 1 Stem Preven tive Maint enance Disass emble d and Inspec ted Shell 7 1 bly Dama ged Used As Is - Monit or Condit ion HP Page 5 agm 4 1 bly Dama ged Used As Is - Warra nts Repair 8 1 Key Dama ged Used As Is - Warra nts Replac ement 1 1 on Erosio n Spe Used As Is - Warra nts Repair IP agm 5 bly Dama ged Used As Is - Warra nts Repair LP agm 9 1 Key Dama Used Page 6 ged As Is - Warra nts Replac ement 2
UNI036336 | Casco Bay Power Station | g_GE_Energy_Services_D11_Major_Inspection_Technical_Direction_for_Dynergy__LS_Power_MAINE_INDEPENDENCE_Unit_1_Steam_Turbine_270T432_2007-04-09 | 270T432 | Steam Turbine | e284c616089947d7900ebb8ae6d6169e | 36 | 2007-07-12 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | The Seal Oil Piping was cut away from the Lower Half End Shields to allow for easier disassembly of the Generator. | GEK81515 | Focused Generator Review ¦ End Shield ¦ GEK81515 | H2 Seal Oil Piping Piping; Feed & Drain Lines Generator Serial #290X432 Seal Oil Piping was modified during the Major Inspection. The Seal Oil Piping was cut away from the Lower Half End Shields to allow for easier disassembly of the Generator. The Lube Oil Feed Line for T-4 Bearing was also removed (cut) at this time. A PAC Case was opened to evaluate the proper method to flush piping whenever an oil system (piping) is modified. (Refer to PAC Case # 20070510-0030). GE Product Service evaluated
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | c97678728376e0bdf5e30a07091ec315 | 11 | 2006-05-31 | Mechanical | Hydrogen Seals | Blue Check; Oil Deflector Alignment | 4 | Blue Check, Oil Deflector Alignment, Oil Deflectors, Seal Rings | 5,6 The T-5 and T-6 bearing seal rings were disassembled, cleaned and inspected.; Dimensional checks were performed on the seal rings and compared to the journal diameter.; A spare set of T-5 and T-6 bearing seal rings should be available for the next outage.; The joint was ground flat and a blue check to the upper half was conducted to insure all high spots were removed and the joint would close.; The final oil deflector alignment is recorded on the applicable data sheet included in this report. |  | Blue Check; Oil Deflector Alignment ¦ Blue Check ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | (None this outage) BEARINGS Generator Journal Bearing Babbitt; 5,6 The T-5 and T-6 journal bearings were disassembled and inspected. A dye penetrant test was conducted on the babbitted tilt pads and crack-like indications were noted on the lower pads of both T-5 and T-6 bearings. The pads were removed from both bearing housings and prepped for shipping to an offsite repair facility. Spare bearing assemblies for both T-5 and T-6 were available from customer stock and were installed at assembly. R
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | 9511440775874d0df6fe284f0ebd6613 | 38 | 2006-05-31 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | CE The CE hydrogen seal assembly was disassembled, cleaned and inspected.; A refurbished set of seal rings was available and were used at assembly.; The seal rings were contact checked to the casing and were lapped as needed until a satisfactory contact pattern was achieved.; The existing seal rings should be repaired and placed in stock and retained as a spare.; TE The TE hydrogen seal assembly was disassembled, cleaned and inspected. |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | H2 Seal Oil System Ring; CE The CE hydrogen seal assembly was disassembled, cleaned and inspected. The air and gas side seal ring segments were removed and set on a surface plate. The rings were checked for flatness with a dial indicator and a feeler gauge to the surface plate. The lower half air side ring segment was found slightly warped with a .004" runout noted from the butt joint to butt joint on the sealing face. The air side ring segments were clamped together and were measured. The avera
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | 7aa4ae6a7de16d739a7eb41ad2d49c86 | 15 | 2006-05-31 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | A B C C T-5 brg seal rings(a) Bearing Oil Seal Rings Date(m/d/y) 5/11/2006 Turbine Serial No.; A B C C T-6 brg seal rings(a) Date(m,d,y) 5/18/2006 Train Tilting Pad LOAD ON PAD INSPECTIONS & CHECKS Journal Inspection X Babbit Inspection X Lift Check Dimensional Clearance Check X T/C Calib.; BABBITT SMEAR NUMBER AFT AFT AFT AFT AFT AFT NO BABBITT LOSS WAS BABBITT SMEARED ( )? folded over BABBITT DAMAGE ZONES (Each Pad) GT32A021 Journal brgs(b) Oil Deflector Alignment Date (m,d,y) 5/18/2006 Turbine Serial No.; A B B A C C Oil deflectors(a) |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | Date(m/d/y) 5/11/2006 Turbine Serial No. 290T259 Prepared by J. RAZZANO Inspection Final Initial or Final Seal Location A B C Average Shaft Dia. Clearance TE Seal 16.014 16.019 16.020 16.0177 15.999 0.0187 GE Seal 16.009 16.022 16.019 16.0167 15.999 0.0177 Comments: Final dimensions. A B C C T-5 brg seal rings(a) Bearing Oil Seal Rings Date(m/d/y) 5/11/2006 Turbine Serial No. 290T259 Prepared by J. RAZZANO Inspection Final Initial or Final Seal Location A B C Average Shaft Dia. Clearance TE Seal
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | 00c2b4eedd3e95d4ef4bc8861a0e343b | 40 | 2006-05-31 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Date(m,d,y) 5/10/2006 Turbine Serial No. 290T259 Prepared by J. RAZZANO INSPECTIONS & CHECKS CODE Teeth Inspected X X Work Carried Out Journals Inspected X N Not Done Drain Holes Inspected NA Not Applicable Inspect for Rubs X C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Location Oil Deflector Journal Clearance Condition Number A-Dia B-Dia C-Dia Dia Average Min. Max. Comment TE H2 seal 16.042" 16.037" 16.046" 16.000" .042" .037" .046" CE H2 seal 16.034" 16.039" 1
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | 96473db71318ba35bce3bfe5d505fc0e | 14 | 2006-05-31 | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The final oil deflector alignment is recorded on the applicable data sheet included in this report. |  | Oil Deflector Alignment ¦ Oil Deflectors | . The oil deflector was installed and aligned to the rotor. The final oil deflector alignment is recorded on the applicable data sheet included in this report. Oil Deflector Assembly; T-6 outer The T-6 bearing outer oil deflector was cleaned, visually inspected and measured. Some very minor wear was noted and the oil deflector was suitable for continued use without repair. The teeth were in good condition with no notable rubs. The oil deflector clearances were within tolerance. Dimensions were i
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | 1c462dbb0a4d61ba32dce37c89de1be6 | 4 | 2006-05-31 | Inspection | Hydrogen Seals | Focused Generator Review | 2 | End Shield, Seal Rings | CE The existing seal rings should be repaired and placed in stock and retained as a spare.; TE The existing seal rings should be repaired and placed in stock and retained as a spare.; End Shield;; 5,6 A spare set of T-5 and T-6 bearing seal rings should be available for the next outage. |  | Focused Generator Review ¦ End Shield ¦ Seal Rings | Page 4 Inspec tion No. Shift No. n Descri ption Action ator l 2 1 bly Dimen sional Check s Ok - Measu rement s Are Within Tolera nce 3 1 bly Dimen sional Check s Ok - Measu rement s Are Within Tolera nce 1 1 t Crack ed Replac ed 4 1 ion Megge r Test Satisfa ctory Result s 5 1 Seal Out Of Replac Page 5 ring Round ed Oil tor 9 1 bly Dama ged Weld Repair ed 6 1 bly Cleane d And Inspec ted Good Condit ion - No Visual Defect s 8 1 bly Cleane d And Inspec ted Good Condit ion - No Visual Defect s 7 1 b
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | 8c49b9372552c671ce48626191913fc3 | 22 | 2006-05-31 | Inspection | Field | Focused Generator Review | 2 | Collector Rings, Fan Blades | Collector fan The collector fan blades were removed, cleaned and visually inspected.; No indications were noted and all of the fan blades were returned to service.; The fan blades were installed on the field at assembly, torqued to design specifications and lock tabs bent.; TE & CE The main axial fan blades for both the turbine and collector ends of the field were removed, cleaned and visually inspected.; Field Collector Rings; |  | Focused Generator Review ¦ Collector Rings ¦ Fan Blades | Fan Fan Blade; Collector fan The collector fan blades were removed, cleaned and visually inspected. A dye penetrant test was performed on all of the blades. No indications were noted and all of the fan blades were returned to service. The fan blades were installed on the field at assembly, torqued to design specifications and lock tabs bent. Final blade tip to baffle clearances were recorded at assembly and are included on the applicable data sheet in this report. Fan Fan Blade; TE & CE The main
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | dd7be768b82e780125a3606b081ac60a | 26 | 2006-05-31 | Inspection | Field | Focused Generator Review | 1 | Collector Rings | C cplg-final(a) Date (m/d/y) 5/21/2006 Turbine S/N 290T259 Prepared by Component * LP - GEN CPLG Component * Tolerance +/- MIC READING MIC READING 1 12-14 12.698" 12.710" 12 Mils 2 12-14 12.698" 12.710" 12 Mils 3 12-14 12.696" 12.708" 12 Mi |  | Focused Generator Review ¦ Collector Rings | Date (m,d,y) ### Turbine Serial No. 290T259 Prepared by J. RAZZANO POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Median Min. Max Top Bottom Sides TE 60 47 44 Comments As found clearances. ST00381 2 LEFT RIGHT 6 1 4 3 5 ROTOR Fan clearances-as found TE(a) Generator Fan Date (m,d,y)##### Turbine Serial No. 290T259 Prepared by J. RAZZANO POSITION (Mils) CLEARANCE IDEAL POSITION Location 1 2 3 4 5 6 Median Min. Max Top Bottom Sides TE 40 27 54 61 68 51 53 27 68 63 32 52 Comments Fina
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | ed386d56ed940ac90143d8a863ff6389 | 21 | 2006-05-31 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | End Shield Assembly;; Inner TE & CE The TE & CE inner end shields were removed, cleaned and visually inspected.; It should be noted that the inner end shields are not permanently doweled to the stator.; Outer TE & CE The TE & CE outer end shields were removed, cleaned and visually inspected.; At assembly the end shields were pumped with Dow Corning Flourasilicone sealant. |  | Focused Generator Review ¦ End Shield | End Shield Assembly; Inner TE & CE The TE & CE inner end shields were removed, cleaned and visually inspected. No problem areas were noted. It should be noted that the inner end shields are not permanently doweled to the stator. Temporary 1/2" diameter dowels were used at assembly to aid in alignment but the dowels were removed prior to final assembly of the generator. Temporary 1/2" diameter dowels for the lower half inner endshields on the turbine and collector ends should be available during
UNI000886 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Generator_Field_Changeout_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_6_Steam_Turbine_270T259_2006-05-07 | 270T259 | Steam Turbine | b97cdddcbeb0404f4c0cbcf677b5c4c2 | 10 | 2006-05-31 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | RI=Part Recommended for Immediate Restock RO=Part Recommended for the Next Inspection Page 10 Item Ins Rec PU QTY UM Parts Description Cust Stk # Catalog # Drawing # 1 1 X 1 Each Generator Journal Bearing,Babbitt,5 N/A 0964E146P0019 2 1 X 1 Each Generator Journal Bearing,Babbitt,6 N/A 0964E146P0020 3 5 X 1 Each Generator Journal Bearing,Seal ring,5 N/A 159A1090 4 11 X 1 Each H2 Seal Oil System,Ring,CE - Air N/A 181D1438G0003 5 11 X 1 Each H2 Seal Oil System,Ring,CE - Gas N/A 181D1438G0006 6 11 X
UNI000885 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Spring_2006_Valve_Inspection_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_5_Steam_Turbine_270T260_2006-04-29 | 270T260 | Steam Turbine | 2e3673e27f93095b66b3b0c96481cb55 | 16 | 2006-05-25 | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | Retaining Rings, Seal Rings | Crosshead OD 7.238 7.237 Clearance 0.014 0.015 B Bushing ID 3.001 3.001 TRY BAR Stem OD 2.990 2.990 Clearance 0.011 0.011 Bushing ID 3.001 3.001 D Stem OD 2.990 2.990 Clearance 0.011 0.011 H Bushing ID 3.256 3.256 TRY BAR Stem OD 3.240 3.24 |  | Focused Generator Review ¦ Retaining Rings ¦ Seal Rings | Valve; During the outage the Main Stop and Control valve was disassembled and inspected. The valve was rebuilt using parts called for in TIL-1531. The following routine maintenance procedures were performed: dimensional checks, NDT, disk-to-seat contact checks, and a try bar check of stem bushing alignment. There was scale build up present in the valve. This scale was not substantial enough to warrant grit blasting. The NDT showed cracking of the anti-swirl dam. These cracks were ground out and
UNI000885 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Spring_2006_Valve_Inspection_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_5_Steam_Turbine_270T260_2006-04-29 | 270T260 | Steam Turbine | 91ac41829cba53aceff3050091525f3d | 6 | 2006-05-25 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  |  | Focused Generator Review ¦ Seal Rings | . P0030 on 148D4985 (IV) and 145D3217 (RSV) 2 PL Ref. P0032 on 148D4985 (IV) and 145D3217 (RSV) 3 PL Ref. P0035 on 148D4985 (IV) and 145D3217 (RSV) 4 Four used on each IV and RSV disk dump valve 5 A thicker spacer may be required if the stem is replaced spring 2006 ST5 outage parts usedREVISIONS 2 Page 7 Note Qty Gasket CSV/CV Seat 26 Bolt, CSV/CV Seat 6 Lockplate, SV Coupling 5 Spacer, SV Coupling Seal, SV Actuator Notes: Added Sithe stock number to GE list Revise the Sithe parts list to remove
UNI000885 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Spring_2006_Valve_Inspection_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_5_Steam_Turbine_270T260_2006-04-29 | 270T260 | Steam Turbine | 410c6e3529fc6f1d135c933b56bcffd3 | 10 | 2006-05-25 | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | Page 10 Inspection No. Section Component Location Action Combined Stop/CV Valve General Valve Inspection Routine Valve Inspection Completed Combined Reheat Int Valve Assembly General Valve Inspection Routine Valve Inspection Completed Packing Casing 3 Casing Visual Inspection Good Condition - No Visual Defects Lubrication System System Visual Inspection Good Condition - No Visual Defects RECOMMENDATIONS SHOULD BE DONE ON A REGULAR MAINTENANCE SCHEDULE... 1. Valve, Combined Stop/CV; Valve; The re
UNI000885 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Spring_2006_Valve_Inspection_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_5_Steam_Turbine_270T260_2006-04-29 | 270T260 | Steam Turbine | 5acfafa8de525cf6faf9008d1c3c2526 | 14 | 2006-05-25 | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | TIL # 1531 11" Control Valve Disc Cracking During the outage the Main Stop and Control valve was disassembled and inspected. The valve was rebuilt using parts called for in TIL-1531. The following routine maintenance procedures were performed: dimensional checks, NDT, disk-to-seat contact checks, and a try bar check of stem bushing alignment. There was scale build up present in the valve. This scale was not substantial enough to warrant grit blasting. The NDT showed cracking of the anti-swirl da
UNI000885 | INDEPENDENCE POWER STATION | g_GE_Energy_Services_Spring_2006_Valve_Inspection_for_SITHEINDEPENDENCE_POWER_PARTNERS_Sithe_Northeast_Unit_5_Steam_Turbine_270T260_2006-04-29 | 270T260 | Steam Turbine | 3cf9ca8dc1db6ffcbd153222609f423a | 20 | 2006-05-25 | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Crosshead OD 7.238 7.238 Clearance 0.015 0.014 B Bushing ID 3.006 3.006 TRY BAR Stem OD 2.987 2.987 Clearance 0.019 0.019 Bushing ID 3.006 3.006 D Stem OD 2.987 2.987 Clearance 0.019 0.019 H Bushing ID 4.501 4.498 TRY BAR Stem OD 4.486 4.48 |  | Focused Generator Review ¦ Seal Rings | Combined Reheat Int Valve Assembly; Both the left and right hand combined intercept reheat valves were disassembled during the outage. The valve parts were cleaned and inspected. Attached in this report are the dimensional data sheets and photos of the contact checks performed. Both of these valves had scale build up on the valve seats and bodies. The scale was determined not to need any special attention at this time. The valve seats were lapped to remove the scale and achieve 100% contact. The
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | 77e9a82941e0f05260831d60de474b0b | 209 |  | Repair | Field, Stator | Red Eye Repair | 17 | 10-minute 5000 VDC Megger PI, 10-minute Megger, Collector Rings, DC Leakage, End-winding, Focused Generator Inspection, Greasing, High Voltage Bushings, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Visual inspection using MAGIC robot and borescope, Wedge Tightness Test, Wedges, Winding Resistance | 1 - Visual Inspection on Stator Air-Gap Region using the MAGIC Robot 2 - Visual Inspection on Stator End Winding Assembly (Visual and Magic Borescope) 3 - Visual Inspection on Generator Stator Frame 4 - Visual Inspection on High Voltage Bus; 1 - Armature Winding Resistance Test 2 - As found Armature Insulation Resistance Test w/Polarization Index (PI) @ 5000V 3 - RTD Ground Insulation Test (Megger).; 4 - RTD Resistance Test 5 - As found DC Leakage test @ at the GE recommended value of 36 KVDC GENERATOR REPAIR SCOPE:; 1 - Clean CE Stator windings with denatured alcohol, clean rags, and bottle brushes 2 - Apply Red Eye Epoxy (A50A607) to all greasing/dusting locations 3 - Apply Flood Resin (A50A262) to all areas coated with Red Eye Epoxy 4 - Paint CE End ; Due to not performing the GE recommended AC/DC High Potential test at neither the GE nor IEEE value specific for this unit, GE could provide a definitive assessment of the condition of the stator winding insulation's suitability for service | GEK 103566 | Red Eye Repair ¦ 10-minute 5000 VDC Megger PI ¦ 10-minute Megger ¦ Collector Rings ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ GEK 103566 | the core. Inspections of the generator field showed no major abnormalities and was found in satisfactory condition. The results of the electrical test were satisfactory and didn't give any indications for alarm. All Visual inspections and Electrical tests were performed in accordance with GEK 103566K. Generator components tested and inspected during this outage period are discussed, in detail, within the body of this report. Photos and data sheets relevant to this outage inspection are attached
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 6303f493bf7cc13df42e35826be7eef2 | 222 |  | Repair | Field, Stator | Red Eye Repair | 16 | 10-minute 5000 VDC Megger PI, 10-minute Megger, Collector Rings, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, MAGIC Inspection, Polarization Index, Red Eye Repair, Retaining Rings, Stator Winding, Visual inspection using MAGIC robot and borescope, Wedge Tightness Test, Wedges, Winding Resistance | 1 - Visual Inspection on Stator Air-Gap Region using the MAGIC Robot 2 - Visual Inspection on Stator End Winding Assembly (Visual and Magic Borescope) 3 - Visual Inspection on Generator Stator Frame 4 - Visual Inspection on High Voltage Bus; 1 - Armature Winding Resistance Test 2 - As found Armature Insulation Resistance Test w/Polarization Index (PI) @ 5000V 3 - RTD Ground Insulation Test (Megger).; 4 - RTD Resistance Test 5 - As found DC Leakage test @ at the GE recommended value of 36 KVDC GENERATOR REPAIR SCOPE:; 1 - Clean CE Stator windings with denatured alcohol, clean rags, and bottle brushes 2 - Remove ties at Axial Support #1 and #6 3 - Apply Red Eye Epoxy (A50A607) to entire End Winding Support System 4 - Apply Flood Resin (A50A262) to entire ; Due to not performing the GE recommended AC/DC hipotential test at neither the GE nor IEEE value specific for this unit, GE could provide a definitive assessment of the condition of the stator winding insulation's suitability for service pe | GEK 103566 | Red Eye Repair ¦ 10-minute 5000 VDC Megger PI ¦ 10-minute Megger ¦ Collector Rings ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ GEK 103566 | Inspections of the generator field showed no major abnormalities and was found in satisfactory condition. All Visual inspections and Electrical tests were performed in accordance with GEK 103566k. Generator components tested and inspected during this outage period are discussed, in detail, within the body of this report. Photos and data sheets relevant to this outage inspection are attached to this report as well. GENERATOR STATOR VISUAL INSPECTION (Performed): 1 - Visual Inspection on Stator Ai
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | b3fc9cdcca5e6dd29a75f2c6be6b8b4b | 111 |  | Electrical | Hydrogen Seals, Stator | DLRO; Winding Resistance | 14 | AC Impedance, Belly Bands, Core, DC Hipot, DC Leakage, DLRO, End Shield, Focused Generator Inspection, Greasing, MAGIC Inspection, Polarization Index, Stator Winding, Wedges, Winding Resistance | 337X711 Generator U21 Test And Inspect Report 11_2_20 REV1 Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • Core compression flange nut torque check • Removal of existin; New shim packs were installed in all three belly bands and gap measurements were made on a best effort basis to ensure adequate contact between the belly bands and the generator spring bars.; Belly bands were final torqued to a value of 500ft/lbs and locking welds were completed on the shim packs and bolts for all three belly bands.; Generator U21 Test And Inspect Report 11_2_20 REV1 Job Summary • Core tightness completed on the TE core compression nuts in the four cardinal positions.; No further checks of additional core compression nuts were required or requested by the customer. |  | DLRO; Winding Resistance ¦ AC Impedance ¦ Belly Bands ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ DLRO | For Lamar Power Partners Generator Serial #: 337X711 Generator U21 Test And Inspect Report 11_2_20 REV1 Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • Core compression flange nut torque check • Removal of existing shim packs and re-torqueing of belly bands • MAGIC robotic inspection • Stator slot RTD measurement and megger • Field AC Impedance, resistance, and 500 vDC megger • Stator megger/PI 5KvDC prior to belly band tigh
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 5f97ed4ae41999725bffaf8ffa608f27 | 71 |  | Electrical | Field, Hydrogen Seals, Stator | DLRO; Winding Resistance | 13 | AC Impedance, Collector Rings, Core, DC Leakage, DLRO, End Shield, Focused Generator Inspection, High Voltage Bushings, MAGIC Inspection, Polarization Index, Stator Winding, Wedges, Winding Resistance | Dave Cathey, Steve Proctor Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • MAGIC robotic inspection • Stator slot RTD resistance measurement and megger 500vDC • Field A; The lower half end shield (CE) was in place and the (TE) was not opened, except for the round access cover to route the dehumidifier duct work.; A MAGIC inspection was performed, there was evidence of dusting on the wedges and end windings.; Job Summary • DC resistance measurements were made using a Digital Low Resistance Ohmmeter (DLRO) and resistances were found to be consistent with factory resistance.; A 5000vDC Megger test was conducted for 10 minutes on each isolated phase of the stator winding with the other two phases grounded and Polarization Index calculated. |  | DLRO; Winding Resistance ¦ AC Impedance ¦ Collector Rings ¦ Core ¦ DC Leakage ¦ DLRO ¦ End Shield | For Lamar Power Partners Generator Serial #: 290T435 Generator Test and Inspect MAGIC Stator Inspection: William Howard Generator Specialist: Dave Cathey, Steve Proctor Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • MAGIC robotic inspection • Stator slot RTD resistance measurement and megger 500vDC • Field AC Impedance, resistance, and 500 vDC megger • Stator resistance, megger/PI 5KvDC • Stator DC Leakage test at 36KvDC Jo
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | dadef090a81d9ecc9d2aea0eefe1848c | 242 |  | Repair | Stator | Red Eye Repair | 13 | DC Leakage, End-winding, Focused Generator Inspection, Greasing, High Voltage Bushings, MAGIC Inspection, Polarization Index, Red Eye Repair, Stator Winding, Visual inspection using MAGIC robot and borescope, Wedge Tightness Test, Wedges, Winding Resistance | 1 - Visual Inspection on Stator Air-Gap Region using the MAGIC Robot 2 - Visual Inspection on Stator End Winding Assembly (Visual and Magic Borescope) 3 - Visual Inspection on Generator Stator Frame 4 - Visual Inspection on High Voltage Bus; 1 - Armature Winding Resistance Test 2 - As found Armature Insulation Resistance Test w/Polarization Index (PI) @ 5000V 3 - RTD Ground Insulation Test (Megger).; 4 - RTD Resistance Test 5 - As found DC Leakage test @ at the GE recommended value of 36 KVDC GENERATOR REPAIR SCOPE:; 1 - Clean CE Stator windings with denatured alcohol, clean rags, and bottle brushes 2 - Remove ties at Axial Support #1 and CR Block & Tie Location "E" 3 - Perform Cogebi Insulation repair of damaged connection rings 4 - Apply Red Eye Epoxy; Due to not performing the GE recommended AC/DC hipotential test at neither the GE nor IEEE value specific for this unit, GE could provide a definitive assessment of the condition of the stator winding insulation's suitability for service pe |  | Red Eye Repair ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ High Voltage Bushings ¦ MAGIC Inspection | Generator components tested and inspected during this outage period are discussed, in detail, within the body of this report. Photos and data sheets relevant to this outage inspection are attached to this report as well. GENERATOR STATOR VISUAL INSPECTION (Performed): 1 - Visual Inspection on Stator Air-Gap Region using the MAGIC Robot 2 - Visual Inspection on Stator End Winding Assembly (Visual and Magic Borescope) 3 - Visual Inspection on Generator Stator Frame 4 - Visual Inspection on High Vo
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 82049c0faec09d9c1017a76cb31ac27b | 224 |  | Repair | Field, Stator | Red Eye Repair | 13 | Centering Ring, Collector Rings, End-winding, Fan Blades, Field Body, Focused Generator Inspection, Greasing, MAGIC Inspection, Red Eye Repair, Retaining Rings, Stator Winding, Wedge Tightness Test, Wedges | Particle PT Penetrant NA Not Applicable S Satisfactory Z Zyglo INSPECTIONS & CHECKS GENERAL STATOR SLOT PORTION Hardware (bolts, nuts, etc.) VS Between Bar Filler Movement Axially Internal Cleanliness ( Foreign Material) Core iron Condition; Greasing severity between Light, and Moderate was observed within CR Block and Tie assemblies "B", "E" ,"I" , "M", "O", "P", "R", within axial support ties #1, #2, #6, #7, #8, #9, and #11 and within several stator bar-to-bar ties.; The CR Block and Tie assemblies identified with moderate greasings did not show any signs of loose ties therefore each location can be cleaned and coated with the recommended epoxy application to migate further movement.; Additionally, the entire CE end winding should be cleaned with denatured alcohol, and all minor greasing locations identified should be coated with Red Eye Epoxy (A50A607), Flood Resin (A50A262) & Epoxy Paint (A50A535B).; SEE END WINDING DUSTING DATA SHEET D316224 FOR DUSTING AND GREASING LOCATIONS. |  | Red Eye Repair ¦ Centering Ring ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ Field Body ¦ Focused Generator Inspection | . 337X768 - GTG1 Prepared by Sherrod Childers CODE X Work Carried Out C See Comments U Unsatisfactory UT Ultrasonic N Not Done V Visual Inspection MP Mag. Particle PT Penetrant NA Not Applicable S Satisfactory Z Zyglo INSPECTIONS & CHECKS GENERAL STATOR SLOT PORTION Hardware (bolts, nuts, etc.) VS Between Bar Filler Movement Axially Internal Cleanliness ( Foreign Material) Core iron Condition VS oil, dust VC Ventilation Ducts Free of Material VS metallic, non-metallic Core Iron Hot Spots Insulat
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 841085b2dc953d073069a4fa7f644b02 | 176 |  | Electrical | Field, Stator | DLRO; Winding Resistance | 12 | AC Impedance, Collector Rings, DC Leakage, DLRO, Greasing, High Voltage Bushings, Keybars, MAGIC Inspection, Polarization Index, Stator Winding, Wedges, Winding Resistance | Dave Cathey, Steve Proctor Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • MAGIC robotic inspection • Stator slot RTD resistance measurement and megger 500vDC • Field A; A MAGIC inspection was performed, there was little to no indication of movement on end wedges.; A few spots of minor greasing was also noted on the end windings.; Job Summary • DC resistance measurements were made using a Digital Low Resistance Ohmmeter (DLRO) and resistances were found to be consistent with factory resistance.; A 5000vDC Megger test was conducted for 10 minutes on each isolated phase of the stator winding with the other two phases grounded and Polarization Index calculated. |  | DLRO; Winding Resistance ¦ AC Impedance ¦ Collector Rings ¦ DC Leakage ¦ DLRO ¦ Greasing ¦ High Voltage Bushings | For Lamar Power Partners Generator Serial #: 337X710 Generator Test and Inspect MAGIC Stator Inspection: William Howard Generator Specialist: Dave Cathey, Steve Proctor Job Summary • Scope of inspection • Generator visual inspection as accessible • Field visual inspection as accessible • MAGIC robotic inspection • Stator slot RTD resistance measurement and megger 500vDC • Field AC Impedance, resistance, and 500 vDC megger • Stator resistance, megger/PI 5KvDC • Stator DC Leakage test at 36KvDC Jo
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | b5a0b415f7d99124a42b84eb850b5118 | 2 |  | Electrical | Field, Stator | Polarization Index; DC Leakage | 11 | AC Impedance, Collector Rings, DC Leakage, End-winding, Field Body, Focused Generator Inspection, Loose End-winding Blocking, Polarization Index, Retaining Rings, Wedge Tightness Test, Wedges | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 2 1.4 Work Scope __________ 6 2 Technical __________ 7 2.1 Recommendations __________ 7 3 Turbine | FMI F6291G25 | Polarization Index; DC Leakage ¦ AC Impedance ¦ Collector Rings ¦ DC Leakage ¦ End-winding ¦ Field Body ¦ Focused Generator Inspection ¦ FMI F6291G25 | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 2 1.4 Work Scope __________ 6 2 Technical __________ 7 2.1 Recommendations __________ 7 3 Turbine __________ 9 3.1 FMI F6291G25 - Mechanical Upgrade __________ 9 3.1.1 ML 0509 Fuel Gas Control Valve __________ 9 3.1.2 ML 0705 Turbine Case Arrangement __________ 15 3.1.3 ML 0909 Cooling and Sealing Piping Arrangement - Orifices Replacement Only __________
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | fc9f35960f3430676a46df00793c8d8a | 291 |  | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 11 | Core, DC Hipot, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges | Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic RTD Element Resistance Gas and Winding RTD’s Checks for calibrat |  | Polarization Index; DC Leakage ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings | . This example is meant to demonstrate how generator inspection and maintenance intervals would be synchronized for a gas turbine with the referenced intervals. Steam Turbine Generator Gas Turbine Steam Turbine Generator Gas Turbine GEK103566_L (1) Creating an Effective Generator Maintenance Program GEK 103566L 10 without prior permission of the copyright owner. FIGURE 3 Example of Fossil Coal Steam Turbine Inspection and Maintenance Intervals (24K EOH Inspection Interval) Effective Operating Ho
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | c01d267cd62b59f5b19ca9d9150043cd | 363 |  | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 11 | Core, DC Hipot, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges | Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic RTD Element Resistance Gas and Winding RTD’s Checks for calibrat |  | Polarization Index; DC Leakage ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings | . This example is meant to demonstrate how generator inspection and maintenance intervals would be synchronized for a gas turbine with the referenced intervals. Steam Turbine Generator Gas Turbine Steam Turbine Generator Gas Turbine GEK103566_L (1) Creating an Effective Generator Maintenance Program GEK 103566L 10 without prior permission of the copyright owner. FIGURE 3 Example of Fossil Coal Steam Turbine Inspection and Maintenance Intervals (24K EOH Inspection Interval) Effective Operating Ho
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 8e35ff1e1fc387624e91cbb026c0e137 | 332 |  | Electrical | Hydrogen Seals, Stator | Polarization Index; DC Leakage | 11 | Core, DC Hipot, DC Leakage, End-winding, Focused Generator Inspection, High Voltage Bushings, Hydrogen Seal Assembly, Polarization Index, Stator Winding, Wedge Tightness Test, Wedges | Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic RTD Element Resistance Gas and Winding RTD’s Checks for calibrat |  | Polarization Index; DC Leakage ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ Focused Generator Inspection ¦ High Voltage Bushings | . This example is meant to demonstrate how generator inspection and maintenance intervals would be synchronized for a gas turbine with the referenced intervals. Steam Turbine Generator Gas Turbine Steam Turbine Generator Gas Turbine GEK103566_L (1) Creating an Effective Generator Maintenance Program GEK 103566L 10 without prior permission of the copyright owner. FIGURE 3 Example of Fossil Coal Steam Turbine Inspection and Maintenance Intervals (24K EOH Inspection Interval) Effective Operating Ho
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | d686ca3aca9ca7c260ab5e6e37e1ca4a | 211 |  | Repair | Field, Stator | Red Eye Repair | 9 | Centering Ring, Collector Rings, End-winding, Fan Blades, Field Body, Greasing, Red Eye Repair, Retaining Rings, Wedges | Particle PT Penetrant NA Not Applicable S Satisfactory Z Zyglo INSPECTIONS & CHECKS GENERAL STATOR SLOT PORTION Hardware (bolts, nuts, etc.) VS Between Bar Filler Movement Axially Internal Cleanliness ( Foreign Material) Core iron Condition; Light dusting and greasing were noted on select axial support ties.; It is recommended to perform a through end winding cleaning with denatured alcohol and nylon bristle brushes to clean dusting/greasing and to get a closer look at the ties in question.; Please see "End Winding Inspection" document for exact dusting/greasing locations and further recommendations.; Particle PT - Penetrant NA - Not Applicable S - Satisfactory Z - Zyglo INSPECTIONS & CHECKS ROTATING FIELD Physical Appearance of Visible Overheating at End - Field Forging (Body) VS Wedges & Retaining Rings VS - Retaining Rings VS Physical |  | Red Eye Repair ¦ Centering Ring ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ Field Body ¦ Greasing | . 338X731 Prepared by John Deter CODE X Work Carried Out C See Comments U Unsatisfactory UT Ultrasonic N Not Done V Visual Inspection MP Mag. Particle PT Penetrant NA Not Applicable S Satisfactory Z Zyglo INSPECTIONS & CHECKS GENERAL STATOR SLOT PORTION Hardware (bolts, nuts, etc.) VS Between Bar Filler Movement Axially Internal Cleanliness ( Foreign Material) Core iron Condition VS oil, dust VC Ventilation Ducts Free of Material VS metallic, non-metallic Core Iron Hot Spots Insulator Physical D
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 078b5ff0331e4eaae70934d75ea93082 | 245 |  | Inspection | Field, Stator | MAGIC Inspection | 9 | Amortisseur, Centering Ring, Collector Rings, End-winding, Fan Blades, Field Body, MAGIC Inspection, Retaining Rings, Wedges | Particle PT - Penetrant NA - Not Applicable S - Satisfactory Z - Zyglo INSPECTIONS & CHECKS ROTATING FIELD Physical Appearance of Visible Overheating at End - Field Forging (Body) VS Wedges & Retaining Rings VS - Retaining Rings VS Physical; Grooving, Retaining Rings Burning, and Brush Film VS - Spindle Mounted Verify Correct Radial - Body Mounted X & Axial Position of Brush Rigging - Cylinder Mounted Verify Brush Holders for Wear, - Magnetic Arcing & Burning VS - Non-Magnetic ; Field Body was in satisfactory condition.; The assessible areas of the Retaining Rings (RR) were in satisfactory condition.; Centering Rings, Fan Rings and Blades, see Mechanical Inspection Report. |  | MAGIC Inspection ¦ Amortisseur ¦ Centering Ring ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ Field Body | . 337X767 - GTG2 Prepared by Sherrod Childers CODES X - Work Carried Out C - See Comments U - Unsatisfactory UT - Ultrasonic N - Not Done V - Visual Inspection MP - Mag. Particle PT - Penetrant NA - Not Applicable S - Satisfactory Z - Zyglo INSPECTIONS & CHECKS ROTATING FIELD Physical Appearance of Visible Overheating at End - Field Forging (Body) VS Wedges & Retaining Rings VS - Retaining Rings VS Physical Condition of Rotor Body - Centering Rings VS Wedges VS - Fan Rings VS Ventilation Holes F
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 18dc9ca626654b8f4f6e775d20fea938 | 292 |  | Inspection | Field, Hydrogen Seals, Stator | Oil Deflector Alignment | 9 | Centering Ring, Collector Rings, End-winding, Fan Blades, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Retaining Rings, Wedges | Retaining Rings 2.; Centering Rings 3.; Fan Blades 10.; Body Plugs - staked/secure Retaining Rings Fan Blades Lead Insulation Brush Type Manufacture NCC Grade 634 Brush Holder Constant Pressure 18Mn-18Cr Non-Magnetic Body Mounted Steel Nomex NA NA NA Satisfactory Satisfactory Satisfactory NA NA ; End Wedges - staked/secure 14. |  | Oil Deflector Alignment ¦ Centering Ring ¦ Collector Rings ¦ End-winding ¦ Fan Blades ¦ MAGIC Inspection | The collector ring insulation was inspected for general cleanliness and signs of overheating and degradation. The insulation was in good condition with no signs of degradation. The insulation was cleaned with denatured alcohol and clean rags during this outage. The overall inspection of the Field Collector Assembly was satisfactory. All relevant photos and data sheets of the inspection have been attached to this report. g Field Inspection Date 10/15/2020 Generator Serial No. 337X767-GTG2 Prepare
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 07e73d0873dba1e059640f3218090ee6 | 229 |  | Inspection | Stator | Wedge Tightness Test | 8 | End-winding, Focused Generator Inspection, Greasing, MAGIC Inspection, Step Iron, Wedge Looseness, Wedge Tightness Test, Wedges | The stator wedges were visually inspected for dusting that would indicate movement in the slots during operation.; There were 27 slots on the CE that showed signs of greasing on the ends of the end wedges and between the wedge and step iron and 18 slots on the TE that would indicate wedge or slot support material movement.; Subsequently, the Magic Jr equipment was unable to access the stator end wedges to assess tightness due to the units configuration.; This unit has a total of 1680 wedges.; Out of 1680 wedges only 1531 wedges could be tested due to the flux probe and the unit configuration that impedes the ability of the Magic Jr equipment to test the stator end wedges. |  | Wedge Tightness Test ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Step Iron ¦ Wedge Looseness | The stator wedges were visually inspected for dusting that would indicate movement in the slots during operation. There were 27 slots on the CE that showed signs of greasing on the ends of the end wedges and between the wedge and step iron and 18 slots on the TE that would indicate wedge or slot support material movement. As a result of the Stator Wedge Tightness - Misdiagnosis Using the Wedge Inspection Test System (WITS) during the previous outage, this unit was affected by TIL2091. TIL2091 re
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | aae7386703fddd424af19713883eaec6 | 227 |  | Repair | Stator | Red Eye Repair | 8 | End-winding, Focused Generator Inspection, Greasing, MAGIC Inspection, Red Eye Repair, Stator Winding, Wedge Tightness Test, Wedges | Blocking YES Light and Moderate greasing 2.; Ties YES Light and Moderate greasing 3.; Binding band / supports YES Light greasing 8.; Inner axials (gun stocks) YES Light greasing and dusting 10.; %Loose YES 99% of wedges tested were Tight %Hollow 1% Comments: | GEK103566 | Red Eye Repair ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Stator Winding ¦ GEK103566 | Continue to inspect the stator air gap components on a regularly scheduled maintenance program. Reference GEK103566 for guidance developing an effective maintenance plan. g Stator Inspections Date(m/d/y) 10/13/2020 Generator Serial No. 337X768 Prepared by Sherrod Childers Manufacture: GE Turbine Serial No. 297623 Customer: Dynergy WPP Field Serial No. FSR No. 10330252 Sketch No. A. FRAME & FRAME EXTENSION Satisfactory Remarks 1. Internal Cleanliness (oil, dust) YES Minor oil film along the surfa
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | c0fb1167062ae27b76fbd650e37fae30 | 255 |  | Inspection | Field, Hydrogen Seals, Stator | MAGIC Inspection | 8 | End Shield, End-winding, MAGIC Inspection, Main Lead, Pole Jumper, Retaining Rings, Sub-slots, Turn Insulation Migration | Each coil stack was inspected for elongation, distortion, signs of overheating, and turn-to- turn insulation migration.; The overall inspection of the field end winding regions underneath the CE/TE retaining rings was satisfactory.; See the report appendix section for the attached Magic Photo ID Sheet and the corresponding Photo Layout that shows all relevant photos taken of the major components within the CE/TE Field End Winding Region during the Magic Inspection.; Continue to inspect for abnormal or unsatisfactory conditions of the major components within both the CE/TE Field End Winding Regions underneath the field retaining rings when access is available.; Inspections can be performed either when the end shields are removed or through the end shield inspection portals. |  | MAGIC Inspection ¦ End Shield ¦ End-winding ¦ Main Lead ¦ Pole Jumper ¦ Retaining Rings | The field sub slots were inspected obstruction from foreign material that could impact proper cooling. All of the sub slots were free from obstruction. Coil Stacks: Each coil stack was inspected for elongation, distortion, signs of overheating, and turn-to- turn insulation migration. Overall, the coil stacks look to be in satisfactory condition. The overall inspection of the field end winding regions underneath the CE/TE retaining rings was satisfactory. See the report appendix section for the a
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | fdf42cb41d7d8aae881974f72f71accf | 120 |  | Inspection | Field, Stator | Stator Findings Review | 7 | Belly Bands, Collector Rings, End-winding, Greasing, High Voltage Bushings, Keybars, Retaining Rings | Generator U21 Test And Inspect Report 11_2_20 REV1 The end winding basket ties were found to be in good condition with minimal greasing.; Generator U21 Test And Inspect Report 11_2_20 REV1 Tig welded and surface coated Generator U21 Test And Inspect Report 11_2_20 REV1 Collector rings were found in good condition with even wear indicating even distribution of footprint.; Generator U21 Test And Inspect Report 11_2_20 REV1 Generator U21 Test And Inspect Report 11_2_20 REV1 The belly bands were inspected and gaps measured prior to loosening. |  | Stator Findings Review ¦ Belly Bands ¦ Collector Rings ¦ End-winding ¦ Greasing ¦ High Voltage Bushings ¦ Keybars | . All other hardware visually accessible was found to be intact without movement. Generator U21 Test And Inspect Report 11_2_20 REV1 No visible evidence of movement on binding band ties. Generator U21 Test And Inspect Report 11_2_20 REV1 The end winding basket ties were found to be in good condition with minimal greasing. Generator U21 Test And Inspect Report 11_2_20 REV1 Generator U21 Test And Inspect Report 11_2_20 REV1 Heavy oil accumulation was noted throughout the end windings Generator U21
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 3d5f9b53c57ce7da314a30493ca78139 | 147 |  | Inspection | Field, Stator | Stator Findings Review | 7 | Greasing, High Voltage Bushings, Main Lead, Pole Jumper, Step Iron, Sub-slots, Wedges | (518) 385‐3178 Generator Specialist Steve Proctor Slot 22 View of dripping oil/greasing on packages ~22” from CE RR Image 42 Slots 19 - 16 View of greasing on CE step iron Image 43 Slot 20 View of foreign material in vent slot ~34” from CE |  | Stator Findings Review ¦ Greasing ¦ High Voltage Bushings ¦ Main Lead ¦ Pole Jumper ¦ Step Iron ¦ Sub-slots | . 55 Rm. 263 Generator # 337X711 Schenectady, New York 12345 Date 10‐28‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W. Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor Slot 22 View of dripping oil/greasing on packages ~22” from CE RR Image 42 Slots 19 - 16 View of greasing on CE step iron Image 43 Slot 20 View of foreign material in vent slot ~34” from CE RR Image 44 Slot 13 View of greasing on packages and wedges ~19” from CE RR Image 45 Slot 13 View of greasing on CE step iro
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | e232a5e20362d3a915ae4a7ce493023f | 2 |  | Electrical | Field, Hydrogen Seals, Stator | Polarization Index; DC Leakage | 7 | DC Leakage, End-winding, Fan Blades, High Voltage Bushings, Hydrogen Seal Assembly, MAGIC Inspection, Polarization Index | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 3 1.4 Work Scope __________ 4 1.5 EHS __________ 5 1.6 Quality __________ 5 2 Technical _________ |  | Polarization Index; DC Leakage ¦ DC Leakage ¦ End-winding ¦ Fan Blades ¦ High Voltage Bushings ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 3 1.4 Work Scope __________ 4 1.5 EHS __________ 5 1.6 Quality __________ 5 2 Technical __________ 6 2.1 Recommendations __________ 6 3 Turbine __________ 11 3.1 Auxiliaries __________ 11 3.1.1 Piping and Flexible Metal Hoses __________ 11 3.2 Inlet Section __________ 15 3.2.1 Thrust Bearing __________ 15 3.2.2 Inlet Bellmouth __________ 16 3.2.3 Inlet Gu
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | bc31911933340baa19e9ba457459b0e6 | 294 |  | Electrical | Stator | DC Leakage; DC Hipot | 7 | Core, DC Hipot, DC Leakage, End-winding, High Voltage Bushings, Stator Winding, Wedges | Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Dynamic Frequency response Stator End Winding Potentially damagi; O – Optional 1 This test does not apply to units with asphalt stator windings or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds.; 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 7 DC Leakage and Partial Discharge testing are optional but highly recommended for setting baselines for trending. |  | DC Leakage; DC Hipot ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ High Voltage Bushings ¦ Stator Winding | . Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Dynamic Frequency response Stator End Winding Potentially damaging resonance X X X O Core Ring Test Stator Core Insulation Weak or damaged core enamel X X X O Tan Delta Stator Winding Stator insulation degradation X X X O AC Hipot2 Stator Winding Ground wall insulation integrity X X X O Air – Air Cooled Generator HYD – H
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | a035fb5d7af30f2bb2728cd35c770d1b | 268 |  | Repair | Stator | Red Eye Repair | 7 | End-winding, Focused Generator Inspection, Greasing, MAGIC Inspection, Red Eye Repair, Wedge Tightness Test, Wedges | Binding band / supports YES Light greasing 8.; Inner axials (gun stocks) YES Light to Moderate greasing and dusting 10.; %Loose YES 99% of wedges tested were Tight %Hollow Comments:; Greasing/Dusting severity between Light, and Heavy was observed within CR Block and Tie assemblies "A", "B" ,"C" , "E", "J", "N", "O", "P", "Q", "R" and within axial support ties #1, #6, and #10.; The CR Block and Tie assemblies identified with LIGHT greasings did not show any signs of loose ties therefore each location can be cleaned and coated with the recommended epoxy application to migate further movement. |  | Red Eye Repair ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Wedge Tightness Test | . Nose ring N/A 6. Tee bolts (torque) N/A 7. Binding band / supports YES Light greasing 8. Outer axial support asm. N/A 9. Inner axials (gun stocks) YES Light to Moderate greasing and dusting 10. Core compression nuts/washers YES 11. Asphalt bleeding N/A 12. End winding support hardware YES 13. R.T.D. and T.C. wiring hardware N/A 14. Fan baffle support studs N/A C. CORE & SLOTS Satisfactory Remarks 1. Bar borescope examination N/A Field in place 2. Bars bottomed in slot YES As viewed by borescop
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 440c94a0a0565648ae601d7a59867ab8 | 288 |  | Inspection | Field, Hydrogen Seals, Stator | MAGIC Inspection | 7 | End Shield, End-winding, MAGIC Inspection, Main Lead, Retaining Rings, Sub-slots, Turn Insulation Migration | Each coil stack was inspected for elongation, distortion, signs of overheating, and turn-to- turn insulation migration.; The overall inspection of the field end winding regions underneath the CE/TE retaining rings was satisfactory.; See the report appendix section for the attached Magic Photo ID Sheet and the corresponding Photo Layout that shows all relevant photos taken of the major components within the CE/TE Field End Winding Region during the Magic Inspection.; Continue to inspect for abnormal or unsatisfactory conditions of the major components within both the CE/TE Field End Winding Regions underneath the field retaining rings when access is available.; Inspections can be performed either when the end shields are removed or through the end shield inspection portals. |  | MAGIC Inspection ¦ End Shield ¦ End-winding ¦ Main Lead ¦ Retaining Rings ¦ Sub-slots | leafs, and overheating. Both leads were found in good condition. Pole-to-Pole Jumpers: Each jumper was inspected for overheating, breaks, cracks and proper brazing. All jumpers were in satisfactory condition. Coil Jumpers: Each coil jumper was inspected for overheating, breaks, cracks and proper brazing. All jumpers were in satisfactory condition. Sub Slots: The field sub slots were inspected obstruction from foreign material that could impact proper cooling. All of the sub slots were free from
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 009a2dbae3c011f3859fea444e793eb8 | 243 |  | Repair | Stator | Red Eye Repair | 7 | End-winding, Focused Generator Inspection, Greasing, MAGIC Inspection, Red Eye Repair, Wedge Tightness Test, Wedges | Particle PT Penetrant NA Not Applicable S Satisfactory Z Zyglo INSPECTIONS & CHECKS GENERAL STATOR SLOT PORTION Hardware (bolts, nuts, etc.) VS Between Bar Filler Movement Axially Internal Cleanliness ( Foreign Material) Core iron Condition; Greasing/Dusting severity between Light, and Heavy was observed within CR Block and Tie assemblies "A", "B" ,"C" , "E", "J", "N", "O", "P", "Q", "R" and within axial support ties #1, #6, and #10.; The CR Block and Tie assemblies identified with LIGHT greasings did not show any signs of loose ties therefore each location can be cleaned and coated with the recommended epoxy application to migate further movement.; Additionally, the entire CE end winding should be cleaned with denatured alcohol, and all minor greasing locations identified should be coated with Red Eye Epoxy (A50A607), Flood Resin (A50A262) & Epoxy Paint (A50A535B).; SEE END WINDING DUSTING DATA SHEET D316224 FOR DUSTING AND GREASING LOCATIONS. | GEK 103566 | Red Eye Repair ¦ End-winding ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Wedge Tightness Test ¦ GEK 103566 | GE publication GEK 103566: "Creating An Effective Maintenance Program", is available from the local GE office and has been attached to the appendix section of this report. This publication provides a detailed discussion of GE's recommendations for inspecting and testing generators and should be referenced by the customer when planning for future generator outages and inspections. g Stator Inspection Checklist Date:(m,d,y) 10/15/2020 Serial No. 337X767 - GTG2 Prepared by Sherrod Childers CODE X W
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | af10a0d60de3e3fa4c0c028faf47074e | 366 |  | Electrical | Stator | DC Leakage; DC Hipot | 7 | Core, DC Hipot, DC Leakage, End-winding, High Voltage Bushings, Stator Winding, Wedges | Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Dynamic Frequency response Stator End Winding Potentially damagi; O – Optional 1 This test does not apply to units with asphalt stator windings or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds.; 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 7 DC Leakage and Partial Discharge testing are optional but highly recommended for setting baselines for trending. |  | DC Leakage; DC Hipot ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ High Voltage Bushings ¦ Stator Winding | . Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Dynamic Frequency response Stator End Winding Potentially damaging resonance X X X O Core Ring Test Stator Core Insulation Weak or damaged core enamel X X X O Tan Delta Stator Winding Stator insulation degradation X X X O AC Hipot2 Stator Winding Ground wall insulation integrity X X X O Air – Air Cooled Generator HYD – H
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 9a90bdc5daf16ad0704427f4cf4c496d | 335 |  | Electrical | Stator | DC Leakage; DC Hipot | 7 | Core, DC Hipot, DC Leakage, End-winding, High Voltage Bushings, Stator Winding, Wedges | Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Dynamic Frequency response Stator End Winding Potentially damagi; O – Optional 1 This test does not apply to units with asphalt stator windings or units with the “camelback” wedge system.; DC Hipot may be used at customer’s discretion during stator rewinds.; 3 Consider replacement of high voltage bushings around 30 years of age and minimize removal/reinstallation to prevent wear that could increase hydrogen leakage on hydrogen cooled generators.; 7 DC Leakage and Partial Discharge testing are optional but highly recommended for setting baselines for trending. |  | DC Leakage; DC Hipot ¦ Core ¦ DC Hipot ¦ DC Leakage ¦ End-winding ¦ High Voltage Bushings ¦ Stator Winding | . Table 3 Recommended Stator Tests and Inspections Stator and Core AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment First Inspection Borescope Robotic Dynamic Frequency response Stator End Winding Potentially damaging resonance X X X O Core Ring Test Stator Core Insulation Weak or damaged core enamel X X X O Tan Delta Stator Winding Stator insulation degradation X X X O AC Hipot2 Stator Winding Ground wall insulation integrity X X X O Air – Air Cooled Generator HYD – H
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | ad45b7d73c582d17b199496480f7181b | 229 |  | Inspection | Field, Stator | Wedge Tightness Test | 7 | Amortisseur, Field Body, Focused Generator Inspection, Greasing, MAGIC Inspection, Wedge Tightness Test, Wedges | Additionally, and at a minimum, a 10% borescope inspection of the stator bars within the slot end ventilation passages should be performed to inspect for bar abrasion caused by potential SRS movement and to confirm that the bars are properl; Continue to inspect the axial alignment of the field body wedges, slot amortisseur, and creepage blocks when the field is removed or via remote means i.e., [MAGIC Insitu (Robotics) or borescope). |  | Wedge Tightness Test ¦ Amortisseur ¦ Field Body ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection | It is recommended that the generator field be removed during the next scheduled major outage so that the stator end wedge tightness can be physically assessed by hand and by using a small 2oz ball peen hammer. Additionally, and at a minimum, a 10% borescope inspection of the stator bars within the slot end ventilation passages should be performed to inspect for bar abrasion caused by potential SRS movement and to confirm that the bars are properly bottomed in the slots where greasing is occurrin
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | 9673ac6a6f20e3f354bb2c47dac0fe27 | 5 |  | Inspection | Hydrogen Seals | Generator Pressure Test; Oil Deflector Alignment | 6 | End Shield, Generator Pressure Test, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | The Generator Collector End Shield was removed and a MAGIC inspection was performed. |  | Generator Pressure Test; Oil Deflector Alignment ¦ End Shield ¦ Generator Pressure Test ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflector Alignment ¦ Oil Deflectors | . All of the shims that were less than 0.040” were removed and the unit was shimmed and the blades were machined to get the drops within specs. The shims that were installed were not pinned by request of the customer. The Combustion Section was disassembled and the coatings were examined for damage. There was not any extensive chipping, burning, or darkening of the coatings in the liners or TPs. The Fuel Nozzles had some deposits on the tips, but not any extensive damage or wear. The Fuel Nozzle
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | d8a9ac0fb2472bf8e0245a4e141e8e42 | 219 |  | Inspection | Field, Hydrogen Seals | Wedge Tightness Test; Generator Pressure Test | 6 | Fan Blades, Generator Pressure Test, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | outer oil deflector, upper half bearing cap, T4 bearing, upper out end-shield, H2 seal cage, H2 seal, upper half field fan blades, upper half inner air-shield, and inner oil deflector.; · All oil deflectors were cleaned and visually inspected.; All oil deflectors were returned to service · Upper half inner air-shield was removed and visually inspected.; · Upper half generator field fan blades were removed, cleaned, and visually inspected.; All removed fan blades were reassembled with new lock tab. |  | Wedge Tightness Test; Generator Pressure Test ¦ Fan Blades ¦ Generator Pressure Test ¦ MAGIC Inspection ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | Part Condition: Fair Part Description: Generator underwent MAGIC Jr. inspection and electrical test. The following components on collector end were disassembled to facilitate for this inspection and testing: outer oil deflector, upper half bearing cap, T4 bearing, upper out end-shield, H2 seal cage, H2 seal, upper half field fan blades, upper half inner air-shield, and inner oil deflector. The following components on turbine end were disassembled to facilitate a bearing inspection: upper half ou
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | b2433eabf3f6b52c34edcf91e42fa200 | 170 |  | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 6 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA NA NA NA NA Fan Blade J Inner Oil Deflector K 16.022 16.033 16.022 | EM3404 | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings ¦ EM3404 | lapping seal contact checks CE dissasembly new seals new seals g Hydrogen Seal Casing Date 11/2/2020 Generator Serial No. 337X310 Prepared by GE Opening INSPECTIONS & CHECKS CODE Cleaned Joints X X X Work Carried Out Dowels X N Not Done Assembly per NA Not Applicable EM3404 X C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant "A' GAP DIMENSIONS LOCATION PINS IN PINS OUT Top Left 1.624 N/A Top 1.623 N/A Top Right 1.624 N/A Bottom Left 1.625 N/A Bottom 1.625 N/A Bottom
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 3315999ec6736c05d64b98f1dc3d363e | 196 |  | Inspection | Field, Stator | Stator Findings Review | 6 | Greasing, High Voltage Bushings, Main Lead, Pole Jumper, Step Iron, Sub-slots | (518) 385‐3178 Generator Specialist Steve Proctor Slots 40 - 37 View of light red dusting on packages ~52” from CE RR Image 43 Slots 40 - 41 View of light dusting on packages ~98” from CE RR Image 44 204 Deg Scratches on field ~147” from CE |  | Stator Findings Review ¦ Greasing ¦ High Voltage Bushings ¦ Main Lead ¦ Pole Jumper ¦ Step Iron ¦ Sub-slots | . Overall the unit is in good condition. g GE Power Inspection & Life Extension Services Photo I.D.Worksheet Job # 10326236 1 River Road, Bldg. 55 Rm. 263 Generator # 337X710 Schenectady, New York 12345 Date 11‐03‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W.Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor Slots 40 - 37 View of light red dusting on packages ~52” from CE RR Image 43 Slots 40 - 41 View of light dusting on packages ~98” from CE RR Image 44 204 Deg Scratches on fi
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 0683122a5223f801f1013118fe29fe44 | 13 |  | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 6 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Cold Coupling Postion Z Shaft Grounding Brushes A Outer Oil Deflector B 0.008 0.008 0.007 0 |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | Generator - H2 Case Megger CE g Hydrogen Seals Equip Code: Air and Gas Side Date(m/d/y) Turbine Serial No. Prepared by Generator Serial No. Data set Units recorded in Seal Type / System Type / No. of Poles Nominal Shaft Dia. (in.) GE Part No. H2 SEAL ID MEASUREMENTS (NEAREST .001 in.) TURBINE END COLL. END POSITION AIR HYD AIR HYD 1 16.013 16.005 2 16.014 16.006 3 16.013 16.007 4 16.013 16.008 5 16.013 16.009 6 16.013 16.007 AVERAGE 16.013 16.007 SHAFT DIA. CLEARANCE 0.013 0.007 H2 SEAL SPRING M
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | 5340180727f55c094d092e9336a353ac | 208 |  | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 6 | End Shield, End-winding, Greasing, MAGIC Inspection, Red Eye Repair, Retaining Rings | The upper, outer/inner gas shields were removed from the Collector End (CE) as well as the lower inner end shield to facilitate the magic and the borescope inspection.; The specific areas inspected were the generator air- gap region, the CE stator end-winding region, the accessible areas of the generator field and the region underneath the CE retaining rings.; Light dusting and greasing were observed within the stator CE end winding support system within the stator.; All ties exhibiting dusting or greasing were examined for physical movement and for the possibilities of damaging the insulation beneath them.; Red Eye Epoxy and Flooding Resin were applied to all locations exhibiting greasing/ dusting within the End Winding Support System to help mitigate further movement and risk of failure during operation. |  | Red Eye Repair ¦ End Shield ¦ End-winding ¦ Greasing ¦ MAGIC Inspection ¦ Retaining Rings | Implementing a thorough maintenance program is the most effective way to retain generator reliability and avoid major failure expenses. However, it must be cost effective in that there are demonstrated savings in improved availability & reliability to offset the cost of implementing the program. The three important elements of a thorough program are maintenance frequency, electrical testing, and visual inspection. Generator electrical testing is focused on the integrity of insulation systems. Ch
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | 7de0741867e253c65204060acd7a8394 | 288 |  | Electrical | Stator | DC Leakage | 6 | Core, DC Leakage, Focused Generator Inspection, Stator Winding, Wedge Looseness, Wedges | Maintenance Planning Rotor tooth and wedge inspection and repair to remove hardened material Rotor vibration trends coupled with flux probe shorted turns or blocked ventilation passages Rings off cleaning up to field rewind Stator wedge loo; As the stator core is exposed during a rewind, a detailed inspection of the core is recommended including at minimum a visual inspection, EL-CID and core tightness testing.; However, this is also an opportune time to perform a core ring test and retighten of core compression features if applicable |  | DC Leakage ¦ Core ¦ Focused Generator Inspection ¦ Stator Winding ¦ Wedge Looseness ¦ Wedges | . Inspection intervals are based on the age of the stator. For those units not accessible by a robot, more frequent Borescope Inspections, pulling the rotor, use of monitoring or some combination of these options should be used. In such a case, contact your local GE service representative for assistance in optimization of inspection and maintenance intervals and scope. While following maintenance and inspection intervals define within this GEK, conditions may dictate that a future outage will re
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | ab986dbe80a59a5ab879d3795bc64052 | 243 |  | Inspection | Field, Stator | MAGIC Inspection | 6 | End-winding, MAGIC Inspection, Main Lead, Retaining Rings, Sub-slots, Turn Insulation Migration | The main leads or goosenecks, at 0 and 180 degrees, were inspected for looseness, broken leaves, and overheating.; Each coil stack was inspected for elongation, distortion, signs of overheating, and turn-to- turn insulation migration.; The overall inspection of the field end winding regions underneath the CE retaining rings was satisfactory.; See the report appendix section for the attached Magic Photo ID Sheet and the corresponding Photo Layout that shows all relevant photos taken of the major components within the CE Field End Winding Region during the Magic Inspection.; Collector End Main Lead Hardware @ 0 Deg. |  | MAGIC Inspection ¦ End-winding ¦ Main Lead ¦ Retaining Rings ¦ Sub-slots ¦ Turn Insulation Migration | The main leads or goosenecks, at 0 and 180 degrees, were inspected for looseness, broken leaves, and overheating. Both leads were found in good condition. Pole-to-Pole Jumpers: Each jumper was inspected for overheating, breaks, cracks and proper brazing. All jumpers were in satisfactory condition. Coil Jumpers: Each coil jumper was inspected for overheating, breaks, cracks and proper brazing. The overall condition of the jumpers was satisfactory. Sub Slots: The field sub slots were inspected obs
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | 7fab463cbb3d02e507fedc15d929d440 | 297 |  | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically designed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . 4 . Testing Generator electrical testing is focused on the insulation systems. There are other tests used to monitor for degradation in other components. A list of the typical tests recommended and the test purpose is shown in Tables 3, 4, and 5. Historical records of test results should be maintained and compared to the new test results. Changes between outage test results may point to needed repairs that may not be evident from the absolute test values themselves. Many of the tests require s
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 7cc9fe4b25818515f8e92080a3b6546e | 360 |  | Electrical | Stator | DC Leakage | 6 | Core, DC Leakage, Focused Generator Inspection, Stator Winding, Wedge Looseness, Wedges | Maintenance Planning Rotor tooth and wedge inspection and repair to remove hardened material Rotor vibration trends coupled with flux probe shorted turns or blocked ventilation passages Rings off cleaning up to field rewind Stator wedge loo; As the stator core is exposed during a rewind, a detailed inspection of the core is recommended including at minimum a visual inspection, EL-CID and core tightness testing.; However, this is also an opportune time to perform a core ring test and retighten of core compression features if applicable |  | DC Leakage ¦ Core ¦ Focused Generator Inspection ¦ Stator Winding ¦ Wedge Looseness ¦ Wedges | . Inspection intervals are based on the age of the stator. For those units not accessible by a robot, more frequent Borescope Inspections, pulling the rotor, use of monitoring or some combination of these options should be used. In such a case, contact your local GE service representative for assistance in optimization of inspection and maintenance intervals and scope. While following maintenance and inspection intervals define within this GEK, conditions may dictate that a future outage will re
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 2efd12945203bf9eec7ba9945de88ca1 | 369 |  | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically designed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . 4 . Testing Generator electrical testing is focused on the insulation systems. There are other tests used to monitor for degradation in other components. A list of the typical tests recommended and the test purpose is shown in Tables 3, 4, and 5. Historical records of test results should be maintained and compared to the new test results. Changes between outage test results may point to needed repairs that may not be evident from the absolute test values themselves. Many of the tests require s
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 30fb0ae59ca185c1b0255ab443d319ae | 246 |  | Inspection | Stator | Wedge Tightness Test | 6 | Focused Generator Inspection, Greasing, MAGIC Inspection, Step Iron, Wedge Tightness Test, Wedges | The stator wedges were visually inspected for dusting or greasing that would indicate movement in the slot during operation.; There was an indication of minor greasing visible on a small number of End wedges on both the TE and CE.; The greasing seen was between the end wedges and Core Step Iron packages.; Greasing on this area indicates a movement of components inside the slot, which includes the bar, side/top ripple springs, fillers, and the wedges.; This unit has a total of 1680 wedges. |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Step Iron ¦ Wedges | The stator wedges were visually inspected for dusting or greasing that would indicate movement in the slot during operation. There was an indication of minor greasing visible on a small number of End wedges on both the TE and CE. The greasing seen was between the end wedges and Core Step Iron packages. Greasing on this area indicates a movement of components inside the slot, which includes the bar, side/top ripple springs, fillers, and the wedges. A color-coded wedge map is created from the curv
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | c008c08bfb225edaddd77ca9a8fd8ac9 | 241 |  | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 6 | End Shield, End-winding, Greasing, MAGIC Inspection, Red Eye Repair, Retaining Rings | The upper, outer/inner gas shields were removed from the Collector End (CE) as well as the lower inner end shield to facilitate the magic and the borescope inspection.; The specific areas inspected were the generator air- gap region, the CE stator end-winding region, the accessible areas of the generator field and the region underneath the CE retaining rings.; Red Eye Epoxy and Flooding Resin was applied to all locations exhibiting greasing/dusting within the End Winding Support System to help mitigate further movement and risk of failure during operation. |  | Red Eye Repair ¦ End Shield ¦ End-winding ¦ Greasing ¦ MAGIC Inspection ¦ Retaining Rings | Implementing a thorough maintenance program is the most effective way to retain generator reliability and avoid major failure expenses. However, it must be cost effective in that there are demonstrated savings in improved availability & reliability to offset the cost of implementing the program. The three important elements of a thorough program are maintenance frequency, electrical testing and visual inspection. Generator electrical testing is focused on the integrity of insulation systems. Cha
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 7d1ce4409a544dfa3bdb5d2a1800f779 | 284 |  | Inspection | Field, Stator | Stator Findings Review | 6 | Gooseneck, Greasing, Main Lead, Step Iron, Sub-slots, Wedges | (518) 385-3178 Generator Specialist Sherrod Childers Slot 40 View of damage on wedge ~ 145” from CE RR Image 44 Slot 39 View of greasing on end wedge/package at TE RR Image 45 Slot 37 View of damage on wedge ~ 120” from CE RR Image 46 Slot |  | Stator Findings Review ¦ Gooseneck ¦ Greasing ¦ Main Lead ¦ Step Iron ¦ Sub-slots ¦ Wedges | See content below. g GE Power Inspection & Life Extension Services Photo I.D.Worksheet Job # 10330252 1 River Road, Bldg. 55 Rm. 263 Generator # 337X768 Schenectady, New York 12345 Date 10-18-2020 Office: (518) 385-1751, 8*235-1751 Operator W. Howard / J. Kopetchny Fax: (518) 385-3178 Generator Specialist Sherrod Childers Slot 40 View of damage on wedge ~ 145” from CE RR Image 44 Slot 39 View of greasing on end wedge/package at TE RR Image 45 Slot 37 View of damage on wedge ~ 120” from CE RR Ima
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | ea871f4c9fea146a31cd330577eef767 | 338 |  | Inspection | Field, Stator | Wedge Tightness Test | 6 | Core, Focused Generator Inspection, MAGIC Inspection, Retaining Rings, Wedge Tightness Test, Wedges | Rotor In-Situ Inspection via Robotics GE’s robots provide a thorough visual inspection of the stator core and windings and rotor body using the robot’s on-board high-resolution video cameras.; Additionally, robots can provide quantitative wedge tightness and Electromagnetic Core Imperfection Detection (ELCID) assessments.; Rotor Life Management Modern generator rotor forging and retaining rings are typically designed for normal transient events including 10,000 start/stop cycles. |  | Wedge Tightness Test ¦ Core ¦ Focused Generator Inspection ¦ MAGIC Inspection ¦ Retaining Rings ¦ Wedges | . 4 . Testing Generator electrical testing is focused on the insulation systems. There are other tests used to monitor for degradation in other components. A list of the typical tests recommended and the test purpose is shown in Tables 3, 4, and 5. Historical records of test results should be maintained and compared to the new test results. Changes between outage test results may point to needed repairs that may not be evident from the absolute test values themselves. Many of the tests require s
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | eae911fae755120d45bc5849b7fe44a4 | 329 |  | Electrical | Stator | DC Leakage | 6 | Core, DC Leakage, Focused Generator Inspection, Stator Winding, Wedge Looseness, Wedges | Maintenance Planning Rotor tooth and wedge inspection and repair to remove hardened material Rotor vibration trends coupled with flux probe shorted turns or blocked ventilation passages Rings off cleaning up to field rewind Stator wedge loo; As the stator core is exposed during a rewind, a detailed inspection of the core is recommended including at minimum a visual inspection, EL-CID and core tightness testing.; However, this is also an opportune time to perform a core ring test and retighten of core compression features if applicable |  | DC Leakage ¦ Core ¦ Focused Generator Inspection ¦ Stator Winding ¦ Wedge Looseness ¦ Wedges | . Inspection intervals are based on the age of the stator. For those units not accessible by a robot, more frequent Borescope Inspections, pulling the rotor, use of monitoring or some combination of these options should be used. In such a case, contact your local GE service representative for assistance in optimization of inspection and maintenance intervals and scope. While following maintenance and inspection intervals define within this GEK, conditions may dictate that a future outage will re
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | bcce5b85b1cc3e79ba8f281be20f7dcf | 2 |  | Electrical | Field, Stator | Polarization Index; DC Leakage | 6 | DC Leakage, End-winding, Fan Blades, MAGIC Inspection, Polarization Index, Wedges | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Work Scope __________ 3 1.4 EHS __________ 3 1.5 Quality __________ 3 2 Technical __________ 4 2.1 Recommendations __________ |  | Polarization Index; DC Leakage ¦ DC Leakage ¦ End-winding ¦ Fan Blades ¦ MAGIC Inspection ¦ Polarization Index ¦ Wedges | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Work Scope __________ 3 1.4 EHS __________ 3 1.5 Quality __________ 3 2 Technical __________ 4 2.1 Recommendations __________ 4 3 Turbine __________ 5 3.1 Auxiliaries __________ 6 3.1.1 Piping and Flexible Metal Hoses __________ 6 3.2 Inlet Section __________ 14 3.2.1 Thrust Bearing __________ 14 3.2.2 Inlet Bellmouth __________ 16 3.2.3 Inlet Guides Vanes __________ 18 3.3 Compresso
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | 3993d7789129b378ca0f633d78d26fcf | 224 |  | Inspection | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Fan Blades, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | LENGTH ST00066 Cooler Assembly;Hydrogen Coolers When the Generator End Shield was removed, there was oil found in the cooler bays.; Oil Cooler Bay Oil Cooler Bay GENERATOR STATOR Oil Cooler Bay Oil Cooler Bay GENERATOR STATOR Oil Cooler Bay Oil Cooler Bay GENERATOR STATOR Oil Cooler Bay Generator Closeout GENERATOR STATOR Generator Closeout Generator Closeout GENERATOR ; The end shields did not show any signs of damage or show any indications that would cause a leak.; The fan blades were also removed for the MAGIC inspection.; The bolting and the lock plates on the fan blades were replaced and the blades were reinstalled with .120” clearance with the shroud. |  | Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ MAGIC Inspection ¦ Oil Deflectors | . Seal Oil Flow G.P.M. b. Hydrogen Pressure P.S.I. c. Unit Speed R.P.M. 337X152 SHAMSI English - inches Scavenging 1 2 3 4 5 6 COIL DIA. WIRE DIA. LENGTH ST00066 Cooler Assembly;Hydrogen Coolers When the Generator End Shield was removed, there was oil found in the cooler bays. The outer and middle coolers were removed and all the oil that had pooled in the bottom of the generator was removed and the coolers were cleaned off. The upper access manway showed signs of leaking, it was removed, cleane
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | cc5cf053929abae421f61a761e41111c | 14 |  | Inspection | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Fan Blades, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | · Disassembled, visually inspected, cleaned, and reinstalled CE components (outer oil deflector, UH end-shield, H2 seal and cage, UH field fan blades, and UH inner air-shield) as per outage work scope.; · Lift oil lines were removed and replaced on both T3 and T4 bearings, lift check conducted for both bearings · A magic inspection consists of a full visual inspection of the generator stator and field components and a complete set of elect; The magic inspection had been conducted from CE only as the TE End shield was not removed during this outage CONTROLS: | ER-20200407-0368, ER-20200413-0376, ER-20200429-0594, FMI F6291G25 | Oil Deflector Alignment ¦ End Shield ¦ Fan Blades ¦ MAGIC Inspection ¦ Oil Deflectors ¦ ER-20200407-0368 ¦ ER-20200413-0376 | with new flexible metal hoses as per FMI F6291G25 Fuel Gas System: · All fuel gas valves (SRV, PM1, PM2, and Quaternary) were removed, send off to Moog for overhaul as per outage work scope · PM3 fuel gas valve was removed and replaced with new valve as per FMI F6291G25 Alignment – Turbine and Compressor Clearances: · Conducted 16-point turbine to generator alignment check as per GE specification drawing 334A1553; no turbine to generator alignment correction was required. · Conducted opening and
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 114eba0a041201de974ff1c7dae55227 | 217 |  | Electrical |  | DLRO; Winding Resistance | 5 | 10-minute 5000 VDC Megger PI, 10-minute Megger, DLRO, Polarization Index, Winding Resistance | 1 - Field Winding Resistance Test 2 - Field Winding AC-Impedance Test 3 - Field Winding 10-Minute Megger & Polarization Index (PI) The field tests results were satisfactory.; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.35 1.70 6.09 20.21 3.34 6.05 30.14 4.95 6.09 40.09 6.54 6.13 49.93 8.06 6.19 60.26 9.58 6.29 69.95 11.00 6.36 79.99 12.37 6.47 90.20 13.70 6.58 100.00 14.92 6.70 107.61 15.83 6.80 INSULA; CAL Date 2250822 07/22/2020 2260824 07/22/2020 Date NA Turning Gear Hrs Check per TM4010 8 Point Resistance Check (Optional - Except for 390H and certain 450H & 9A5 units) - TM4010 and TM4030 Factory @25 ºC megger dlro Instrument Descriptio | TM4010, TM4020, TM4030 | DLRO; Winding Resistance ¦ 10-minute 5000 VDC Megger PI ¦ 10-minute Megger ¦ DLRO ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | Part Condition: Good Part Description: 1 - Field Winding Resistance Test 2 - Field Winding AC-Impedance Test 3 - Field Winding 10-Minute Megger & Polarization Index (PI) The field tests results were satisfactory. Field Measurements Date Turbine No.: 297493 Prepared by: Equipment Generator No.: 337X155 Project ID: OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.35 1.70 6.09 20.21 3.34 6.05 30.14 4.95 6.09 40.09 6.54 6.13 49.93 8.06 6.19 60.26 9.58 6.29 69.95 11.00 6.36 79.99 12.37 6.47 90.2
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 13c1072bca7bf51636b3e919cefd8d3c | 7 |  | Inspection | Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | The planned maintenance activities on the unit consisted of a Hot Gas Path Inspection on the gas turbine, MAGIC inspection on the generator, removing the CDC to replace the S17s, & replacing exhaust flex seal.; TASK COMPLETED Disassembly · Unwired and removed instrumentation (Customer) · Removed turbine compartment roof piping and roofs (forward and AFT) · Performed rotor position checks · Removed fuel gas piping · Removed fuel nozzle endcovers an; Replaced damaged ones · Visually inspected roofs and enclosure panels · Golden Brush cleaned, prepped and painted inlet bellmouth (closeout with customer) · Cleaned and inspected Collector end generator parts (hydrogen seals, oil deflectors; · Cleaned, visually inspected collector end generator outer oil deflectors · Removed, cleaned and visually inspected collector end generator inner oil deflector. |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | This report details the maintenance activities conducted on unit GT-22, S/N 297257/337X710, in Paris, Texas. The planned maintenance activities on the unit consisted of a Hot Gas Path Inspection on the gas turbine, MAGIC inspection on the generator, removing the CDC to replace the S17s, & replacing exhaust flex seal. This outage was performed by GE, FieldCore, APMSS bucket technicians, LES and NDE technicians. Borescope inspection was also performed on the compressor and inlet sections. FieldCor
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | a58833e50e8d987415a37d8fbe92b173 | 7 |  | Inspection | Hydrogen Seals | Generator Pressure Test | 5 | End Shield, Generator Pressure Test, Hydrogen Seal Assembly, MAGIC Inspection, Seal Rings | Intercept Valves – stems and bushings, disks, balance chambers, seal rings and crosshead guide bushings.; The Generator CE was disassembled to accommodate Magic inspections and electrical testing.; Only the upper half end shields were removed for this.; The CE was reassembled, and outer end shield was pumped with sealant.; All end shield, bearing, manway and bushing box closeouts were verified by Plant Engineers. |  | Generator Pressure Test ¦ End Shield ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Seal Rings | . Foreign objects were detected and recovered from the right-side IV strainer. NDE discovered a cracked rivet on the left-side IV strainer which was weld repaired by Zachry on site. NDE indicated cracking on both IV steam dams and repair procedures were recommended but Luminant made a decision to postpone until the next major. Try bars were utilized on all valve bushings. All CRV bushings were honed to achieve allowable passable clearance for try bars. RHSVs received new disks and nuts. After ap
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 551f6c8cf5630a12b113d2d08de3af2e | 184 |  | Electrical | Stator | Winding Resistance | 5 | Belly Bands, Core, MAGIC Inspection, Wedges, Winding Resistance | (b) Rev 1.1 - 03/28/2013 GE Energy Proprietary Information Generator U21 Test And Inspect Rep… Armature Winding Resistance Equip Code Date (m/d/y) 10/29/2020 Turbine Serial No.; The MAGIC and visual inspections showed evidence of minor movement in the end- windings, and stator end wedges.; The belly bands were successfully tightened as well as the original installation allowed.; The stator core laminations and tightness of the core was found to be in good condition. |  | Winding Resistance ¦ Belly Bands ¦ Core ¦ MAGIC Inspection ¦ Wedges | Left Center Right Serial No. of Equipment: Calibration Date: Calibration Due Date: D3162044 Sheet: (b) Rev 1.1 - 03/28/2013 GE Energy Proprietary Information Generator U21 Test And Inspect Rep… Armature Winding Resistance Equip Code Date (m/d/y) 10/29/2020 Turbine Serial No. Prepared by Generator Serial No. 337X711 ERP Project ID Applicable Figure FIG 7 A B C D E F T3 T2 T1 T6 T5 T4 Left Center Right T6 T5 T4 T3 T2 T'1 0.001192 0.001192 0.001190 7.5 0.001278 0.001278 0.001276 0.001290 0.001290 0
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | bfdb8894409d648095a26800a96e2d22 | 104 |  | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 5 | Collector Rings, Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.006 0.003 0.006 0.006 0.009 0.006 Hydrogen Seal Casing C 0.182 0.18; (a) Rev 1.3 - 06/28/14 GE Power & Water Proprietary Information Turbine End Generator Field Clearance… The oil deflectors were removed, cleaned, visually inspected and measurements recorded.; The decision was to replace the inner oil deflectors on each end and the outer was replaced on the collector end.; g Generator Inner Oil Deflectors Equip Code Date(m,d,y) 10/30/2020 Turbine Serial No.; ERP Project ID Units recorded in Data set Perform visual inspection of teeth, drain holes and overall condition of oil deflectors. |  | Oil Deflector Alignment ¦ Collector Rings ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | . 337X711 ERP Project ID Units recorded in Data set Notes: 1) Applicable for LSTG (unit serial numbers starting with 180X or 280T) and 450H units. 2) For hydrogen seal clearances see D316501. 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.006 0.003 0.006 0.006 0.009 0.006 Hydrogen Seal Casing C 0.182 0.182 0.182 0.184 0.184 0.184 Middle Oil Deflector D 0.014 0.020 0.016 0
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 638365f92f2b5f01b8850ce1eb61aef4 | 7 |  | Inspection | Hydrogen Seals | Oil Deflector Alignment | 5 | End Shield, Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | This report details the Hot Gas Inspection and MAGIC Inspection performed at Luminant Lamar in Paris, Tx, on unit #21 SN 297258.; - Removed collector end outer end shield and upper inner air shield for MAGIC inspection.; - Removed, cleaned, visually inspected and replaced generator outer oil deflectors on both ends from customer stock.; - Removed, cleaned and visually inspected generator inner oil deflectors.; - Removed turbine end upper half outer end shield and upper half inner air shield for through bolt tightening. |  | Oil Deflector Alignment ¦ End Shield ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | This report details the Hot Gas Inspection and MAGIC Inspection performed at Luminant Lamar in Paris, Tx, on unit #21 SN 297258. The outage work scope was executed working two, ten-hour shifts per day starting October 22, 2020 at 07:00. General Electric/FieldCore provided technical direction, craft labor, EHS and tooling. Bucket removal/installation, blade mapping and blending performed by APMSS. The customer provided equipment rental, scaffolding, I&E support along with the operational team wor
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | f331779e548aabc7fae5f73a57d338d6 | 302 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Greasing, MAGIC Inspection, Main Lead, Step Iron, Wedges | (518) 385-3178 Generator Specialist Sharrod Childers Location Comments Photo Identification 318 deg Typical view of TE RR Image 01 Slot 31 Typical view of end wedge dowel pin at TE RR Image 02 318 deg Typical view of step irons at TE RR Ima; View of CE RR Image 44 Slots 19-16 View of end wedges and step irons on CE Image 45 54 deg.; View in field vent slot ~6” from CE RR Image 46 Slots 10-5 View of red dusting ~30” from CE RR Image 47 Slots 10-5 View of red dusting ~30” from CE RR Image 48 Slots 4-0 View of red dusting ~30” from CE RR Image 49 Slots 60-55 View of red d; Image 52 CE RR View of main lead and hardware @ 0 deg.; Image 53 CE RR View of main lead and hardware @ 0 deg |  | MAGIC Inspection ¦ Greasing ¦ Main Lead ¦ Step Iron ¦ Wedges | . g GEK 103566L (02/2017) GEK103566_L (1) g GE Power Inspection & Life Extension Services Magic Photo I.D.Worksheet Job # 10329389#exbl-298158-02 1 River Road, Bldg. 55 Rm. 263 Generator # 338X731 Schenectady, New York 12345 Date 11-06-2020 Office: (518) 385-1751, 8*235-1751 Operator Pat Higgins Fax: (518) 385-3178 Generator Specialist Sharrod Childers Location Comments Photo Identification 318 deg Typical view of TE RR Image 01 Slot 31 Typical view of end wedge dowel pin at TE RR Image 02 318 d
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | 111f6ed61fb7b55ab3e37fa2574e8bc3 | 218 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Core, End-winding, MAGIC Inspection, Retaining Rings, Sub-slots | The areas of interest, within both end winding regions consist of the following, the stator end windings, stator end winding support system, stator end winding support hardware, and the stator core compression nuts.; Using a high-resolution borescope, a thorough visual inspection was performed on the field end-winding region underneath the CE Retaining Rings. |  | MAGIC Inspection ¦ Core ¦ End-winding ¦ Retaining Rings ¦ Sub-slots | With the use of the MAGIC borescope equipment, a thorough inspection was performed on the CE Stator End Winding Region for defects on general areas of interest. The following paragraphs will discuss the inspection results of each area of interest. The areas of interest, within both end winding regions consist of the following, the stator end windings, stator end winding support system, stator end winding support hardware, and the stator core compression nuts. Using a high-resolution borescope, a
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | cf8b81ab3479b5c52180b1e6a1f15b65 | 213 |  | Inspection | Stator | Wedge Tightness Test | 5 | Focused Generator Inspection, Greasing, MAGIC Inspection, Wedge Tightness Test, Wedges | The stator wedges were visually inspected for dusting or greasing that would indicate movement in the slot during operation.; Indications of light greasing on the Collector End (CE) & Turbine End (TE) end wedges were noted.; This unit has a total of 1,680 wedges.; Due to the location the flux probe and the design of the robot, all end wedges, the remaining 26 wedges in slot 32, and two wedges in slot 33 could not be access for tightness assessment.; A total of 1,532 wedges were able to be tested. |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Greasing ¦ MAGIC Inspection ¦ Wedges | The stator wedges were visually inspected for dusting or greasing that would indicate movement in the slot during operation. Indications of light greasing on the Collector End (CE) & Turbine End (TE) end wedges were noted. A color-coded wedge map is created from the curve based off the percent tight number calculated. A value of 67 - 100 correlates to a tight wedge. 34 - 66 is the threshold for marginal tightness or hollow and any value less than 34 is determined loose. A wedge tightness analysi
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | c5a2d459f901358a37934c5806f824f4 | 213 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Core, Field Body, MAGIC Inspection, Retaining Rings, Wedges | For the stator, the areas of interest consist of the stator core iron, stator wedge system, stator ventilation ducts, and the stator inside/outside space blocks.; For the field, the areas of interest consist of the field body, field wedges, field body plugs, field ventilation passages and the accessible areas of the retaining rings. |  | MAGIC Inspection ¦ Core ¦ Field Body ¦ Retaining Rings ¦ Wedges | A MAGIC Visual Inspection of the Stator Air Gap region was performed using two high- resolution CCD cameras attached to a crawler. One camera provided a wide-angle forward- looking view, which was used for general navigation and inspection. The second camera was mounted looking radially with the ability to rotate 360 degrees providing a very sharp close- up view of defects on general areas of interest. The following paragraphs will discuss the inspection results of each area of interest within t
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | d6e9296ce390009a05ccefdb6532121f | 265 |  | Electrical | Stator | DLRO; Winding Resistance | 5 | DC Leakage, DLRO, Polarization Index, Stator Winding, Winding Resistance | The resistance of each of the three armature phases was measured using a Digital Low Range Ohmmeter (DLRO).; Armature Winding Resistance Equip Code Date (m/d/y) 11/7/2020 Turbine Serial No.; (a) Rev 2.2 - 03/11/2020 Stator Winding Resistance 338X731 … A ten-minute megger and polarization index (PI) test was performed on each of the three armature phases.; The 10 minute / 1 minute ratio for each phase indicated approximately 42,000 Megohms /3,900 Megohms with a polarization index of 10.3 or better for all three phases.; The results on all 3 phases were well above the minimum acceptable criteria prior to performing DC Leakage testing and prior to operation. | TM2030 | DLRO; Winding Resistance ¦ DC Leakage ¦ DLRO ¦ Polarization Index ¦ Stator Winding ¦ Winding Resistance ¦ TM2030 | The resistance of each of the three armature phases was measured using a Digital Low Range Ohmmeter (DLRO). Serial No. of Equipment: 53174 0113, Calibration Date: 3/4/20 (Calibration Due: 3/4/21). The individual phase resistances were measured at 0.001246, 0.001249, and 0.001243 ohms respectively for the left, center, and right phases. The readings were recorded at 21C. The corrected resistances at 25C are 0.001269, 0.001265, 0.001262 ohms respectively for the left, center, and right phases. The
UNI035727 | Fayette Energy Facility | Field_Service_Report_ProjectID_A-1377308_FSP-260331_C-10329389.pdf | 298158 | Gas Turbine | b32c43f189247112e09497cf490a6ff2 | 305 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Greasing, MAGIC Inspection, Step Iron, Sub-slots, Wedges | Image 118 TE RR View of sub-slots @ 90 deg.; Image 125 TE EW View of end wedge and step irons @ 7 o’clock.; Image 131 TE EW View of end wedge and step irons @ 12 o’clock.; Image 132 TE EW View of greasing on the step iron @ 12 o’clock.; Image 134 TE EW View of greasing on the step iron @ 1 o’clock. |  | MAGIC Inspection ¦ Greasing ¦ Step Iron ¦ Sub-slots ¦ Wedges | . Image 118 TE RR View of sub-slots @ 90 deg. Image 119 TE RR View of turns and insulation @ 90 deg. Image 120 TE RR View of insulation @ 0 deg. Image 121 TE RR View of blocking @ 0 to 270 deg. Image 122 TE RR View of turns and insulation @ 270 deg. Image 123 TE RR View of insulation @ 0 deg. Image 124 TE EW View of inner basket @ 6 o’clock. Image 125 TE EW View of end wedge and step irons @ 7 o’clock. Image 126 TE EW View of end caps @ 9 0’clock. Image 127 TE EW View of oil on the floor on TE I
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 07609eace92dbd6e9241491b265b8b29 | 366 |  | Electrical | Field, Stator | AC Impedance | 5 | AC Impedance, End-winding, Gooseneck, Main Lead, Stator Winding | Phos-Free H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Test Inspection Objectives and Assessment Borescope Robotic Borescope Robotic Borescop; Table 5 Recommended Rotor Test Rotor AIR HYD LCSW Inspection Test Component Inspection Objectives and Assessment 1st Inspection Borescope Robotic Winding Copper Resistance Rotor Winding Checks for poor connections and breaks X X X O X X Ins; Another method is the use of RSO and AC Impedance testing when flux probes are not present. |  | AC Impedance ¦ End-winding ¦ Gooseneck ¦ Main Lead ¦ Stator Winding | . GEK103566_L (1) Creating an Effective Generator Maintenance Program GEK 103566L 13 without prior permission of the copyright owner. Table 4 Recommended Water Cooled Stator Leak Tests for High Oxygen Systems†‡ What about legacy Alstom stainless steel windings?? Stator Clip-Strand Braze: Phos Containing Global Epoxy Injection or Clip-Strand Braze: Phos-Free H2 Leak Monitoring Method Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Installed Orig SLMS, Bagged Vent, or No Monitoring SLMS HP Instal
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 96dbaca1c8bd2d9be90e587fc96b966b | 246 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Core, Field Body, MAGIC Inspection, Retaining Rings, Wedges | For the stator, the areas of interest consist of the stator core iron, stator wedge system, stator ventilation ducts, and the stator inside/outside space blocks.; For the field, the areas of interest consist of the field body, field wedges, field body plugs, field ventilation passages and the accessible areas of the retaining rings. |  | MAGIC Inspection ¦ Core ¦ Field Body ¦ Retaining Rings ¦ Wedges | A MAGIC Visual Inspection of the Stator Air Gap region was performed using two high- resolution CCD cameras attached to a crawler. One camera provided a wide-angle forward- looking view, which was used for general navigation and inspection. The second camera was mounted looking radially with the ability to rotate 360 degrees providing a very sharp close- up view of defects on general areas of interest. The following paragraphs will discuss the inspection results of each area of interest within t
UNI037112 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1377050_FSP-261004_C-10330490.pdf | 297624 | Gas Turbine | 3765c96bcacaf6f0b0c886e41281ba58 | 358 |  | Inspection | Stator | Stator Findings Review | 5 | Blocked Vent Ducts, Core, End-winding, Stator Winding, Wedges | During the first several months of operation, the stator winding support system and some of the other generator components experience a break-in period.; Some examples that may point to the abnormal aging of the generator includes repeated heavy dusting on the stator end windings, early or frequent stator re-wedge, blocked vent ducts in the rotor winding, repeated oil ingress, red dust on st |  | Stator Findings Review ¦ Blocked Vent Ducts ¦ Core ¦ End-winding ¦ Stator Winding ¦ Wedges | . Plant operating experience, plant history, previous maintenance or component specific recommendations may make additional scope applicable to an inspection. It is the intent of these recommendations to remove the generator rotor only when a repair requires rotor removal for necessary access. Some generators may have design features that limit robotic inspection, in which case the rotor should be removed. Your local GE service representative can assist in maintenance planning. During the first
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 6665a33a3959ff01ebc150fdf69681b1 | 221 |  | Repair | Field, Hydrogen Seals, Stator | Red Eye Repair | 5 | End Shield, End-winding, MAGIC Inspection, Red Eye Repair, Retaining Rings | The upper, outer/inner gas shields were removed from the Collector End (CE) as well as the lower inner end shield to facilitate the magic and the borescope inspection.; The specific areas inspected were the generator air- gap region, the CE stator end-winding region, the accessible areas of the generator field and the region underneath the CE retaining rings. |  | Red Eye Repair ¦ End Shield ¦ End-winding ¦ MAGIC Inspection ¦ Retaining Rings | Implementing a thorough maintenance program is the most effective way to retain generator reliability and avoid major failure expenses. However, it must be cost effective in that there are demonstrated savings in improved availability & reliability to offset the cost of implementing the program. The three important elements of a thorough program are maintenance frequency, electrical testing and visual inspection. Generator electrical testing is focused on the integrity of insulation systems. Cha
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 15c77096212506684e245cdd867db464 | 226 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Core, Field Body, MAGIC Inspection, Retaining Rings, Wedges | For the stator, the areas of interest consist of the stator core iron, stator wedge system, stator ventilation ducts, and the stator inside/outside space blocks.; For the field, the areas of interest consist of the field body, field wedges, field body plugs, field ventilation passages and the accessible areas of the retaining rings. |  | MAGIC Inspection ¦ Core ¦ Field Body ¦ Retaining Rings ¦ Wedges | A MAGIC Visual Inspection of the Stator Air Gap region was performed using two high- resolution CCD cameras attached to a crawler. One camera provided a wide-angle forward- looking view, which was used for general navigation and inspection. The second camera was mounted looking radially with the ability to rotate 360 degrees providing a very sharp close- up view of defects on general areas of interest. The following paragraphs will discuss the inspection results of each area of interest within t
UNI037113 | Washington Energy Facility | Field_Service_Report_ProjectID_A-1376780_FSP-261003_C-10330252.pdf | 297623 | Gas Turbine | 931bcc08fe535205f5bf1eaf0bd154ab | 225 |  | Inspection | Field, Stator | MAGIC Inspection | 5 | Centering Ring, Collector Rings, End-winding, MAGIC Inspection, Retaining Rings | The assessible areas of the Retaining Rings (RR) were in satisfactory condition.; Centering Rings, Fan Rings and Blades, see Mechanical Inspection Report.; The condition of collector rings was satisfactory. |  | MAGIC Inspection ¦ Centering Ring ¦ Collector Rings ¦ End-winding ¦ Retaining Rings | . The assessible areas of the Retaining Rings (RR) were in satisfactory condition. Centering Rings, Fan Rings and Blades, see Mechanical Inspection Report. The Vent holes that could be viewed with the Magic equipment were in satisfactory condition. The condition of collector rings was satisfactory. The overall inspection of the generator fields exterior body and end winding region was satisfactory. Minor contamination along collector ring surface should be wiped down with denatured alcohol and c
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | 81e3aa8b6a69789c7d487d0fb856c7a0 | 1 |  | Inspection | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, MAGIC Inspection, Oil Deflector Alignment, Oil Deflectors | Gas Turbine Generator Mechanical Support Systems Other Systems Combustion Inspection (complete) Coupling / Alignment MAGIC Inspection Major Inspection (complete) Bearings Hot Gas Path Inspection (complete) Hydrogen Seals Oil Deflectors Tota; and a MAGIC inspection of the Generator with the bearings shipped off for cleaning and inspection. |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ MAGIC Inspection ¦ Oil Deflectors | GAS TURBINE INSPECTION REPORT GT1 Major Inspection and Generator MAGIC for ODESSA-ECTOR POWER PARTNERS, LP Odessa-Ector Facility, Unit GT1 Equipment Serial #: 297490 Job Start Date: October 03, 2011 Report Issued: Oracle Project Id: 10103595 Report Printed: December 09, 2011 This report may contain Confidential and Proprietary information subject to a confidentiality agreement. Prepared By: ATIF SHAMSI Field Engineer Approved By: BRIAN STALCUP Service Manager PAGE JOB SUMMARY 1 INSPECTION SUMMAR
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 3802194fe0a8b6119cf6a2bddf348c83 | 206 |  | Electrical | Stator | Polarization Index; DC Leakage | 4 | DC Hipot, DC Leakage, Polarization Index, Stator Winding | Stator Winding Insulation Resistance / HV Proof Tests Generator Test and Inspections Date 04/14/2020 Turbine No.:; Date 2250823 03/19/2021 DC hipot tester Megger 2260824 07/22/2020 Current (Amps) Yuriy Denisov Scott Schmeltzer 10323897 Winding Temperature (oC) Recommended Test Voltage HIGH VOLTAGE PROOF TEST per TM2050 Ambient Tempature (oC) Relative Hu; Failed test at [KV/Time(sec)] Excitation Voltage (Volts) NA Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044. | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Hipot ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | Part Condition: Good Part Description: The test results were satisfactory. Stator Winding Insulation Resistance / HV Proof Tests Generator Test and Inspections Date 04/14/2020 Turbine No.: Prepared by: Equipment 7FH2 Generator No.: OEM GE Stator Voltage: Project ID: DC INSULATION RESISTANCE (Megohms) per TM2030 Voltage: 5000 Volts Time(Min) Left Center Right 0.5 2100 2040 2170 1.0 4650 4580 4880 2.0 9620 9590 10100 3.0 14180 13690 14690 4.0 17720 18050 19250 5.0 21100 22000 23400 6.0 25700 25800
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | a5507210605d649fb529452dba63ca71 | 230 |  | Electrical | Stator | Winding Resistance; Polarization Index | 4 | DC Leakage, Polarization Index, Stator Winding, Winding Resistance | (a) Rev 2.2 - 09/25/2019 Armature Winding Resistance Equip Code Date (m/d/y) 11/4/2020 Turbine Serial No.; (a) Rev 2.2 - 03/11/2020 Stator Winding Insulation Resistance / HV Proof Tests Date 11/04/2020 Generator No.:; Left (CE) Center (CE)Right (CE) Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Tes; (a) Rev 2.1 - 08/05/2020 g Armature Insulation DC Leakage Test Date(m/d/y) 11/4/2020 Generator Serial No. | TM2030, TM2050, TM4010 | Winding Resistance; Polarization Index ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ Winding Resistance ¦ TM2030 ¦ TM2050 | . Proctor GE Winding Temp.s (ºC ) Resistance (ohms) Ambient Temperature Relative Humidity Comments Reading Checks per TM4010 Previous Test Correct to 25 ºC Prior Test @25 ºC Historical Resistance Readings 0 1 2 3 4 5 6 7 0 50 100 150 Z(ohms) Applied Voltage (volts) FIELD IMPEDANCE D316303 Sheet: (a) Rev 2.2 - 09/25/2019 Armature Winding Resistance Equip Code Date (m/d/y) 11/4/2020 Turbine Serial No. Prepared by Generator Serial No. 337X710 ERP Project ID Applicable Figure FIG 7 A B C D E F T3 T2
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | f6e87e66593863b954e735ebd4c9761e | 17 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings | (b) Rev 2.2 - 08/28/2018 FINAL_D316512 - H2 Case Oil Deflect… g Generator Oil Deflectors Equip Code Date(m,d,y) 11/4/2020 Turbine Serial No.; ERP Project ID Units recorded in Data set Perform visual inspection of teeth, drain holes and overall condition of oil deflectors.; Use form to record middle oil deflectors for air cooled units, for H2 cooled units use form D316512.; (a) Rev 1.0 - 06/29/14 GE Power & Water Proprietary Information FINAL_D316610 -Oil Deflectors CE g Hydrogen Seals Equip Code: |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | . = 0.000 in. 'E' OIL DEFLECTOR (inches) LOCATION DIAMETER JOUR. DIA. CLEARANCE A 16.037 15.999 .038 B 16.037 15.999 .038 C 16.037 15.999 .038 AVERAGE .038 Voltage Note: All dimensions must be entered into Oil Deflector 500 table in order to calculate average clearance CAL Date FieldCore FE English - inches Seal Width "B" Measurement (From 316501) Stack Check = Acasing - (Bair seal+Bhyd seal) 7FH2 Megohms Casing Insulation Resistance 0.999 Instrument Description 11/4/2020 Cleaned Joints Dowels I
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | ff6c52869096681c060050c6f3c14c79 | 96 |  | Inspection | Field, Stator | Stator Findings Review | 4 | End-winding, Greasing, High Voltage Bushings, Sub-slots | (518) 385‐3178 Generator Specialist Steve Proctor TE RR View of turn to turn insulation Image 87 TE RR View of turn to turn insulation Image 88 TE RR View of turn to turn insulation Image 89 TE RR View of blocking Image 90 TE RR View of sub |  | Stator Findings Review ¦ End-winding ¦ Greasing ¦ High Voltage Bushings ¦ Sub-slots | . Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor TE RR View of turn to turn insulation Image 87 TE RR View of turn to turn insulation Image 88 TE RR View of turn to turn insulation Image 89 TE RR View of blocking Image 90 TE RR View of sub slots Image 91 TE RR View of blocking Image 92 TE RR View of turn to turn insulation Image 93 CE EW View of high voltage bushings Image 94 CE EW View of minor greasing on connections rings at 5 o’clock position Image 95 CE EW View of phase conne
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 9708c24c8240dd02fcb2cb98710f6300 | 94 |  | Inspection | Field, Stator | Stator Findings Review | 4 | Greasing, Retaining Rings, Step Iron, Wedges | (518) 385‐3178 Generator Specialist Steve Proctor Location Comments Photo Identification Slot 15 View of TE end wedge dowel pin Image 01 Slots 27 - 24 View of TE step iron Image 02 336 Deg / Slot 30 View of TE RR nose Image 03 Slot 28 View |  | Stator Findings Review ¦ Greasing ¦ Retaining Rings ¦ Step Iron ¦ Wedges | . 55 Rm. 263 Generator # 290T435 Schenectady, New York 12345 Date 11‐05‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W. Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor Location Comments Photo Identification Slot 15 View of TE end wedge dowel pin Image 01 Slots 27 - 24 View of TE step iron Image 02 336 Deg / Slot 30 View of TE RR nose Image 03 Slot 28 View of bent punching ~118” from CE RR Image 04 Slot 27 View of bent punching ~152” from CE RR Image 05 Slot 27 / 12 Deg View of
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 91ab3e8f6330f35749c0423f77aebf20 | 149 |  | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 4 | Fan Blades, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Oil Deflectors and Hydrogen Seals Access Door Gaskets Quantity:; Oil Deflectors and Hydrogen Seals Gas Side Hydrogen Seal Quantity:; Oil Deflectors and Hydrogen Seals Bushing Box Door Gaskets Quantity: |  | Oil Deflector Alignment ¦ Fan Blades ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Oil Deflectors and Hydrogen Seals Access Door Gaskets Quantity: 3 Catalog #: 341A6573P0001 Drawing #: 112E2803 Customer Part #: Part Serial #: Fan Blade Lock Plates Quantity: 16 Catalog #: 0719A679P0013 Drawing #: Customer Part #: Part Serial #: Oil Deflectors and Hydrogen Seals Gas Side Hydrogen Seal Quantity: 1 Catalog #: 585D2468G0022 Drawing #: Customer Part #: Part Serial #: Air Side Hydrogen Seal Quantity: 1 Catalog #: 585D2468G0001 Drawing #: Customer Part #: Part Serial #: Oil Deflectors
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | cc8374b09ceb6f03a22600e0891b0386 | 132 |  | Inspection | Stator | MAGIC Inspection; Focused Generator Inspection | 4 | Core, Focused Generator Inspection, Keybars, MAGIC Inspection | The source of the red dusting should be investigated at the next available opportunity, a behind the core inspection of the core laminations and key bars along with a core tightness check should be done. |  | MAGIC Inspection; Focused Generator Inspection ¦ Core ¦ Focused Generator Inspection ¦ Keybars ¦ MAGIC Inspection | Left Center Right Serial No. of Equipment: Calibration Date: Calibration Due Date: D3162044 Sheet: (b) Rev 1.1 - 03/28/2013 GE Energy Proprietary Information Unit Condition Summary The electrical tests conducted, proved the stator and field to be in good electrical condition. The MAGIC and visual inspections showed evidence of movement in the end- windings. Minimal oil ingress was observed. The source of the red dusting should be investigated at the next available opportunity, a behind the core
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 0c007c1515e8696b770b9c94e8dc1c90 | 95 |  | Inspection | Field, Stator | Focused Generator Review | 4 | Main Lead, Pole Jumper, Sub-slots, Wedges | (518) 385‐3178 Generator Specialist Steve Proctor Slot 20 View of damaged punching ~30” from CE RR Image 43 60 Deg View looking down field vent hole ~21” from CE RR Image 44 72 Deg /Slot 17 View of field and packages ~45” from CE RR Image 4 |  | Focused Generator Review ¦ Main Lead ¦ Pole Jumper ¦ Sub-slots ¦ Wedges | . 55 Rm. 263 Generator # 290T435 Schenectady, New York 12345 Date 11‐05‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W. Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor Slot 20 View of damaged punching ~30” from CE RR Image 43 60 Deg View looking down field vent hole ~21” from CE RR Image 44 72 Deg /Slot 17 View of field and packages ~45” from CE RR Image 45 Slot 51 View of foreign material on stator wedge ~14” from CE RR Image 46 258 Deg View of partially blocked field vent hol
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 1614969f6642c7db9569956294c887a6 | 94 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings |  | EM3406 | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings ¦ EM3406 | Collector End Gas Side Collector End Gas Side2 Turbine End Air Side Turbine End Gas Side g Hydrogen Seal Casing Collector End Casing Date (m/d/y) Turbine Serial No. Prepared by Equipment Generator Serial No. 337X711 Units INSPECTIONS & CHECKS CODE X Work Carried Out N Not Done NA Not Applicable C See Comments V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Air Hydrogen Average 0.748 0.751 'A' GAP DIMENSIONS (inches) LOCATION PINS IN PINS OUT Top Left 16.625 16.625 Top 16.625 16.6
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 086d91a322c3170b5fbdb9c4307d6a21 | 98 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 4 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors, Seal Rings |  |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors ¦ Seal Rings | . = 0.000 in. 'E' OIL DEFLECTOR (inches) LOCATION DIAMETER JOUR. DIA. CLEARANCE A 16.032 16.000 .032 B 16.032 16.000 .032 C 16.030 16.000 .030 (if applicable) AVERAGE .031 Voltage Note: All dimensions must be entered into Oil Deflector 500 table in order to calculate average clearance CAL Date Cleaned Joints Dowels Insp per GN-2151 Casing Insulation Resistance Megohms Instrument Description ID No. Comments 10/30/2020 Durrant English - inches Seal Width "B" Measurement (From 316501) Stack Check =
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 6714f1dc55daacce6f9d3bbe6e36c91d | 176 |  | Inspection | Stator | Wedge Tightness Test | 4 | Focused Generator Inspection, Keybars, Wedge Tightness Test, Wedges | Steve Proctor COLLECTOR END TURBINE END W E D G E S W E D G E S W E D G E S W E D G E S 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 S 1 96 98 93 95 97 97 92 96 94 91 87 80 1 S L 2 96 96 97 94 96 95 93 87 71 81; 5 keybars could be reached for measurement. |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Keybars ¦ Wedges | . Howard Test Date: Generator Specialist: Steve Proctor COLLECTOR END TURBINE END W E D G E S W E D G E S W E D G E S W E D G E S 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 S 1 96 98 93 95 97 97 92 96 94 91 87 80 1 S L 2 96 96 97 94 96 95 93 87 71 81 83 77 2 L O 3 95 96 97 99 96 97 93 86 89 93 83 98 3 O T 4 96 95 98 99 98 94 85 91 83 77 84 87 4 T S 5 78 93 94 97 94 94 90 88 91 78 89 83 5 S 6 93 96 97 94 96 95 84 95 91 84 90 89 6 S 7 98 92 96 98 97 93 89 90 82 71 8
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 0c46b59792025d2c6ba7bbe553395e09 | 177 |  | Electrical | Stator | Winding Resistance; Polarization Index | 4 | DC Leakage, Keybars, Polarization Index, Winding Resistance | 5 keybars could be reached for measurement.; C, N, P or O ohms ºC RTD INSULATION RESISTANCE TEST RESULTS (MEGOHMS) RTD INSULATION RESISTANCE (MEGOHMS) @ 500 Volts DC # 1A thru # 9B = 5780 megohms As Found # 1A thru # 9B = 4300 megohms Post DC Leakage Megger SN:; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.06 1.95 5.16 20.23 3.97 5.10 30.49 6.00 5.08 40.56 7.93 5.11 50.55 9.85 5.13 60.47 11.68 5.18 70.56 13.46 5.24 80.27 15.10 5.32 90.71 16.80 5.40 100.35 18.31 5.48 110.49 19.86 5.56 120.4 | TM2010, TM4010, TM4020, TM4030 | Winding Resistance; Polarization Index ¦ DC Leakage ¦ Keybars ¦ Polarization Index ¦ Winding Resistance ¦ TM2010 ¦ TM4010 | . 5 keybars could be reached for measurement. Collector End (CE) and Turbine End (TE) are used for axial orientation of the compression bands and gap measurements. AS FOUND CE TE Band 1 Band 2 Band 3 KB1 0 0.055 0 0.055 0.025 0 KB2 0 0.03 0 0.015 0.021 0 KB3 0 0.033 0 0.012 0.035 0 KB4 0 0.025 0 0.012 0.04 0 KB5 0 0.041 0 0.01 0.059 0 CE TE CE TE CE TE AS LEFT Band 1 Band 2 Band 3 KB1 0 0.015 0 0.005 0.025 0 KB2 0 0.01 0 0.006 0.021 0 KB3 0 0.007 0 0.008 0.015 0 KB4 0 0.002 0 0.01 0.005 0 KB5 0
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | d9d084a1e8c8332816c1e984d2a74e8f | 93 |  | Mechanical | Field, Hydrogen Seals | Oil Deflector Alignment | 4 | Collector Rings, Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | The collector brushes should ride fully on the collector rings when the unit is at running tempeature.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Entrance Baffle H NA NA Inner Oil Deflector K 0.011 X 0.013 0.013 0.027 0.011 Middle Oil De; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Outer Oil Deflector B 0.008 0.008 0.009 0.010 0.016 0.010 Hydrogen Seal Casing C 0.185 X 0.; 3) Left / Right orientation is defined as looking from the coupling towards the collector rings Clearances (inches) Description Location 1 2 3 4 5 6 Inner Oil Deflector K 0.007 0.006 0.008 0.008 0.016 0.007 Middle Oil Deflector L 0.013 X 0. |  | Oil Deflector Alignment ¦ Collector Rings ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | The hydrogen seals from both ends were removed, cleaned, visually inspected and measurements were recorded. The seals didn't appear to be in bad condition. The measurements that were taken showed the seals to be out of specification. New seals were installed from the customers stock. Collector End Air Side During disassembly of both of the ends of the generator the clearances were taken. Nothing out of the ordinary was discovered. g Generator Field Clearance Equip Code: Collector End (Axial Fan)
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | 68688b89c05435480364545b0b675f1f | 35 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | New journal bearings come with new seal rings as part of the assembly.; New oil seal rings and hardware installed.; All oil deflectors were replaced. |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | . New journal bearings come with new seal rings as part of the assembly. New oil seal rings and hardware installed. C C B B A A Bearing Oil Deflector Clearances Date 12/7/2011 Turbine Serial No. Prepared by C. Helget Data Type Final INSPECTIONS & CHECKS CODE Deflector Inspected X X Work Carried Out Journals Inspected X N Not Done NA Not Applicable X C See Comments X V Visual Inspection MP Mag. Particle UT Ultrasonic PT Penetrant Location Oil Rings Journal Clearance Condition Number A-Dia B-Dia C
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | e53404ced4b16b93b319b27640aa510f | 6 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | All seal rings and oil deflectors were replaced. | FMI F6441G10 | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings ¦ FMI F6441G10 | . All three nozzle stages were replaced. All shroud and nozzle seals, pins, and plugs were replaced. All clearance and boroscope seal pins and plugs were also replaced. Exhaust Summary- The exhaust case had typical inner skin cracking around the struts and was repaired by onsite welders. The flex seals and exhaust cone rope seal was replaced. The graphite/steel gasket was also replaced in case a balance shot would be required through the S3 exhaust cone window. During disassembly of the T2 beari
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | 2e377138033c48dbe29e3727c6eeee22 | 11 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings |  |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | . RECOMMENDATIONS Item InsRec PU RI QTY UM PartsDescription CustStk Catalog Drawing 1 1 X 2 1 Bearing, Journal,Assembly,Wire Packing Gland G0235 227C9753P002 2 1 X 4 1 Bearing, Journal,Assembly,Wire Packing Gland G0235 227C9753P004 3 1 X 4 1 Bearing, Journal,Assembly,Thermocouple G0235 362A1885G001 4 1 X 1 1 Bearing, Journal,Assembly,T1 Fwd Oil Deflector G0801 110E2905G002 5 1 X 1 1 Bearing, Journal,Assembly,T1 Aft Air Seal G0801 199C4740P001 6 1 X 1 1 Bearing, Journal,Assembly,T1 Mid Oil Deflec
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | 6ccaa7a3ab9d6ada6a3d48c898b31eae | 26 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Seal Rings | Bearing seal rings were sent out with the bearings and re-babbited as well.; The LH T2 oil deflectors were found warped and were cut out.; T1 oil deflectors were found in typical condition with some slight oil burn marks.; All new oil deflectors were installed.; T1 showing new lift oil mod lines installed BEARINGS T1 final assembly T2 as found BEARINGS T2 LH RS score T2 LH RS score BEARINGS T2 aft seal ring bolting broken T2 as found oil deflectors warped BEARINGS T2 journal back from the service s |  | Oil Deflector Alignment ¦ Oil Deflectors ¦ Seal Rings | . A light score was found in the LH RS pad of T2. Pads were rebabbitted and internal lift hoses were replaced at the service shop. Lift oil check valve orientation was verified with supply air prior to installing. The T2 aft bearing seal bolting at the horizontal joint was found broken on both sides during disassembly. Bearing seal rings were sent out with the bearings and re-babbited as well. T1 lift oil lines were upgraded with the new mod during this inspection. Lift was verified prior to dis
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 22118e6346468d10a8a05e3f7995052e | 236 |  | Mechanical | Hydrogen Seals | Wedge Tightness Test; Oil Deflector Alignment | 3 | Oil Deflector Alignment, Oil Deflectors, Wedge Tightness Test | TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check TE Gen 16.024" 16.024" 24.0 Mils 24.0 Mils 1.6 Mils 0.0 Mils  CE Gen 16.024" 16.024" 23.0 Mils 23.0 Mils 1.6 Mils 0.0 Mils  TWIST; (a) Rev 0.0 - 09/03/93 GE Energy Proprietary Information Journal bearing clearance_As-Left g Generator Oil Deflector Alignment Date (m,d,y) Turbine Serial No.; (a) Rev 0.0 - 09/03/93 GE Energy Proprietary Information Oil Deflector Alignment_As-Left g Bearing To Journal Alignment For Bearings With Ball Seats Date(m/d/y) 4/7/2020 Turbine Serial No.; TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check TE Gen 16.024" 16.024" 23.0 Mils 23.0 Mils 1.6 Mils 0.0 Mils  CE Gen 16.024" 16.024" 22.0 Mils 22.0 Mils 1.6 Mils 0.0 Mils  TWIST |  | Wedge Tightness Test; Oil Deflector Alignment ¦ Oil Deflector Alignment ¦ Oil Deflectors ¦ Wedge Tightness Test | . 337X155 Prepared by NOTE: 1. On most generator bearings, the end leakage groove is on the outboard end. 2. On hood bearings, the outboard end is set low to compensate for vacuum deflection. TILT Brg Section Reading in Inches Reading in Mils Limits Actual Tolerance # IV OV IT OT 0.0 To (Mils) Check TE Gen 16.024" 16.024" 24.0 Mils 24.0 Mils 1.6 Mils 0.0 Mils  CE Gen 16.024" 16.024" 23.0 Mils 23.0 Mils 1.6 Mils 0.0 Mils  TWIST Brg Readings in Mils Tolerance # Section IL OL IR OR Limits Actual
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | b25bea3ebf21afde930149c579f492bc | 208 |  | Electrical |  | Polarization Index; DC Leakage | 3 | DC Hipot, DC Leakage, Polarization Index | g Armature Insulation DC Leakage Test Date(m/d/y) 4/14/2020 Generator Serial No.; (a) Rev 1.1 - 03/28/13 GE Energy Proprietary Information D3162044_DC Leakage_337X155 g Armature Insulation DC Leakage Test Date(m/d/y) 4/14/2020 Generator Serial No.; 0.00 1.00 2.00 3.00 4.00 5.00 6.00 7.00 0 10 20 30 40 50 60 70 A KV DC Leakage Test Left Center Right Serial No.; DC hipot tester 2250823 Calibration Date:; (b) Rev 1.1 - 03/28/2013 GE Energy Proprietary Information D3162044_DC Leakage_337X155 |  | Polarization Index; DC Leakage ¦ DC Hipot ¦ DC Leakage ¦ Polarization Index | Part Condition: Good Part Description: The test results were satisfactory. g Armature Insulation DC Leakage Test Date(m/d/y) 4/14/2020 Generator Serial No. 337X155 Prepared by Yuriy Denisov Customer Odessa-Ector Turbine Serial No. Scott Schmeltzer Manufacture GE FSR No. A 15 KV DC voltage was applied to each phase with the other two phases grounded for a period of 10 minutes. Readings were recorded at specific time intervals. On the basis of these readings a time schedule is established for read
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | ab3244bdba917d2398ec2f2b2ed5f0fd | 228 |  | Electrical |  | Winding Resistance; Polarization Index | 3 | DC Leakage, Polarization Index, Winding Resistance | Project ID RTD INSULATION RESISTANCE TEST RESULTS (MEGOHMS) # 1A thru # 9B = megohms Initial # 1A thru # 9B = megohm Post DC Leakage # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = megohms # thru # = m; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.35 1.98 5.23 20.03 3.84 5.22 30.12 5.75 5.24 40.32 7.62 5.29 50.28 9.40 5.35 60.20 11.14 5.40 70.39 12.85 5.48 80.65 14.51 5.56 90.32 16.01 5.64 100.01 17.47 5.72 110.47 18.98 5.82 120.6 | TM2010, TM4010, TM4020, TM4030 | Winding Resistance; Polarization Index ¦ DC Leakage ¦ Polarization Index ¦ Winding Resistance ¦ TM2010 ¦ TM4010 | . Prepared By Turbine Serial No. Project ID Test Article Reference: TM2010 Winding Temperature: 14.5 ºC Device: RTD RESISTANCE No. AB AC BC (AB+AC)/2 - BC 1 P 108.85 108.84 1.55 107.30 18.95 1' P 108.82 108.89 1.45 107.41 19.23 2 P 108.84 108.84 1.69 107.15 18.57 2' P 108.91 108.91 1.69 107.22 18.75 3 P 108.80 108.79 1.70 107.10 18.43 3' P 108.83 108.85 1.70 107.14 18.55 4 P 108.09 108.09 1.10 106.99 18.16 4' P 108.27 108.27 1.09 107.18 18.65 5 P 108.29 108.29 1.29 107.00 18.18 5' P 108.34 108.3
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 1c7c538dd792615b7175dc9fa823a4a7 | 223 |  | Mechanical | Stator | Wedge Tightness Test | 3 | Wedge Looseness, Wedge Tightness Test, Wedges | 22 Number of Wedges: |  | Wedge Tightness Test ¦ Wedge Looseness ¦ Wedges | Holdings, LLC / Lamar Power Partners Unit 22 / 337X710 24 Image97 Image98 Image99 Image100 11/3/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 22 / 337X710 25 Image101 Image102 Image103 Image104 11/3/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 22 / 337X710 26 Image105 Image106 11/3/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 22 / 337X710 27 ? ? ? Customer: Lamar Power Partners Number of Slots: 60 Hollow Wedge Lowest Valu 34 Site/Unit: 22 Number of Wedges
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 0f3588bdd066f051174b90c9258e5826 | 169 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Inner Gas Shield, Oil Deflector Alignment, Oil Deflectors | The Collector end inner gas shield was removed from the generator stator and inspected for damage and wear.; The Collector end inner or outer oil deflectors were removed from the generator and inspected for damage and wear.; The oil deflectors were cleaned and dimensional checks were performed after reassembly. |  | Oil Deflector Alignment ¦ Inner Gas Shield ¦ Oil Deflectors | The Collector end upper half outer endshield was removed from the generator stator and inspected for damage and wear. No abnormal conditions were noted during this outage. The outer endshield was installed back onto the stator frame and pumped with dow corning to ensure a proper seal. A Clearance check was taken on the horizontal and vertical joints to ensure a proper seating on the endshields. The Collector end inner gas shield was removed from the generator stator and inspected for damage and
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 19866d41ce145b7900e84e6281989b93 | 2 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 2 1.4 Work Scope __________ 4 1.5 EHS __________ 4 1.6 Quality __________ 4 2 Turbine __________ |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Table Of Contents 1 Summary __________ 1 1.1 Timers and Counters __________ 1 1.2 Site Personnel __________ 1 1.3 Executive Summary __________ 2 1.4 Work Scope __________ 4 1.5 EHS __________ 4 1.6 Quality __________ 4 2 Turbine __________ 5 2.1 Auxiliaries __________ 5 2.1.1 Hydraulic Pumps and Motors __________ 5 2.1.2 Turning Gear __________ 5 2.1.3 Fuel Gas Valves __________ 5 2.1.4 Piping and Flexible Metal Hoses __________ 5 2.2 Inlet Section __________ 25 2.2.1 Inlet Bellmouth __________
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 4613e6ef931beff432be15d37955c2fe | 227 |  | Inspection | Stator | Wedge Tightness Test | 3 | Focused Generator Inspection, Wedge Tightness Test, Wedges | Steve Proctor COLLECTOR END TURBINE END W E D G E S W E D G E S W E D G E S W E D G E S 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 S 1 93 96 96 93 97 95 92 92 98 96 87 97 1 S L 2 94 91 97 90 98 97 93 96 97 97 | TM2010 | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Wedges ¦ TM2010 | . Howard Test Date: Generator Specialist: Steve Proctor COLLECTOR END TURBINE END W E D G E S W E D G E S W E D G E S W E D G E S 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 S 1 93 96 96 93 97 95 92 92 98 96 87 97 1 S L 2 94 91 97 90 98 97 93 96 97 97 99 95 2 L O 3 97 96 89 97 98 98 97 90 91 89 92 90 3 O T 4 91 95 88 94 96 96 98 99 97 91 92 96 4 T S 5 90 90 94 96 96 97 86 90 85 91 93 84 5 S 6 96 95 94 94 92 97 95 85 90 98 93 89 6 S 7 94 83 96 94 94 94 92 83 86 80 9
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 7af373823e0105efc58b344c42eb4cff | 36 |  | Inspection | Stator | Stator Findings Review | 3 | Greasing, Step Iron, Wedges | (518) 385‐3178 Generator Specialist Steve Proctor Location Comments Photo Identification Slot 35 Typical view of CE end wedge dowel pin Image 01 228 Deg Typical view of CE RR nose Image 02 Slots 33 - 31 Typical view of CE step iron Image 03 |  | Stator Findings Review ¦ Greasing ¦ Step Iron ¦ Wedges | . 78 297257 Luminant Energy - Lamar Pow… Page 31 of 263 g GE Power Inspection & Life Extension Services Photo I.D.Worksheet General Electric International, Inc Job # 10326236 1 River Road, Bldg. 55 Rm. 263 Generator # 337X710 Schenectady, New York 12345 Date 11‐03‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W.Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor Location Comments Photo Identification Slot 35 Typical view of CE end wedge dowel pin Image 01 228 Deg Typical view of CE
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | c9a061c66a8c7abb66081112fc979e8c | 126 |  | Electrical |  | Winding Resistance; Polarization Index | 3 | DC Leakage, Polarization Index, Winding Resistance | # 7 thru # 12 = 22000 megohms C, N, or P (only) # 13 thru # 17 = 27000 megohms C = Copper # thru # = megohms N = Nickel # 1 thru # 17 = 21000 megohms After DC Leakage Megger Serial No:; OEM FIELD IMPEDANCE (TM4020) Voltage Amps Z (ohms) 10.20 1.71 5.96 20.51 3.53 5.81 30.04 5.15 5.83 40.09 6.85 5.85 50.30 8.58 5.86 60.50 10.25 5.90 70.06 11.67 6.00 80.30 13.10 6.13 90.05 14.38 6.26 100.53 15.65 6.42 110.32 16.71 6.60 120.7; (a) Rev 2.2 - 09/25/2019 Armature Winding Resistance Equip Code Date (m/d/y) 11/6/2020 Turbine Serial No. | TM4010, TM4020, TM4030 | Winding Resistance; Polarization Index ¦ DC Leakage ¦ Polarization Index ¦ Winding Resistance ¦ TM4010 ¦ TM4020 | . Prepared By Turbine Serial No. Project ID RTD TEST Winding Temperature: 17 ºC Device: Type must be entered as follows: C, N, or P. *See Note below. RTD RESISTANCE No. AB AC BC (AB+AC)/2 - BC Terminal Strip 1 P 111.10 111.12 1.71 109.40 23.97 2 P 111.54 111.53 1.89 109.65 24.59 3 P 111.39 111.40 1.91 109.49 24.19 4 P 111.86 118.86 1.12 114.24 36.31 5 P 112.05 112.05 1.15 110.90 27.80 6 P 111.56 111.57 0.94 110.63 27.09 7 P 110.98 110.97 1.50 109.48 24.16 8 P 111.37 111.37 1.56 109.81 25.02 9 P
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | e90fd6c0c7aebe00ed6b72d7731f3d3b | 117 |  | Mechanical | Stator | Wedge Tightness Test | 3 | Wedge Looseness, Wedge Tightness Test, Wedges | ST 20 Number of Wedges: |  | Wedge Tightness Test ¦ Wedge Looseness ¦ Wedges | La Frontera Holdings, LLC / Lamar Power Partners Unit 20 / 290T435 21 Image85 Image86 Image87 Image88 11/5/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 20 / 290T435 22 Image89 Image90 Image91 Image92 11/5/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 20 / 290T435 23 Image93 Image94 Image95 Image96 11/5/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 20 / 290T435 24 Image97 Image98 Image99 Image100 11/5/2020 La Frontera Holdings, LLC / Lamar Power Partners Un
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 7baa7a7b57e53942fbceb3ccae3f3d93 | 2 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 3 | Hydrogen Seal Assembly, Oil Deflector Alignment, Oil Deflectors | Table Of Contents 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 2 1.3 EHS __________ 4 1.4 Quality __________ 4 2 Technical __________ 5 2.1 Recommendations __________ 5 3 Turbine __________ 6 3.1 B |  | Oil Deflector Alignment ¦ Hydrogen Seal Assembly ¦ Oil Deflectors | Table Of Contents 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 2 1.3 EHS __________ 4 1.4 Quality __________ 4 2 Technical __________ 5 2.1 Recommendations __________ 5 3 Turbine __________ 6 3.1 Bearing __________ 6 3.1.1 T-6 Upper Half Bearing __________ 6 3.1.2 Oil Deflectors and Hydrogen Seals __________ 8 3.2 Rotors __________ 17 3.2.1 LP Rotor __________ 17 3.3 Shells __________ 27 3.3.1 HP/IP Shell __________ 27 3.4 Valves __________ 36 3.4.1 Mai
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 56fe64b0b0b0facbdffde49a020a92b3 | 128 |  | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | (a) Rev 2.2 - 03/11/2020 Stator Winding Insulation Resistance / HV Proof Tests Date 11/05/2020 Generator No.:; Left (CE) Center (CE)Right (CE) 15 16 47% Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC L; (a) Rev 2.1 - 08/05/2020 g Armature Insulation DC Leakage Test Date(m/d/y) 11/6/2020 Generator Serial No. | TM2030, TM2050 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | . Selection Customer Designation Calibration Due Date 7/2/2020 7/2/2021 Test Equipment Information Pass Rules: 1. The spread of copper resistance readings between the phases should be within 1%. 2. When comparing to historical test results each phase should be within +/- 1% of the previous reading for that phase. 3. When comparing to factory test results, each phase should be within +/- 2% of the original factory measurement for that phase. 4. When comparing to calculated values, each phase shou
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 3bd08de30467f5e21ab777a359ce8d9c | 125 |  | Inspection | Stator | Wedge Tightness Test | 3 | Focused Generator Inspection, Wedge Tightness Test, Wedges | Proctor W E D G E S W E D G E S 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 S 1 75 96 98 91 97 98 97 96 96 94 98 95 1 S L 2 73 87 96 89 98 97 97 95 94 96 97 90 2 L O 3 79 88 97 97 98 98 91 97 97 99 86 75 3 O T 4 94 96 97 97 97 98 96 97 98 |  | Wedge Tightness Test ¦ Focused Generator Inspection ¦ Wedges | . Howard Test Date: Generator Specialist: S. Proctor W E D G E S W E D G E S 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 S 1 75 96 98 91 97 98 97 96 96 94 98 95 1 S L 2 73 87 96 89 98 97 97 95 94 96 97 90 2 L O 3 79 88 97 97 98 98 91 97 97 99 86 75 3 O T 4 94 96 97 97 97 98 96 97 98 95 92 94 4 T S 5 94 96 98 95 96 96 92 98 97 97 77 75 5 S 6 84 96 92 95 98 96 97 96 98 88 95 74 6 S 7 82 94 96 97 95 96 84 94 97 94 87 88 7 S L 8 88 97 97 91 97 98 95 94 96 93 87 70 8 L O 9 82 94 95 93 92 97 98 93 87
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | af978995aeebf21f4d4926991f97edb1 | 179 |  | Electrical | Stator | Polarization Index; DC Leakage | 3 | DC Leakage, Polarization Index, Stator Winding | (a) Rev 2.2 - 09/25/2019 Generator U21 Test And Inspect Rep… Stator Winding Insulation Resistance / HV Proof Tests Date 10/29/2020 Generator No.:; Left (CE) Center (CE)Right (CE) Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Tes; (a) Rev 2.1 - 08/05/2020 Generator U21 Test And Inspect Rep… Stator Winding Insulation Resistance / HV Proof Tests Date 11/01/2020 Generator No.:; Failed test at [kV/Time(sec)] Excitation Voltage (Volts) DC Conditions During HV Proof Test Winding Temperature (oC) Ambient Temperature (oC) 2.) For DC, the test is performed at the end of the DC Leakage Test, use D3162044 | TM2030, TM2050, TM4010, TM4030 | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index ¦ Stator Winding ¦ TM2030 ¦ TM2050 | . Proctor GE Winding Temp.s (ºC ) Resistance (ohms) Ambient Temperature Relative Humidity Comments Date NA Turning Gear Hrs Check per TM4010 8 Point Resistance Check (Optional - Except for 390H and certain 450H & 9A5 units) - TM4010 and TM4030 Factory @25 ºC 0 1 2 3 4 5 6 0 50 100 150 Z(ohms) Applied Voltage (volts) FIELD IMPEDANCE D316303 Sheet: (a) Rev 2.2 - 09/25/2019 Generator U21 Test And Inspect Rep… Stator Winding Insulation Resistance / HV Proof Tests Date 10/29/2020 Generator No.: Prepa
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | b7c350c1442d7cd5ab66d8e74599402f | 164 |  | Mechanical | Stator | Wedge Tightness Test | 3 | Wedge Looseness, Wedge Tightness Test, Wedges | 21 Number of Wedges: |  | Wedge Tightness Test ¦ Wedge Looseness ¦ Wedges | U21 Test And Inspect Report 11_2_ Image65 Image66 Image67 Image68 10/29/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 21 / 337X711 17 Generator U21 Test And Inspect Report 11_2_ Image69 Image70 Image71 Image72 10/29/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 21 / 337X711 18 Generator U21 Test And Inspect Report 11_2_ Image73 Image74 Image75 Image76 10/29/2020 La Frontera Holdings, LLC / Lamar Power Partners Unit 21 / 337X711 19 Generator U21 Test And Inspect Report 1
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 7ae90af7041200838c6b69f6ee74872b | 148 |  | Inspection | Field | Focused Generator Review | 3 | Main Lead, Pole Jumper, Sub-slots | (518) 385‐3178 Generator Specialist Steve Proctor CE RR View of 90 deg turn to turn insulation stack Image 86 CE RR View of 90 deg turn to turn insulation stack Image 87 CE RR View of 90 deg turn to turn insulation stack Image 88 CE RR View |  | Focused Generator Review ¦ Main Lead ¦ Pole Jumper ¦ Sub-slots | . Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor CE RR View of 90 deg turn to turn insulation stack Image 86 CE RR View of 90 deg turn to turn insulation stack Image 87 CE RR View of 90 deg turn to turn insulation stack Image 88 CE RR View of 180 deg main lead goose neck/hardware Image 89 CE RR View opposite side of 180 deg main lead goose neck/hardware Image 90 CE RR View of 180 deg main lead goose neck Image 91 CE RR View of 180 deg main lead stud insulator Image 92 CE RR View o
UNI036594 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425464_FSP-256871_C-10326234.pdf | 297258 | Gas Turbine | 5bc80028fe87ecad55625f97e65af1e6 | 146 |  | Inspection | Stator | Stator Findings Review | 3 | Greasing, Step Iron, Wedges | (518) 385‐3178 Generator Specialist Steve Proctor Location Photo Identification 288 Deg Typical view of TE RR nose Image 01 Slot 35 View of TE end wedge dowel pin Image 02 Slots 36‐38 View of greasing on TE step iron Image 03 Slots 35 ‐ 36 |  | Stator Findings Review ¦ Greasing ¦ Step Iron ¦ Wedges | . 55 Rm. 263 Generator # 337X711 Schenectady, New York 12345 Date 10‐28‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W. Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor Location Photo Identification 288 Deg Typical view of TE RR nose Image 01 Slot 35 View of TE end wedge dowel pin Image 02 Slots 36‐38 View of greasing on TE step iron Image 03 Slots 35 ‐ 36 View of greasing on TE step iron and wedges Image 04 Slot 35 / 288 Deg View of field and stator packages ~126” from CE RR Im
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | 3c8821388a08bccd12eabb64e05fe7f8 | 241 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The outboard oil deflectors on the generator did not show any signs of rubbing and had clearance all around the shaft. |  | Oil Deflector Alignment ¦ Oil Deflectors | . GENERATOR FIELD ALIGNMENT & CLEARANCES OVERVIEW Unit 1 was brought to crank speed on 11/22/2011 and checked for leaks and rubbing after 24+ hrs on turning gear. The turning gear and the collector brushes were in good overall condition when the unit was turning and did not need any adjustment. The outboard oil deflectors on the generator did not show any signs of rubbing and had clearance all around the shaft. There was a slight leak on the lift oil line on T3 that was found where the ½” tubing
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | ad603f16d6011e667575df0f4d96c79d | 33 |  | Inspection | Field, Hydrogen Seals | Focused Generator Review | 2 | Collector Rings, End Shield | 15 Liner Cap, Combustion Assembly Combustion Visual Inspection Good Condition - No Visual Defects 16 Transition Piece, Combustion Assembly Combustion Visual Inspection Good Condition - No Visual Defects 17 Combustion Liner Crossfire Tube Co; 31 Alignment - Coupling Coupling Load & Collector Compartment Alignment Check Alignment Acceptable 37 Body Collector Rings Exciter Visual Inspection Good Condition - No Visual Defects INSPECTION SUMMARY 297490 ODESSA-ECTOR POWER PARTNERS, L |  | Focused Generator Review ¦ Collector Rings ¦ End Shield | . Section Component Location Description: Action: 1 Rotor, Compressor Assembly Rotor Dimensional Checks Ok - Measurements Are Within Tolerance 19 Inlet Guide Vane Assembly Compressor Visual Inspection Good Condition - No Visual Defects 26 Stator Vanes, Compressor Assembly Compressor Stator Visual Inspection Good Condition - No Visual Defects 33 Rotor, Compressor Assembly Compressor Visual Inspection Good Condition - No Visual Defects 2 Clearances - Turbine Assembly Compressor Dimensional Checks
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | 143b167df7f828a271da3028b261c530 | 201 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Bearing Cap Pinch Check Shim Thickness Lead Wire Thickness Interference INSPECTION REPORT Gas Turbine Maintenance g Bearings MS 3002, 5001, 5002, 6001, 7001, 7001F, 9001, 9001F Oil Deflectors, Alignment Date 2011-10-30 Turbine S/N Prepared |  | Oil Deflector Alignment ¦ Oil Deflectors | . The bearing was inspected at the shop with a mandrel and returned to site. The hydraulic oil piping was replaced and the bearing was returned to service. g Bearings MS7001F Twist, Tilt, and Bearing Cap Pinch Check Date 10/22/2011 Turbine S/N Prepared by SHAMSI Data Type Turbine End Collector End X 16.000 OL 0.018 OR 0.018 IL 0.018 Twist 0.001 IR 0.018 Allowable 0.005 0.023 0.023 0.000 0.002 0.010 0.007 -0.003 CLOSE Journal Diameter Twist = (OL-IL+IR-OR)/2 Max Allowable Twist = Journal Diameter
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | b814d623b279a712e3adbdd6b3410c77 | 237 |  | Inspection | Field | Focused Generator Review | 2 | Collector Rings, Fan Blades | Body Collector Rings;Exciter The Collector Rings on the Generator Field were polished by Orbital Machining.; fan blades and shroud were also re centered and checked for rubbing. |  | Focused Generator Review ¦ Collector Rings ¦ Fan Blades | . Final set point reading was taken during early AM hours, and rim and face readings are acceptable. Turning gear alignment was carried out using Optialign laser alignment tool to correct for vertical, horizontal and face. Axial set point was checked moved to achieve a gap of 0.210 inches which is within tolerance; vertical and horizontal moves were made, and turning gear is set within tolerance. GENERATOR ALIGNMENT & CLEARANCES g Alignment MS 3002, 5001, 5002, 6001B, 7001F, 9001E Generator Alig
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | f73b393dd1a301816a01f420bc1cf3a8 | 232 |  | Mechanical | Field | Generator Pressure Test | 2 | Fan Blades, Generator Pressure Test | CE Fan Blades GENERATOR STATOR CE Shield Closeout CE Shield Closeout GENERATOR STATOR Barometric Pressure Gen Stator Temp #4 Hydrogen Casing Pressure Ambient Temperature 11/1/11 0:00 26.89 62.35 0.00 57.68 11/1/11 1:00 26.89 62.47 0.00 56.3 |  | Generator Pressure Test ¦ Fan Blades | . Periodically check float trap drain operation to determine if the unit is operating with high consumption. CE Fan Blades GENERATOR STATOR CE Shield Closeout CE Shield Closeout GENERATOR STATOR Barometric Pressure Gen Stator Temp #4 Hydrogen Casing Pressure Ambient Temperature 11/1/11 0:00 26.89 62.35 0.00 57.68 11/1/11 1:00 26.89 62.47 0.00 56.38 11/1/11 2:00 26.88 62.59 0.00 55.98 11/1/11 3:00 26.87 62.71 0.00 55.62 11/1/11 4:00 26.87 62.82 0.00 55.35 11/1/11 5:00 26.84 62.94 0.00 55.09 11/1/
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | 6b8c25480ca11500c82bdac74c3df96d | 148 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | The LH T2 oil deflectors were found warped and were cut out.; T1 oil deflectors were found in typical condition with some slight oil burn marks.; All new oil deflectors were installed. |  | Oil Deflector Alignment ¦ Oil Deflectors | . T1 lift oil lines were upgraded with the new mod during this inspection. Lift was verified prior to disassembly and on reassembly. A rexroth valve was replaced on T1 for the LS pad. Dial indicators were set up for side movement and it appeared only one pad was getting lift after final assembly. The lift oil hoses were disconnected and lift was verified by connecting the hytorc to the new lift oil hoses. Both pads and hoses were found to be in good condition and it was ruled the issue was at th
UNI036661 | Pleasants County Peaking Power | Field_Service_Report_ProjectID_EV-159640_EVP-538627.pdf | 297784 | Gas Turbine | fed9ebb0fb5e0c1f8db74c0ed9e8f523 | 5 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | Mechanical Scope: 9/15/2025: • Mobilized to site. • LOTO on gas turbine at 1300 for EBI. Labor provided by customer. No APM involvement. • LOTO on generator at 1715. • Took opening clearances on CE outer oil seal. • Remove CE outer oil seal for inspection. • Found frayed wires on TC harness. • Customer will test the bearing and the harness. 9/16/2025: • Customer came in first thing this morning and tested the collector end bearing. • It was determined that the installed TC in the bearing was goo
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1628248_FSP-298346_C-10353097.pdf | 297256 | Gas Turbine | 10fa91a9de85630099bc8a7e888bd154 | 8 |  | Inspection | Stator | Focused Generator Review | 2 | Core, Wedges | NA – Parts were not inspected during this inspection NV – No visible indications / abnormal findings AF – Observed visible / abnormal finding Collector End Components Inspected YES/NO Disposition Peripheral List Below Inspected YES/NO Dispo |  | Focused Generator Review ¦ Core ¦ Wedges | GE Power & Water Inspection & Life Extension Services 1. Foreword This report describes and documents the borescope examination of the unit that is described in the inspection details section listed on page 3; with respect to abnormal depositing, foreign object damage (FOD) and normal wear. A 4.5m X 6.1mm flexible videoscope was utilized for the examination. The interior of the unit was illuminated by employing fiberoptics to transmit light from an external light source. Color images were captur
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1628248_FSP-298346_C-10353097.pdf | 297256 | Gas Turbine | 140f61eb601f86e2eef08c9c61358136 | 2 |  | Inspection | Stator | Stator Findings Review | 2 | End-winding, Loose End-winding Blocking |  |  | Stator Findings Review ¦ End-winding ¦ Loose End-winding Blocking | Table Of Contents 1 Summary __________ 1 1.1 Site Personnel __________ 1 1.2 Executive Summary __________ 1 2 Generator __________ 2 2.1 Field (Rotor)-Borescope Inspection __________ 2 2.1.1 Borescope Inspection. __________ 2 2.1.2 Coil-to-Coil Jumpers/Connectors __________ 24 2.1.3 Pole-to-Pole Jumpers/Connectors __________ 27 2.1.4 Goosenecks/Assemblies __________ 27 2.1.5 Coil Stucks and Coil Insulation __________ 27 2.1.6 End Winding Blocking __________ 27 GE Power Power Services GEGEGE 2972
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1628248_FSP-298346_C-10353097.pdf | 297256 | Gas Turbine | 7746d2f0596bd2f8f637d0aaab1527d7 | 12 |  | Inspection | Field | Focused Generator Review | 2 | Main Lead, Pole Jumper | Inspection Images Section Collector End-Field Sub-Section Field Component Main Lead Location 0 Degree Position Observation Typical Comments Collector_End-Field_ad_0_Degree_Position001.JPG Section Collector End-Field Sub-Section Field Compon |  | Focused Generator Review ¦ Main Lead ¦ Pole Jumper | . Inspection Images Section Collector End-Field Sub-Section Field Component Main Lead Location 0 Degree Position Observation Typical Comments Collector_End-Field_ad_0_Degree_Position001.JPG Section Collector End-Field Sub-Section Field Component Main Lead Location 0 Degree Position Observation Typical Comments Collector_End-Field_ad_0_Degree_Position002.JPG GE Power & Water Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Main Lead Location 0 Degree Po
UNI036591 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1628248_FSP-298346_C-10353097.pdf | 297256 | Gas Turbine | d2032017ed06eeadc032aadd8ede6458 | 21 |  | Inspection | Field | Focused Generator Review | 2 | Pole Jumper, Sub-slots | Section Collector End-Field Sub-Section Field Component Pole Jumper Location 90 Degree Position Observation Typical Comments Collector_End-Fiel__90_Degree_Position02002.JPG GE Power & Water Inspection & Life Extension Services Section Colle |  | Focused Generator Review ¦ Pole Jumper ¦ Sub-slots | Section Collector End-Field Sub-Section Field Component Pole Jumper Location 90 Degree Position Observation Typical Comments Collector_End-Fiel__90_Degree_Position02002.JPG GE Power & Water Inspection & Life Extension Services Section Collector End-Field Sub-Section Field Component Pole Jumper Location 270 Degree Position Observation Typical Comments Collector_End-Fiel_270_Degree_Position02001.JPG Section Collector End-Field Sub-Section Field Component Pole Jumper Location 270 Degree Position Ob
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 698aaa25a7087f14c4add2b21647d123 | 13 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | T1 aft oil seal was returned to service · All bearing oil deflectors were replaced with undersized oil deflector to match rotor undersized condition. | FMI F6291G25, FMI G62921G24 | Oil Deflector Alignment ¦ Oil Deflectors ¦ FMI F6291G25 ¦ FMI G62921G24 | back with GE specification. · Performed visual inspection of stator vanes per ETC 147. All stator damaged stator vanes were replaced with new vanes. · Removed, visually inspected, cleaned, and reinstalled following UH cases: mid- compressor, compressor discharge, and inner barrel Combustion: · Removed, visually inspected, and replaced all TPs as per FMI F6291G25 · Removed, visually inspected, and replaced all combustion liners, inner and outer crossfire tubes as per FMI F6291G25 · Removed, visua
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 090f06945fe421ac90f427734068842e | 171 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Both T2 oil deflectors were replace with new parts (PNs 188D7278G003 and 188C9483G003) due to underside journal at location of the following:; Going forward, recommend site use these PNs to order new T2 oil deflectors.; Clearances were tight on the left side of the oil deflectors as well as in the HGP section warranting a laser alignment check of the bearing placement.; N/A Both oil deflectors were replaceded due to underside journal.; 4/16/2020 inches 297493 FieldCore Team New oil deflectors C C B B A A D309104 Sheet: |  | Oil Deflector Alignment ¦ Oil Deflectors | Part Description: A visual inspection was performed on T2 bearing following turbine rotor removal. It was found with minimal wear. A none destructive test was conducted by site’s third-party vendor, site reported NDT indicated no abnormal conditions were found. T2 bearing was returned to service. T2 bearing floating oil seals were found to be in a distressed state. Numerous scored were found on both oil seal, both oil seals were replaced with new parts from site’s inventory. Both T2 oil deflecto
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 3d1a1024f00fed74ecdc45245b4ee6a3 | 17 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | Going forward, recommend site use these PNs to order new T2 oil deflectors.; Clearances were tight on the left side of the oil deflectors as well as in the HGP section warranting a laser alignment check of the bearing placement. |  | Oil Deflector Alignment ¦ Oil Deflectors | Next Outage Parts Normally PNs for T2 bearing are as follow: 188D7278G001 and 188C9483G001. However, due to underside journal the new PNs for oil deflector are 188D7278G003 and 188C9483G003. Going forward, recommend site use these PNs to order new T2 oil deflectors. It is recommended to perform an internal alignment during the next major. Clearances were tight on the left side of the oil deflectors as well as in the HGP section warranting a laser alignment check of the bearing placement. This sh
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | c67b92c4e5c1a3f9eb03da666440c353 | 54 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors | All oil deflectors and air seal were replaced with new except for 1S3 due to underside journal at locations of the following:; oil deflectors 1S1, 1S4, and 1S5 (18.477”), and air deflector 1S6 (21.477”) Lift oil line hoses for T1 bearing were replace during this outage. | EM5260 | Oil Deflector Alignment ¦ Oil Deflectors ¦ EM5260 | Part Condition: Fair Part Description: A visual inspection was performed on T1 bearing following turbine rotor removal. It was found with minimal wear. The wear patterns are typical of central align journal. No visual crack was found. None destructive test was conducted by customer third party vendor. T1 bearing was returned to service. T1 bearing oil seals were removed, cleaned, and visually inspected. No abnormal condition was found on aft oil seal (1S10) and deem acceptable for continue opera
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 1265808e8fa236373308c06e7269045a | 59 |  | Mechanical | Hydrogen Seals | Oil Deflector Alignment | 2 | Oil Deflector Alignment, Oil Deflectors |  |  | Oil Deflector Alignment ¦ Oil Deflectors | . Particle UT Ultrasonic PT Penetrant Location Oil Rings Journal Clearance Condition Number A-Dia B-Dia C-Dia Dia Average Min. Max. Comment 1S1 (Fwd.) 18.529 18.529 18.533 18.477 0.053 0.052 0.056 New 1S2 (Fwd.) 18.520 18.534 18.533 18.477 0.052 0.043 0.057 New 1WF1 (Fwd.) 17.535 17.527 17.540 17.477 0.057 0.050 0.063 1S3 (Mid-Fwd.) 1S4 (Mid-Aft) 18.535 18.521 18.530 18.477 0.052 0.044 0.058 New 1S5 (Mid-Aft) 18.534 18.527 18.531 18.477 0.054 0.050 0.057 New 1S6 (Aft) 21.536 21.517 21.542 21.477
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 45be847c48e55fff0a0abc3078e51ff0 | 9 |  | Inspection | Hydrogen Seals | Focused Generator Review | 2 | End Shield, Hydrogen Seal Assembly | Planned Outage Turbine Hot Gas Path Inspection, Compressor Section Generator Minor (rotor in), End Shield(s) Off, Hydrogen Seals, Bearings |  | Focused Generator Review ¦ End Shield ¦ Hydrogen Seal Assembly | Outage Type: Planned Outage Turbine Hot Gas Path Inspection, Compressor Section Generator Minor (rotor in), End Shield(s) Off, Hydrogen Seals, Bearings
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 71aaa97fb6e98495f905052c5e09d5c6 | 234 |  | Electrical |  | Polarization Index; DC Leakage | 2 | DC Leakage, Polarization Index | (a) Rev 1.1 - 03/28/13 GE Energy Proprietary Information g Armature Insulation DC Leakage Test Date(m/d/y) 11/4/2020 Generator Serial No. |  | Polarization Index; DC Leakage ¦ DC Leakage ¦ Polarization Index | . Manufacture GE FSR No. A 15 KV DC voltage was applied to each phase with the other two phases grounded for a period of 10 minutes. Readings were recorded at specific time intervals. On the basis of these readings a time schedule is established for reading stabilized leakage currents at successively higher voltage values up to a maximum value, approximately twice line-to-line voltage. The current readings are plotted as a function of voltage to determine if a nearly linear relationship exists,
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | c60e24fb6be4fec4b8013eb29d64c708 | 199 |  | Inspection | Field | Focused Generator Review | 2 | Pole Jumper, Sub-slots | (518) 385‐3178 Generator Specialist Steve Proctor CE RR Second view of 180 deg coil to coil jumper, 4-5 Image 87 CE RR Third view of 180 deg coil to coil jumper, 4-5 Image 88 CE RR View of 270 deg pole to pole jumper Image 89 CE RR View of |  | Focused Generator Review ¦ Pole Jumper ¦ Sub-slots | . 263 Generator # 337X710 Schenectady, New York 12345 Date 11‐03‐2020 Office: (518) 385‐1751, 8*235‐1751 Operator W.Howard Fax: (518) 385‐3178 Generator Specialist Steve Proctor CE RR Second view of 180 deg coil to coil jumper, 4-5 Image 87 CE RR Third view of 180 deg coil to coil jumper, 4-5 Image 88 CE RR View of 270 deg pole to pole jumper Image 89 CE RR View of 270 deg pole to pole jumper minor deformation Image 90 CE RR Third View of 270 deg pole to pole jumper Image 91 CE RR View of 270 de
UNI036596 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425468_FSP-256875_C-10326237.pdf | 270T435 | Steam Turbine | 8ca89b99af9786f71957a4978dc0de44 | 6 |  | Inspection | Hydrogen Seals | MAGIC Inspection | 2 | End Shield, MAGIC Inspection | FieldCore also performed a MAGIC inspection and required generator testing.; *Generator Magic Inspection (performed on 11/5/2020).; A magic inspection consisted of a full visual inspection of the generator stator and field components and a complete set of electrical tests.; The magic inspection had been conducted from CE only as the TE End shield was not removed during this outage. |  | MAGIC Inspection ¦ End Shield | FieldCore team was mobilized and arrived on site to commence ST-20 D11 steam turbine minor inspection and technical direction for MSCV replacement on October 22, 2020. FieldCore also performed a MAGIC inspection and required generator testing. In addition, Bently Nevada was mobilized for vibration analysis during startup. Finally, a FieldCore controls engineer was mobilized for valve calibration post assembly. Vinson was contracted for LP Admission Stop and Control valve rebuilds. The planned wo
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_Support_of_Major_Inspection_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-01 | 297490 | Gas Turbine | 003dd0ef31495e5f3363290c4be8a827 | 12 |  | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection | ENCLOSURES Generator Auxiliary Equipment Leads;Load Equipment The flex leads were disconnected from the primary and neutral bus for generator testing and magic inspection. |  | MAGIC Inspection | . For additional information on the gas stop ratio and control valve, refer to the Service Manual under the Fuel System tab. RECOMMENDATIONS Item InsRec PU RI QTY UM PartsDescription CustStk Catalog Drawing 1 7 X 3 EA Mark V Control,39v-t Vib Sensor (seismic) Tur,Turbine Bearing #2 G0415 329A3529P029 2 8 X 1 EA Mark V Control,39v-g Vib Sensor (seismic) Gen,Generator Brg # 3 G0440 329A3529 3 14 X 2 EA Mark V Control,26qt Lube Oil Header Temp,Accessory Module G0416 363A5545 4 26 X 2 EA Mark V Cont
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | ed9fba2db92d6a3b748b162009709a18 | 36 |  | Inspection | Hydrogen Seals | Focused Generator Review | 1 | End Shield | RECOMMENDATIONS 297490 ODESSA-ECTOR POWER PARTNERS, LP Page No 34 Item InsRec PU RI RO QTY UM PartsDescription CustStk Catalog Drawing 1 3 X 92 GT1 Bucket, 1st Stage,Assembly,Turbine Set K G1307 109E9918P001 2 4 X 1 297490 Bucket, 2nd Stage |  | Focused Generator Review ¦ End Shield | . 9. Bucket, 1st Stage;Assembly;Turbine Inspect Buckets during borescope inspections to determine if damage becomes significant. RECOMMENDATIONS 297490 ODESSA-ECTOR POWER PARTNERS, LP Page No 34 Item InsRec PU RI RO QTY UM PartsDescription CustStk Catalog Drawing 1 3 X 92 GT1 Bucket, 1st Stage,Assembly,Turbine Set K G1307 109E9918P001 2 4 X 1 297490 Bucket, 2nd Stage,Assembly,Turbine N/A G1308 353B3024G001 3 5 X 14 297490 Fuel Nozzle,Assembly,Combustion N/A G0513 114E5657G009 4 6 X 92 297490 Buc
UNI036545 | ODESSA ECTOR POWER PLANT | GAS_TURBINE_INSPECTION_REPORT_GT1_Major_Inspection_and_Generator_MAGIC_for_ODESSA-ECTOR_POWER_PARTNERS_LP_Odessa-Ector_Facility_Unit_GT1_Gas_Turbine_297490_2011-10-03 | 297490 | Gas Turbine | e8b154aca7cf3fdeecf3353abef3deef | 207 |  | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Hydrogen Seal Assembly |  |  | Focused Generator Review ¦ Hydrogen Seal Assembly | . The wires were checked for functionality and the unit was returned to service. NOTE: Due to re-routing of the TC wires, re-order TC’s with extra-long (75’+) wires. TC Marshalling Box TC Routing TC Routing Piping/Components (WJ) Connector;Inlet The Water Wash adapter from the header to the nozzle was found cracked and needed replacement. The system was checked for further damage, but none was found. The unit was then returned to service Change out the water wash fittings to ensure they do not l
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | f3015c6a9de40428a35df6e37266e98d | 111 |  | Inspection | Stator | Focused Generator Review | 1 | Wedges | Making alignment side move GENERATOR ALIGNMENT & CLEARANCES Runout with wedges installed between coupling faces GENERATOR ALIGNMENT & CLEARANCES Inlet Filter House Assembly; |  | Focused Generator Review ¦ Wedges | . Load coupling face cleaned prior to rotor install COUPLINGS Coupling MS 7001, 7001F, 9001 Load Date 12/7/2011 Turbine S/N Prepared by C. Helget FSR # Sketches Enclosed? No Photos Enclosed? Yes Data Type Final Vendor Serial # GE Part # COUPLING RUNOUT READINGS COUPLING INTERFERENCE FIT DIMENSIONS Turbine End Generator End Turbine End Generator End Rim (A) Face (B) Rim (C) Face (D) Male Dimension 18.301 NA 0.000 0.000 0.000 0.000 Female Dimension 18.295 NA Fit -0.006 #VALUE! COUPLING BOLT ELONGA
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | e8051d984b20413511c2997c40c876c9 | 19 |  | Inspection | Stator | Focused Generator Review | 1 | Keybars |  |  | Focused Generator Review ¦ Keybars | 14 1 Transition Piece Hardware,Assembly,Bullhorn Lockplate G0717 318A9872P002 121 13 X 14 1 Transition Piece, Combustion,Assembly,Transition Pieces G0702 141E8402G003 122 15 X 4 1 Casing, Compressor Discharge,Assembly,R17 Clearance Pins G0805 239B9719P007 123 15 X 12 1 Casing, Compressor Discharge,Assembly,Stage 14, 15, 16 Murphy Pins G0805 268B4236P001 PARTS USED & RECOMMENDED PU=Part Used During the Inspection RI=Part Recommended for Immediate Restock RO=Part Recommended for the Next Inspectio
UNI036480 | Moss Landing | GAS_TURBINE_INSPECTION_REPORT_Forced_Major_Inspection_for_DYNEGY_MOSS_LANDING_LLC_Moss_Landing_Unit_GT1_Gas_Turbine_297602_2011-10-31 | 297602 | Gas Turbine | f4797dcdba166a11b003e668d32a5a0e | 145 |  | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Bearing seal rings were sent out with the bearings and re-babbited as well. |  | Focused Generator Review ¦ Seal Rings | . The flex seals and exhaust cone rope seal was replaced. The graphite/steel gasket was also replaced in case a balance shot would be required through the S3 exhaust cone window. During disassembly of the T2 bearing conduit down the exhaust tunnel it was noted multiple insulation support studs were broken off. New material was ordered and the studs welded in place. During final assembly the aft exhaust vertical face and exhaust tunnel hatch locktabs were tack welded in place. Visually inspect fl
UNI035720 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_Fairless_Energy_Fall_2011_Enhanced_Borescope_Inspection_for_DOMINION_ENERGY_Fairless_Unit_298177178235236_Gas_Turbine_298178_2011-10-24 | 298178 | Gas Turbine | 4a9593bc85db3943597461f87c028292 | 19 |  | Inspection | Field | Focused Generator Review | 1 | Collector Rings | This need to be correct per drawing 121E4048 (The collector brushes should ride fully on the collector rings.; On S2, unit was on turning gear during inspection and the brushes were riding fully on collector rings (unit may not cool down completely, so position of collector rings may move toward generator slightly more) -Follow GEK35474 for brush ri | GEK35474 | Focused Generator Review ¦ Collector Rings ¦ GEK35474 | . Continue to adhere to valve maintenance intervals as described in the service manual and applicable unit fuel system GEK's. GAS FUEL SYSTEM Excitation System System; The excitation systems on S1 and S2 were inspected. Customer was experiencing conduction alarms and an excitation engineer was brought on site to troubleshoot accordingly. Please see attached report for details of the inspections and recommendations. EXCITATION SYSTEM S1 and S2 EX2100 De-Excitation Conduction Alarm Troubleshooting
UNI035720 | FAIRLESS ENERGY CENTER | GAS_TURBINE_INSPECTION_REPORT_Fairless_Energy_Fall_2011_Enhanced_Borescope_Inspection_for_DOMINION_ENERGY_Fairless_Unit_298177178235236_Gas_Turbine_298178_2011-10-24 | 298178 | Gas Turbine | 5d59f4e08e5c28c385bb729de57ba592 | 23 |  | Inspection | Field | Focused Generator Review | 1 | Collector Rings |  |  | Focused Generator Review ¦ Collector Rings | . Recommendation would be replace current EXAM board with IS200EXAMG1BAA or latest (This only apply to S1 and S2 EX2100). -Site is aware that ACLA boards in EX2100 are obsolescence. TB25030 recommends upgrade to ACLE (this upgrade will need to be whole plane, 2 ACLE boards will be required for each EX2100 upgrade) -TB25009 Failure of 3 legged capacitors due to moisture influx through the epoxy seal of the third leg that in turn makes the positive and negative leads short together, resulting in a
UNI035720 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1749044_EV-139338.pdf | 298178 | Gas Turbine | 0fcd3581606828c0db4f09fbc4957dd0 | 10 |  | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Next Outage Services All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted.
UNI035720 | FAIRLESS ENERGY CENTER | Field_Service_Report_ProjectID_A-1749044_EV-139338.pdf | 298178 | Gas Turbine | f204fa1a34c1fc71b2ae75a0badfcaf6 | 22 |  | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings | All flow sleeves should be inspected during the next scheduled outage, also seal rings should be replaced if excessive wear is noted. |  | Focused Generator Review ¦ Seal Rings | Part Condition: Fair Part Description: The removed flow sleeves were inspected for any signs of hot spots, crack indications, or excessive wear. Slight wear was noted, on the liner stops and cross fire tube retaining clip engagements. The spring seals were checked for lift and inspected for any missing tines. No excessive lift or missing tines were noted. The flow sleeve ring seals at the aft end were found to have steps in the surface due to wear. New floating seals were provided and installed
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | b3f4e85269498bfa8bb55dd5cddb608a | 92 |  | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  | FMI F6291G25 | Focused Generator Review ¦ Retaining Rings ¦ FMI F6291G25 | Part Condition: Fair Part Description: As part of the FMI F6291G25, all combustion fuel nozzles, and replaced with a new set of GEs DLN 2.6+ fuel nozzle with new hardware and gasket. No unusual conditions were found on any removed fuel nozzle. Light carbon built up was observed. No indication of burn nozzle was noticed. CBM: Non CBM Typical as-found conndition of removed fuel nozzle New DLN 2.6+ fuel nozzle Typical view of new gasket installed on FWD can g Combustion MS 7001FA, 7001FA+, 7001FA+e
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 795e0c3fe01c319828ae4b9911621a46 | 12 |  | Inspection |  | MAGIC Inspection | 1 | MAGIC Inspection |  | FMI F6291G25 | MAGIC Inspection ¦ FMI F6291G25 | On March 30, 2020 FieldCore performed a Major Inspection on Block 2, Unit 4, SN 297493, at Luminant, Odessa Ector Power Plant in Odessa, TX. Work Scope included a Rotor Swap Major Inspection with Advance Hot Gas Path and DLN 2.6+ upgrades under GE Field Modified Instruction (FMI F6291G25), MAGIC Jr Inspection (Miniature Air Gap Inspection), and Electrical Testing on Generator with SN 338X155. FieldCore provided project management, Field Engineers, Craft Manpower, and Electrical Manpower for enti
UNI036549 | ODESSA ECTOR POWER PLANT | Field_Service_Report_ProjectID_A-1505048_FSP-253386_C-10323897.pdf | 297493 | Gas Turbine | 8cce0b6cb250ea52fdf24465a8d47526 | 87 |  | Inspection | Hydrogen Seals | Focused Generator Review | 1 | Seal Rings |  | FMI F6291F25, FMI F6291G25 | Focused Generator Review ¦ Seal Rings ¦ FMI F6291F25 ¦ FMI F6291G25 | Part Condition: Fair Part Description: As part of the FMI F6291F25, all combustion aft cans and flow sleeves were removed, visually inspected, and replaced with new set of GEs DLN 2.6+ aft can and flow sleeve. DLN 2.6+ upgrade required new flow sleeve to be pre-installed on top of the aft can as one unit and then the whole unit is installed on each of the combustion chamber. No abnormal conditions were found on any removed combustion aft can and flow sleeve. CBM: Non CBM Typical condition of rem
UNI036595 | LAMAR POWER PARTNERS | Field_Service_Report_ProjectID_A-1425758_FSP-256873_C-10326236.pdf | 297257 | Gas Turbine | 4838aa608859e0a597965cf8462bcf50 | 140 |  | Inspection | Field | Focused Generator Review | 1 | Retaining Rings |  |  | Focused Generator Review ¦ Retaining Rings | . See the attached data sheet. All clearances were sent to PAC and the customer representative for review. All were accepted. g Turbine Equip Code: 7FA.04 Turbine Rotor Clearances Date: 11/5/2020 Turbine S/N: 297257 Prepared by: ERP Job #: As Found Clearance Drw: 100T8575 Units of Measure: Inches As Left Clearance Drw: 100T8575 Rotor Trusted Toward: Exhaust OPENING CLOSING OPENING CLOSING Left Right Left Right Left Right Left Right A SET 1.916 1.918 2F2 0.390 0.392 0.388 0.447 1F2 0.184 0.188 0.

## Summary
Metric | Value
Trains Analyzed | 51
Train IDs | UNI000885, UNI000886, UNI026365, UNI026366, UNI026367, UNI026368, UNI035717, UNI035718, UNI035720, UNI035721, UNI035727, UNI035728, UNI035747, UNI035748, UNI035749, UNI035751, UNI035752, UNI035753, UNI035961, UNI035962, UNI035964, UNI035965, UNI036147, UNI036149, UNI036151, UNI036153, UNI036241, UNI036242, UNI036334, UNI036335, UNI036336, UNI036480, UNI036481, UNI036482, UNI036483, UNI036484, UNI036485, UNI036545, UNI036546, UNI036548, UNI036549, UNI036591, UNI036592, UNI036593, UNI036594, UNI036595, UNI036596, UNI036661, UNI036662, UNI037112, UNI037113
Seed ESNs | 337X750, 337X751, 337X752, 337X753, 337X757, 337X758, 337X759, 337X760, 337X053, 337X063, 337X009, 337X008, 337X003, 337X007, 338X725, 338X726, 338X727, 338X728, 337X767, 337X768, 338X731, 338X732, 337X165, 337X166, 337X236, 337X259, 337X260, 337X261, 337X262, 337X263, 337X708, 337X709, 337X710, 337X711, 337X152, 337X153, 337X154, 337X155, 337X185, 337X186, 338X743, 338X738, 338X737, 338X742, 290T483, 290T484, 290T432, 290T260, 290T259, 290T434, 290T435
Total ESNs Resolved | 102
Unique PDFs Scanned | 310
Metadata Gaps Found | 252
Confirmed by Keyword | 47
Unconfirmed (GT-only reports) | 205
Events Matched by Date | 179
Generator Scope Candidate Chunks | 515
Generator Scope Candidate PDFs | 77