## Sheet1
equipment_type | technology_group | technology | component | Persona | issue_grouping | issue_name | issue_prompt | severity_criteria_0_no_data | severity_criteria_1_light | severity_criteria_2_medium | severity_criteria_3_heavy | severity_criteria_4_immediate | applicable_data_objects
GEN | Hydrogen Cooled |  | Rotor | REL | Electrical Tests | IR, PI | Are there any valid Insulation Resistance (IR), Polarization Index (PI) test results for the rotor (aka field)? If yes, please classify per the FM Severity criteria. Note: For IR results, only use 10 min. Field IR, PI results are usually found on form D316303 | No Results / Test Not Performed | IR > 4000 Megohms AND PI > 1 | 4000 Megohms >= X > 25 Megohms AND PI > 1 | IR <= 25 Megohms OR PI <= 1 | IR = 0 OR Could not hold voltage OR field is grounded | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Electrical Tests | Winding resistance | Are there any valid Winding resistance test results for the Field / Rotor? If yes, please classify the results per the FM Severity criteria. Note: Field winding resistance results are usually found on form D316303 | No Results / Test Not Performed | within +/-2% factory test result OR within +/-1% previous test result | Not Applicable | at or outside +/-2% factory test result OR at or outside +/-1% previous test result. | Clear evidence of Open Circuit, i.e. there is a dis-connection in the winding circuit, so no current will flow in the test | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Shorted Turns | Gen Field Excitation Fleet | What is the Excitation Delta Max Val Ratio for this unit? | No Data | Excitation Delta Max Val Ratio < 1.01 | 1.01 < Excitation Delta Max Val Ratio < 1.05 | Excitation Delta Max Val Ratio > 1.05 | n/a | ACP Analytic, Time Series Data
GEN | Hydrogen Cooled |  | Rotor | REL | Shorted Turns | Shorted Turns | Are there any definitive statements about the presence of shorts or shorted turns in the rotor winding? Information also comes from RSO testing (Recurrent Surge Oscillograph) or flux probe testing. Do not aggregate shorted turns counts across different tests. Only flux probe and RSO can definitively confirm 0 shorted turns. | Not mentioned | 0 Shorts | Evidence of 1 to 3 shorts | 4 shorts or more or evidence of multiple shorts | Not Applicable
GEN | Hydrogen Cooled |  | Rotor | REL |  | Vibration | Does the unit exhibit signs of thermal sensitivity? | No Data | <3 mils AND no signs of thermal sensitivity (< 1 mil variation with excitation current and steady MW) | 1-3mils AND >1 mil variation with excitation current and steady MW (derived from GER3809). | 3mils-6mils AND >1 mil variation with excitation current and steady MW (derived from GER3809). Determined thermally sensitive (from test instruction 503HA212) | ≥ Alarm limits (> 6 mils steady state or >7.5 or 9 mils transient, depending on unit) | Time Series Data
GEN | Hydrogen Cooled |  | Rotor | REL |  | Thermal Sensitivity Test | Was a thermal sensitivity test performed? If yes, please classify the results per the FM Severity criteria. | No Results / Test Not Performed | Evidence of Test with result as pass | Not Applicable | Evidence of Test with result as failure | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | Ventilation hole blocking (migration of slot components) | Was this unit evaluated for migration, aka movement, or ventilation hole blocking? Migration must be related to ventilation hole blocking. Ventilation hole blocking related components include Creepage Blocks, Turn Insulation, Ammortisseur, Leaf Spring, Subslot Cover | Not mentioned at all or not inspected | minor migration AND ventilation hole blocking OR a definitive statement of no migration or ventillation hole blocking | moderate migration AND ventilation hole blocking | Severe or extensive migration AND ventilation hole blocking | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | Turn to turn insulation migration | Was this unit evaluated for signs of turn to turn insulation migration or movement? Migration must be related to the turn to turn isulation, do not include migration of other rotor components | Not mentioned at all or not inspected | definitive statement of no migration | Any observations but not stated as severe or heavy | Noted as severe or heavy, OR > 5 pieces migrated | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | Slot armour migration/damage/cracking | Was this unit evaluated for signs of slot armour migration (aka movement) or damage or cracking? Migration must be related to the slot armour or subslot cover, do not include migration of other rotor components | Not mentioned at all or not inspected | definitive statement of no migration | evidence of slot armor fatigue or movement | Evidence of cracking or significant movement. Signs of shortened creepage distance to ground. | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Migration Issues | EW support blocking migration (end winding) | Was this unit evaluated for any signs of Rotor End Winding (EW) support blocking migration or movement? Migration must be related to the rotor support blocking, do not include migration of other rotor components. Do not include observations from stator end winding. | Not mentioned at all or not inspected | definitive statement of no migration related to rotor support blocking | evidence of migration related to rotor support blocking | Blocks missing or signifcantly moved. Noted as heavy or severe. | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | MTS leaves cracking/distortion (Main Terminal Stud aka goose neck) | Was this unit evaluated for any Main Terminal Stud (MTS) distortion or any MTS leaves cracked? Distortion or cracking must be related to the Main Terminal Stud (MTS). Do not include distortion or cracking of other rotor components. MTS may also be referred to as Main Lead or gooseneck. | Not mentioned at all or not inspected | definitive statement of no cracking or distortion OR cracking or distortion noted on ≤ 2 leaves | Cracking or distortion noted in 3 or 4 leaves | Cracking or distrotion noted on ≥ 5 leaves. | Over half the package cracked. | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | MTS/bore copper contact (Main Terminal Stud aka goose neck) | Was this unit evaluated for any signs of contact or rubbing between the bore copper and the Main Terminal Stud (MTS)? This would include any "copper dust" or flakes present where the MTS screws into the forging. MTS may also be referred to as Main Lead or gooseneck. | Not mentioned at all or not inspected | Definitive statement of no signs of MTS contacting the bore copper | Any observations that were addressed with retightening, and no evidence of subsequent observations | Observed or Copper dust or flakes present where the MTS screws into the forging. | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | Pole to pole connector cracking/distortion | Was this unit evaluated for any signs of pole to pole connector cracking or distortion? Distortion or cracking must be related to the pole to pole connector / jumper. Do not include distortion or cracking of other rotor components. | Not mentioned at all or not inspected | Signs of distortion or fatigue, but no cracks or minor cracks OR a definitive statement of no damage. | Flexible connector that has one or two leaves cracked all the way through (also called laminations) | Flexible connector with more than 2 leaves cracked all the way through , OR a solid connector that is partially cracked | A solid connector cracked all the way through, OR a flexible connector with the majority of leaves cracked all the way through | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL | Connection Issues | Coil to coil connection cracking/distortion | Was this unit evaluated for any signs of coil to coil connector cracking or distortion? Distortion or cracking must be related to the coil to coil connector / jumper. Do not include distortion or cracking of other rotor components. | Not mentioned at all or not inspected | Signs of distortion or fatigue, but no cracks or minor cracks OR a definitive statement of no damage. | Flexible connector that has one or two leaves cracked all the way through (also called laminations) | Flexible connector with more than 2 leaves cracked all the way through , OR a solid connector that is partially cracked | A solid connector cracked all the way through, OR a flexible connector with the majority of leaves cracked all the way through | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | EW distortion | Was this unit evaluated for any signs of End Winding (EW) distortion in the coil or copper? Distortion of insulation should be ignored. | Not mentioned at all or not inspected | no distortion | Minor distortion | Extensive or heavy distortion noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | Retaining ring insulation damage | Was this unit evaluated for retaining ring insulation damage? | Not mentioned at all or not inspected | no damage | Minor damage | Extensive or heavy damage noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | Contamination | Was this unit evaluated for signs of rotor / field contamination? Do not include any observations of stator contamination. | Not mentioned at all or not inspected | light contamination noted OR a definitive statement of no contamination | Medium or unquantified contamination | Extensive or heavy contamination noted | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Rotor | REL |  | FOD (Foreign Object Damage) | Was this unit evaluated for Foreign Object Damage (FOD) indications on the rotor / field, excluding steam turbine rotor findings, bearings, and other non-rotor generator hardware? | Not mentioned at all or not inspected | definitive statement of no FOD during the test | Any evidence of FOD damage | Extensive or heavy FOD damage noted | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | DC leakage | Is there an issue with stator winding DC leakage test results? DC Leakage results are typically reported on form D3162044 | not performed or not mentioned | Zone A or all values provided at 36KV show mA < 7 | Zone B OR any phases with mA >7 at 36KV OR test was performed but no values reported at 36KV | Zone C for more than 1 phase, OR a more than 1 phase with mA >13 at 36KV | Zone C for 1 phase only, OR only 1 phase with mA >13 at 36KV | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | DC Hipot (Optional/rare, and Secondary to DC Leakage) | Were DC Hipot measurements taken, and if so what were the results? Hipot results are typically reported on form D3162044. Note: It will be common for there to be No Data for this issue. Unless there is an explicit mention of Hipot results, or leakage results (in mA column) for a row where value in KV column is > 36, then the result should be No Data | not performed or not mentioned | Zone A or hipot results < 9 mA for all phases | Zone B or the phase with the highest mA value is between 9 and 17 mA | Zone C for more than 1 phase, or more than one phase has value > 17 mA | Zone C for only 1 phase only, or only one phase > 17 mA | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | IR, PI | Is there an issue with the insulation resistance and/or the polarization index test (IR, PI Test) results for the stator? Only use results related to this test for the stator (aka armature). Stator IR, PI results are typically documented on form D3162043 | not performed or not mentioned | Pass or an explicit statement of acceptable results | Decreasing Trend or close to the limit | Fail for more than 1 phase | Fail for exactly 1 phase | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Electrical Tests | Winding resistance | Is there an issue with the Stator winding resistance test (aka DLRO test)? Only use information for the winding resistance test for the stator (aka armature), typically found on form D3162041 | not performed or not mentioned | Pass All Rules or an explicit statement of acceptable results | Pass Rule 1, but Fail 2 and/or 3/4. | n/a | Fail Rule 1 | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Corona | Slot Corona Activity (Can see in end of slots only) | Is there any corona damage in the slot area? Corona must be described as being in the slot, at the end of the slot, or in the step iron region. "Corona" or "Partial Discharge" must be mentioned in evidence and inspections, do not associate other observations in slot area to slot corona activity. | No inspection of the slots occurred, or no mention of the stator slots at all. | Definitive statement that no slot corona activty was observed during slot corona inspections. | Any Slot Corona activity is observed | Slot corona activity is stated as heavy | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Corona | End winding Corona Activity | Is there any corona damage in the end winding area or at phase breaks? Do not include corona in the slot. Do not include corona at the end of the slot. Do not include corona in the step iron region. "Corona" or "Partial Discharge" must be mentioned in evidence and inspections, do not associate with other observations in the end-winding to end winding corona activity. | Not mentioned | Definitive statement that no end winding corona was observed during end winding corona inspection | Any End Winding Corona activity is observed | End Winding Corona activity is stated as Heavy | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | Dusting or Greasing at the ends of the stator slots. | Are there signs of greasing or dusting at the ends of the stator slots or in the core OR any signs of side ripple spring (SRS) migration? Dusting or greasing must be related to the stator slots or stator core or step iron. Do not include dusting/greasing at other parts of the generator. | Not mentioned | stated as minor/light or definitive statement of not present | Stated as medium or moderate. Mentioned but not called light / minor. AND DC Leakage is still zone A | Stated as Heavy or major or extreme. OR any signs of Side Ripple Spring (SRS) migration or SRS digging into a bar. OR Mentioned and DC leakage is zone B or C | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | Connection Ring (CR) dusting or greasing | Are there any observations of greasing or dusting at the connection ring (CR)? Note: Replacement of blocks and ties would reduce severity to Medium until a subsequent outage observation overrides with a new disposition. Dusting or greasing must be related to the connection rings. Do not include dusting/greasing at other parts of the generator. | Not mentioned | Definitive statement of not present or noted as minor or light. If minor or light, cleaning and repair required to remain light | Stated as medium. Cleaning and repair required and will stay medium until reviewed again at the next outage | Stated as heavy. Cleaning and repair required to change to medium. If no repairs are made, the risk remains heavy. | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | End Winding (EW) dusting or greasing | Is there moderate to heavy greasing or dusting at End winding (EW)? Note: Replacement of blocks and ties would reduce severity to Medium until a subsequent outage observation overrides with a new disposition. Do not include dusting/greasing on the connection rings or at the stator slots or core. Stator endwinding related components include Stator Bars End Arms, Binding Bands, Radial Rings and Axial Supports | Not mentioned | definitive statement of not present or noted as minor or light. If minor or light, cleaning and repair required to remain light | Stated as medium. Cleaning and repair required and will stay medium until reviewed again at the next outage | Stated as heavy. Cleaning and repair required to change to medium. If no repairs are made, the risk remains heavy. | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Dusting / Greasing | Oil ingress | Is there indications of greasing or oil present within the generator stator or core? | Not mentioned. | oil or greasing noted, and stated as light. OR Dusting mentioned but no mention of greasing. | Oil or Greasing noted, but stated as moderate or not quantified. | Heavy oil ingress or severe greasing noted. Mention of oil in bushings. Phrases like "pools of oil" or "heavily soaked with oil" or "Pockets of oil". Liquid level detector or belly alarm. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Stator slot wedge tightness | Is there any indication of stator slot wedge looseness or are there any stator slot wedge assessment results? Note: A rewedge or tightening of wedges WILL immediately reset this condition to Light (severity 1) | Not mentioned | Pass | Fail - Partial rewedge or wedge tightening or shimming | Fail - Full rewedge | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Winding Connection Failure (Phase Connection /Series Loop) | Are there any indications of winding connection failure? Winding connection related components include Phase Connections, Phase Straps, Phase Backset , Series Loops, Series Caps | Not mentioned | Not present, no indication, pass copper resistance test, no M&D alarm | Any form of dust/greasing but not stated as heavy. Requires cleaning/repairs to remain medium until reviewed again at the next outage. | Heavy dusting/greasing or signs of movement or failed Copper resistance test or M&D alarm. Heavy dusting/greasing needs cleaning/repairs to change to medium. If no repairs are made, the risk remains heavy. | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Stator core looseness (or low tightness, not tight) | Are there any signs of stator core looseness or any knife test results? Ignore Stator Wedge Assessement or "tap test" results for this issue. Note: This Issue does NOT reset with Stator Rewind. | not mentioned | Passed knife test OR unit stated as tight | Previous signs of looseness that were addressed with tightening | Failed knife test or signs of looseness in core laminations or greasing between laminations | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | High Stator Bar Temps | Has the unit had ER cases related to elevated bar temperatures as observed by analytics RTDs? Or is there any indication for high stator bar temperatures? | not mentioned | Temps below limit and steady (as a function of ambient & load, i.e. trending w/ Hot gas and cold gas temps) | One RTD showing elevated compared to others, or entire machine trending higher | Above limit | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Ventilation duct blocking | Are there any signs of ventilation blocking? Must be related to the stator core | not mentioned | Definitive statement of not present | Present but not causing temperature increase | Noted as heavy OR presence of increased bar temps | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Stator core burning | Are there signs of stator core burning? Any form of repair here is considered to reset the condition. | not mentioned | Not present | n/a | Signs of core discoloration due to heat or melting or localised hotspots | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Shorted Strand in stator bar | Were any shorted strands in the stator bar observed? | not mentioned | Not present | n/a | Observed in any way | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL | Stator Bar Temperature | Reversed fan blades | Are there signs of reversed fan blades on the main generator rotor fan, such as vibrations or fan Differential Pressure (DP or FDP) alarm? Damage is not evidence, reversed means the fan blades have been installed the wrong way. | not mentioned | Not present | n/a | Definitive statement of observing it in any way | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Stator Frame Vibrations | Are there signs of stator frame vibrations? Note: This does NOT reset with Stator Rewind. | not mentioned | Not present | Present but below alarm limits | Above alarm limits or impacting unit operations | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Noisy during operation (Unit noisy) or Red Oxide Dust inside core | Has the unit failed a harmonic noise index (HNI) test? In other words is the unit noisy during operation or is there red oxide dust inside the core? Note: This does NOT reset with a Stator Rewind. And any repair OR replacement requires a subsequent satisfactory HNI test to lower severity. The related components which can cause the red oxide formation are the Stator Core Compression Bands (Belly Bands) when they loosen. | not mentioned | Light red dust | Medium red dust | Heavy red dust or high noise in operation or failed HNI test | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | Inside Space Block (ISSB) or Outside Space Block (OSSB) migration | Were there any signs of Inside Space Block (ISSB) or Outside Space Block (OSSB) migration aka movement? Migration must be related to the ISSB or OSSB, do not include migration of other stator components. NOTE: This issue does NOT reset without a core restack or partial restack. Does not reset with Stator rewind alone. | not mentioned | Not Present | Present and noted as minor | Noted as major or heavy, or already cutting into the stator bar insulation | Not Applicable
GEN | Hydrogen Cooled |  | Stator | REL |  | Contamination | Is there signs in the stator or core region of sand, dirt, carbon dust, metallic contamination, or lead? Ignore oil, dusting and greasing, as these are covered under other issues. | Not present | Noted as light | Noted as medium | Noted as heavy, or any mention of lead contamination | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Stator | REL |  | FOD (Foreign Object Damage) | Was this unit evaluated for Foreign Object Damage (FOD) indications on the stator, excluding other non-stator generator hardware? | Not mentioned at all or not inspected | Definitive statement of no FOD during the test | Any evidence of FOD damage | Extensive or heavy FOD damage noted | Not Applicable | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Collector Ring Repairs / Replacement | Are there any signs of collector ring issues, such as excessive or uneven brush wear, arcing, flashing, foot printing, or dimensional checks out-of-spec? Any mention of dishing or issues with the run-out measurements? Any recommendations for Collector Ring machining? | Not mentined | Definitive statement of no findings OR Symptoms noted as light or acceptable. | Symptoms noted, but not quantified OR suggested to address at a future outage. | Symptoms stated as heavy or extreme, OR a recommendation to address it now or at first opportunity. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Collector Assembly / Brush Rigging | Are there any indications of uneven brush wear, loose or mis-aligned brush holders, or damaged collector springbacks? | Not mentined | Definitive statement of no findings OR Symptoms noted as light or acceptable. | Symptoms noted, but not quantified OR suggested to address at a future outage. | Symptoms stated as heavy or extreme, OR a recommendation to address it now or at first opportunity. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Grounding Brushes | Are there any signs of uneven wearing or improper rotor contact of grounding brushes? | Not mentined | Definitive statement of no findings OR Symptoms noted as light or acceptable. | Symptoms noted, but not quantified OR suggested to address at a future outage. | Symptoms stated as heavy or extreme, OR a recommendation to address it now or at first opportunity. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Collector Stud Repair / Tightening | Are there any signs of unaddressed hydrogen leaks, or any recommendations to tighten the collector stud? Was the work completed as recommended? |  | Definitive statement of no findings OR Previous recommendation to tighten the collector stud with evidence that it was perfomed. | Previous recommendation to tight the collector stud without evidence that it was performed. | Evidence of a hydrogen leak or alarm since last outage. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Hydrogen / Scavenging System Maintenance | Are there any signs of hydrogen purity issues or increased hydrogen consumption? | No mention of hydrogen purity | >95% purity | Purity is > 75% buy < 95% | < 75% H2 purity | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Hydrogen Seal Repair or Upgrade | Is there any mention of damage to, repair of, or replacement of hydrogen seals or hydrogen casings? | No mention of hydrogen seal/case repair, replacement, or damage. | Cleaning needed OR observations noted as minor OR a recommendation to repair or replace that has been completed. | indications of scoring, pitting, or damage that can be repaired. | Observations that lead to a recommendation to replace. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Bearings | Any issues with Bearing vibrations or Bearing metal temps? | No mention of bearings. | Definitive statement that the bearings are ok or good condition. | Any recommendation to inspect the bearing or babbet OR Any maintaned bearing metal temps > 225 F OR Any vibrations > 6 mils or a step change in vibrations more than 1 mil increase OR Completed bearing replacements due to observed damage | Any unfulfilled recommendations to repair or replace a bearing or to rebabbet OR Any bearing metal temps above alarm limit (> 250 F) OR Any vibrations > 9 mils | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Bearing Oil deflectors | Are there signs of oil ingress on this unit or visiual indications of damage on the oil deflectors. | No mention of the Oil deflectors OR oil ingress. | recommendations to clean oil deflectors OR minor oil ingress | recommendations to repair the oil deflectors OR moderate oil ingress OR previous completed replacements | unfulfilled recommendations to replace the oil deflectors OR severe oil ingress | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Stator RTD Test | Is there any evidence of failing the stator RTD test? | No mention of RTD test | Pass | n/a | Fail | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | High Voltage Bushings | Any issues with the visual inspection of High Voltage Bushings (HVB) or Stand-off Insulators (SOI), such as insulation degredation, oil leaks, or cracked/chipped porcelin? | No mention of HVB inspection. | Definitive statement of no issues with the HVB or stand-off insulator (SOI). | Any observations of oil leakage, cracking, cracked/chipped porcelin, or damaged insulation OR recommendations to address or repair at next outage. | Any observations quantified as serious, major, or severe OR recommendations to replace at next outage. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Hydrogen Coolers | Is there any evidence of a visual inspection or test of the hydrogen coolers? If yes, please classify per the severity criteria. | No mention of Hydrogen Coolers. | Definitive statement of no issues with the Hydrogen coolers. | Recommendations to clean or inspect the hydrogen coolers | Recommendations to do repairs or replacements to hydrogen coolers OR mention of leaks or corrosion or damage in hydrogen coolers or cooling fins OR failed test of the hydrogen coolers. | n/a | FSR, ER
GEN | Hydrogen Cooled |  | Other | OE |  | Excitation System / LCI | Are there any issues noted with the excitation system or Load Cummulative Inverter (LCI) or Static Start? | Not mentioned | Definitive statement of one or more of these systems having no issues OR mention of a EX2100e. | Any recommendations to upgrade to EX2100e OR mention of a EX2000. | Recommendations to upgrade board or hardware for any of these systems OR statement of obsolete hardware. | n/a | FSR, ER
GT | 7F |  | Gas Turbine Bearing | OE | Bearing | Gas Turbine (GT) Bearing Vibration Issues | Was this unit evaluated for signs of gas turbine (GT) bearing issues? | no mention of gas turbine (GT) bearing vibration. | Definitive statement that the gas turbine (GT) bearing vibrations are within limit | Evidence of gas turbine (GT) bearing vibration spikes or step changes of vibration > 0.1 in/s pk | Evidence of gas turbine (GT) bearing vibration that exceeds M&D limits or high vibrations in critical speed zones | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Bearing | OE | Bearing | Gas Turbine (GT) Bearing Condition | Was this unit evaluated for signs of gas turbine (GT) bearing condition? | no mention of gas turbine (GT) bearing condition. | Definitive statement that gas turbine (GT) bearings are in good condition | Evidence of gas turbine bearing pad scoring | Evidence of gas turbine bearing wipe | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Bearing | OE | Bearing | Gas Turbine (GT) Bearing Oil contamination | Was this unit evaluated for signs of gas turbine (GT) bearing lube oil contamination? | no mention of gas turbine bearing oil contamination | Definitive statement that there is no gas turbine bearing lube oil contamination |  | Evidence of gas turbine bearing lube oil contamination or alarm | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Journal Bearing | OE | Bearing | Journal Bearing Proximity Vibration | Was the unit evaluated for bearing amplitudes? | no mention bearing amplitude data |  | bearing amplitude > 6 mils pp | bearing amplitude > 7.5 mils pp | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Journal Bearing | OE | Bearing | Journal Bearing Seismic Vibration | Was the unit evaluated for bearing vibration sensor? | no mentione of bearing vibration data |  | vibration sensor > 0.50 in/s pk | vibration sensor > 0.65 in/s pk | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Journal Bearing | OE | Bearing | Journal Bearing Lube Oil (Header) Temperature | was the unit evaluated for lube oil header temperature? | no mention of lube oil header temperature data |  | lube oil header temperature > 150 deg F | lube oil header temperature > 164 deg F | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Journal Bearing | OE | Bearing | Journal Bearing Lube Oil Drain Temperature | was the unit evaluated for journal bearing drain temperature? | no mention of journal bearing drain temperature data |  | journal bearing drain temperature > 180 deg F | journal bearing drain temperature > 200 deg F | n/a | FSR, ER, MND
GT | 7F |  | Gas Turbine Journal Bearing | OE | Bearing | Journal Bearing Metal Temperature | Was the unit evaluated for bearing metal temp? | no mention of bearing metal temperature data |  | bearing metal temp > 240 deg F | bearing metal temp > 260 deg F | n/a | FSR, ER, MND
GT | 7F |  | Compressor Bleed Valve (CBV) | OE | Valves | CBV slow response times | Was this unit evaluated for signs of compressor bleed valve (CBV) response times? | no mention of compressor bleed valve response times | Evidence of compressor bleed valve response times less than 5 seconds | Evidence of compressor bleed valve response times greater than 5 seconds | Evidence of compressor bleed valve response times greater than 7.5 seconds OR recommendation to replace, repair or refurbish CBV | n/a | FSR, ER, MND
GT | 7F |  | Compressor Bleed Valve (CBV) | OE | Valves | CBV failure to indicate open/closed | Was this unit evaluated for signs of compressor bleed valve (CBV) failure to open or close? | no mention of compressor bleed valve failing to indicate open or close | Definitive statement that the CBV's are ok or in good condition. |  | Evidence of compressor bleed valves failed to indicate open or closed | n/a | FSR, ER, MND
GT | 7F |  | Compressor Bleed Valve (CBV) | OE | Valves | CBV trips caused by valve operation | Was this unit evaluated for signs of compressor bleed valve (CBV) trips? | no mention of compressor bleed valve trips | Definitive statement of no compressor bleed valve trips | Evidence of 1 compressor bleed valve trip | Evidence of 2 or more compressor bleed valve trips | n/a | FSR, ER, MND
GT | 7F |  | Compressor Bleed Valve (CBV) | OE | Valves | CBV maintenance recommendations | Was compressor bleed valve maintenance recommended? | no mention of recommending compressor bleed valve maintenance |  | Recommendation to repair or perform maintenance on CBV | Recommendation to replace CBV | n/a | FSR, ER, MND
GT | 7F |  | Inlet Bleed Heat (IBH) Valve | OE | Valves | IBH valve position error | Was there an observation of IBH valve position error? | no mention of IBH valve position error |  | valve position error > 7% | valve position error > 10% | n/a | FSR, ER, MND
GT | 7F |  | Inlet Bleed Heat (IBH) Valve | OE | Valves | IBH valve leakage | Was there an observation of IBH valve leak? | no mention of IBH valve leak |  |  | evidence of IBH valve leak alarm created | n/a | FSR, ER, MND
GT | 7F |  | Inlet Bleed Heat (IBH) Valve | OE | Valves | IBH valve trips caused by valve operation | Was this unit evaluated for signs of IBH valve trips? | no mention of IBH valve trips |  | Evidence of 1 IBH valve trip | Evidence of 2 or more IBH valve trips | n/a | FSR, ER, MND
GT | 7F |  | Inlet Bleed Heat (IBH) Valve | OE | Valves | IBH valve maintenance recommendations | Was inlet bleed heat valve maintenance recommended? | no mention of recommending inlet bleed heat valve maintenance |  | Recommendation to repair or perform maintenance on IBH valve | Recommendation to replace IBH valve | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Control (GCV) Valve | OE | Valves | GCV position error | Was there an observation of GHV or GCV valve position error? | no mention of GHV or GCV valve position errors |  | absolute GHV or GCV valve position error is greater than 2 | absolute GHV or GCV valve position error is greater than 3 | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Control (GCV) Valve | OE | Valves | GCV servo current error | Was there an observation of GHV or GCV valve current alarm? | no mention of GHV or GCV valve out of current limit |  | GHV or GCV valve current out of limit. Valve current is less than -7% or greater than 2% | GHV or GCV valve current out of limit. Valve current is less than -8% or greater than 12% | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Control (GCV) Valve | OE | Valves | GCV servo current oscillation/instability | Was there an observation of GHV or GCV valve oscillation alarm? | no mention of GHV or GCV valve oscillation alarm |  |  | evidence of GHV or GCV valve oscillation alarm created | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Control (GCV) Valve | OE | Valves | GCV valve trips caused by valve operation | Was this unit evaluated for signs of GHV or GCV valve trips? | no mention of GHV or GCV valve trips |  | Evidence of 1 GHV or GCV valve trip | Evidence of 2 or more GHV or GCV valve trips | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Control (GCV) Valve | OE | Valves | GCV maintenance recommendation | Was gas control valve maintenance recommended? | no mention of recommending gas control valve maintenance |  | Recommendation to repair or perform maintenance on gas control valve | Recommendation to replace gas control valve | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Stop Ratio Valve (SRV) | OE | Valves | SRV position error | Was there an observation of SRV position error? | no mention of SRV valve position errors |  | absolute SRV valve position error is greater than 2 | absolute SRV valve position error is greater than 3 | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Stop Ratio Valve (SRV) | OE | Valves | SRV servo current error | Was there an observation of SRV servo current error? | no mention of SRV valve out of current limit |  | SRV valve current out of limit. Valve current is less than -7% or greater than 2% | SRV valve current out of limit. Valve current is less than -8% or greater than 12% | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Stop Ratio Valve (SRV) | OE | Valves | SRV servo current oscillation/instability | Was there an observation of SRV servo current oscillation or instability? | no mention of SRV valve oscillation alarm |  |  | evidence of SRV valve oscillation alarm created | n/a | FSR, ER, MND
GT | 7F |  | Gas Fuel Stop Ratio Valve (SRV) | OE | Valves | SRV maintenance recommendation | Was stop ratio valve maintenance recommended? | no mention of recommending stop ratio valve maintenance |  | Recommendation to repair or perform maintenance on stop ratio valve | Recommendation to replace stop ratio valve | n/a | FSR, ER, MND
GT | 7F |  | Inlet Bellmouth | OE | GT Inlet | Inlet Bellmouth paint condition | Were there observations of missing or loose paint on the gas turbine inlet bellmouth with recommendations to paint the inlet bellmouth? | no mention of missing inlet bellmouth paint |  | observations of missing or loose paint on the gas turbine inlet bellmouth | recommendation to paint gas turbine inlet bellmouth | n/a | FSR, ER
GT | 7F |  | Inlet Filtration System | OE | GT Inlet | Damaged inlet filtration | Were there observations of deposits, erosion or oxidations in compressor stages with recommendations to inspect inlet filter? | no mention of damaged gas turbine inlet filter |  | observations of deposits, erosion or oxidations in compressor stages. Evidence of foreign object (FOD) compressor damage | Recommendation to inspect inlet filter | n/a | FSR, ER
GT | 7F |  | Compressor | OE | Compressor | Compressor fouling | Were there observations of deposits, erosion, compressor fouling or oxidations in compressor stages with recommendations to perform waterwash? | no mention of compressor fouling or degradation |  | observations of deposits, erosion, compressor fouling or oxidations in compressor stages | Recommendation to perform compressor waterwash | n/a | FSR, ER
GT | 7F |  | Compressor | REL | Compressor | S17 Bushing Migration | Are there any signs of stage 17 Stator vane (S17) bushing wear, bushing migration? Are there any other signs of damage such as fretting of the Stage 17 shroud? |  | No Data | Definitive statement of typical or good condition of compressor S17 bushings or compressor S17 shrouds. Note: Typical condition can include observations like rocking, wear or fretting that is not quantified as heavy or severe. | An observation of wear or migration on single compressor S17 bushing AND no mention of clashing. | An observation of wear or migration on multiple compressor S17 bushing AND no mention of clashing. | FSR, ER
GT | 7F |  | Compressor | REL | Compressor | S17 Replacement | were S17 stators replaced ? Which version Dwg No. Implemented ? |  | No Data | Definitive statement of compressor S17 stators replacementnt or upgrade | Definitive statement of full set of compressor S17 stators replacementnt or upgrade | n/a | FSR, ER
GT | 7F |  | Compressor | REL | Compressor | Stator Replacements in other stages | were any of stage S## (0-16) stators replaced ? Which version Dwg No. Implemented ? |  | No Data | Definitive statement of S## compressor stators replacement or upgrade | Definitive statement of full set of S## compressor stators replacement or upgrade. Note: Part numbers that include "L" are kit level (i.e. full set). | n/a | FSR, ER